## Legenda
Sheet
Version | P04354
Device
Device Timeout | 300
Device buffer RX (bytes) | 30
Device buffer TX (bytes) | 30
Document info
Author
Date last update | 15/4/2019 @ 16:39:13
Firmware Mask | CUSTOM(20000) | Mskxxx
Firmware Version | 0 | yy
Document version | 0 | zz
Network Address Filter | 1-255
Baud Rate | 115200
Parity | E
Protocol | MODBUS
Filename | AHUEliwell-1.11.bin
Cells filled by:
FIRMWARE TEAM
SOFTWARE TEAM
PROJECT MANAGER TEAM
TEST&VALIDATION TEAM

## Models
POLI | MODEL_NAME | PARAM_MANAGER_NAME | PARAM_MANAGER_NAME_MODBUS
1 | AHUEliwell-1.11 | M20000PM | M20000PM
Note on A1: Guido Bertella: POLI Example: 1025 1026 etc.
Note on B1: Guido Bertella: Example: ID 961LX ID 974LX etc.
Note on C1: Guido Bertella: Example: ID 961LX ID 974LX etc.

## DataAcquisitionInit
FUNCTION | PROTOCOL | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
IDENTIFICATION | ANY | 0: SET(MODELCODE)=Client(Unit_ApplicationCode); 1: GET(MODELCODE)=FIX(1)
Note on A1: HELP: Supported functions are: IDENTIFICATION PRE_AUTOACQUISITION_DISCOVERY PRE_RVD_DISCOVERY
Note on B1: Guido Bertella: Protocol: 1) MICRONET 2) MODBUS

## ParamsDefaults
INDEX | LABEL | 1 | Custom PM model
|  | MODBUS | MODBUS
1 | PSW1 | * | FALSE
2 | PSW2 | * | FALSE
3 | cfgFans | * | FALSE
4 | cfgFanType | * | FALSE
5 | cfgFanRegulation | * | FALSE
6 | cfgFanAlarm | * | FALSE
7 | cfgCoolHeatModules | * | FALSE
8 | cfgCooling | * | FALSE
9 | cfgHeating | * | FALSE
10 | cfgCooling_Heating | * | FALSE
11 | cfgPreHeating | * | FALSE
12 | cfgPostHeating | * | FALSE
13 | cfgAntifreeze | * | FALSE
14 | cfgHeatRecovery | * | FALSE
15 | cfgDefrostHeatRec | * | FALSE
16 | cfgDampers | * | FALSE
17 | cfgHumidifier | * | FALSE
18 | cfgDeHumidifier | * | FALSE
19 | cfgDampersForFans | * | FALSE
20 | cfgAirQuality | * | FALSE
21 | cfgFilterPressostat | * | FALSE
22 | cfgDoorDI | * | FALSE
23 | cfgModeDI | * | FALSE
24 | cfgModeDO | * | FALSE
25 | cfgCoolHeat_NumSteps | * | FALSE
26 | cfgHeat_NumSteps | * | FALSE
27 | cfgPreHeat_NumSteps | * | FALSE
28 | cfgPostHeat_NumSteps | * | FALSE
29 | cfgMixChamberBeforePreHeat | * | FALSE
30 | CfgParallelFans | * | FALSE
31 | cfgEE_free3 | * | FALSE
32 | cfgEE_free4 | * | FALSE
33 | cfgEE_free5 | * | FALSE
34 | cfgEE_free6 | * | FALSE
35 | cfgEE_free7 | * | FALSE
36 | cfgEE_free8 | * | FALSE
37 | ioEE_base_AI_01 | * | FALSE
38 | ioEE_base_AI_02 | * | FALSE
39 | ioEE_base_AI_03 | * | FALSE
40 | ioEE_base_AI_04 | * | FALSE
41 | ioEE_base_AI_05 | * | FALSE
42 | ioEE_base_AI_06 | * | FALSE
43 | ioEE_base_AI_07 | * | FALSE
44 | ioEE_base_AI_08 | * | FALSE
45 | ioEE_base_AI_09 | * | FALSE
46 | ioEE_base_AI_10 | * | FALSE
47 | ioEE_base_AI_11 | * | FALSE
48 | ioEE_base_AI_12 | * | FALSE
49 | ioEE_exp1_AI_01 | * | FALSE
50 | ioEE_exp1_AI_02 | * | FALSE
51 | ioEE_exp1_AI_03 | * | FALSE
52 | ioEE_exp1_AI_04 | * | FALSE
53 | ioEE_exp2_AI_01 | * | FALSE
54 | ioEE_exp2_AI_02 | * | FALSE
55 | ioEE_exp2_AI_03 | * | FALSE
56 | ioEE_exp2_AI_04 | * | FALSE
57 | ioEE_free1 | * | FALSE
58 | ioEE_free2 | * | FALSE
59 | ioEE_free3 | * | FALSE
60 | ioEE_free4 | * | FALSE
61 | ioEE_free5 | * | FALSE
62 | ioEE_free6 | * | FALSE
63 | ioEE_free7 | * | FALSE
64 | ioEE_free8 | * | FALSE
65 | ioEE_base_DI_01 | * | FALSE
66 | ioEE_base_DI_02 | * | FALSE
67 | ioEE_base_DI_03 | * | FALSE
68 | ioEE_base_DI_04 | * | FALSE
69 | ioEE_base_DI_05 | * | FALSE
70 | ioEE_base_DI_06 | * | FALSE
71 | ioEE_base_DI_07 | * | FALSE
72 | ioEE_base_DI_08 | * | FALSE
73 | ioEE_base_DI_09 | * | FALSE
74 | ioEE_base_DI_10 | * | FALSE
75 | ioEE_base_DI_11 | * | FALSE
76 | ioEE_base_DI_12 | * | FALSE
77 | ioEE_exp1_DI_01 | * | FALSE
78 | ioEE_exp1_DI_02 | * | FALSE
79 | ioEE_exp1_DI_03 | * | FALSE
80 | ioEE_exp1_DI_04 | * | FALSE
81 | ioEE_exp2_DI_01 | * | FALSE
82 | ioEE_exp2_DI_02 | * | FALSE
83 | ioEE_exp2_DI_03 | * | FALSE
84 | ioEE_exp2_DI_04 | * | FALSE
85 | ioEE_free9 | * | FALSE
86 | ioEE_free10 | * | FALSE
87 | ioEE_free11 | * | FALSE
88 | ioEE_free12 | * | FALSE
89 | ioEE_free13 | * | FALSE
90 | ioEE_free14 | * | FALSE
91 | ioEE_free15 | * | FALSE
92 | ioEE_free16 | * | FALSE
93 | ioEE_base_DO_01 | * | FALSE
94 | ioEE_base_DO_02 | * | FALSE
95 | ioEE_base_DO_03 | * | FALSE
96 | ioEE_base_DO_04 | * | FALSE
97 | ioEE_base_DO_05 | * | FALSE
98 | ioEE_base_DO_06 | * | FALSE
99 | ioEE_base_DO_07 | * | FALSE
100 | ioEE_base_DO_08 | * | FALSE
101 | ioEE_base_DO_09 | * | FALSE
102 | ioEE_base_DO_10 | * | FALSE
103 | ioEE_base_DO_11 | * | FALSE
104 | ioEE_base_DO_12 | * | FALSE
105 | ioEE_exp1_DO_01 | * | FALSE
106 | ioEE_exp1_DO_02 | * | FALSE
107 | ioEE_exp1_DO_03 | * | FALSE
108 | ioEE_exp1_DO_04 | * | FALSE
109 | ioEE_exp2_DO_01 | * | FALSE
110 | ioEE_exp2_DO_02 | * | FALSE
111 | ioEE_exp2_DO_03 | * | FALSE
112 | ioEE_exp2_DO_04 | * | FALSE
113 | ioEE_free17 | * | FALSE
114 | ioEE_free18 | * | FALSE
115 | ioEE_free19 | * | FALSE
116 | ioEE_free20 | * | FALSE
117 | ioEE_free21 | * | FALSE
118 | ioEE_free22 | * | FALSE
119 | ioEE_free23 | * | FALSE
120 | ioEE_free24 | * | FALSE
121 | ioEE_base_AO_01 | * | FALSE
122 | ioEE_base_AO_02 | * | FALSE
123 | ioEE_base_AO_03 | * | FALSE
124 | ioEE_base_AO_04 | * | FALSE
125 | ioEE_base_AO_05 | * | FALSE
126 | ioEE_base_AO_06 | * | FALSE
127 | ioEE_exp1_AO_01 | * | FALSE
128 | ioEE_exp1_AO_02 | * | FALSE
129 | ioEE_exp2_AO_01 | * | FALSE
130 | ioEE_exp2_AO_02 | * | FALSE
131 | ioEE_free25 | * | FALSE
132 | ioEE_free26 | * | FALSE
133 | ioEE_free27 | * | FALSE
134 | ioEE_free28 | * | FALSE
135 | ioEE_free29 | * | FALSE
136 | ioEE_free30 | * | FALSE
137 | ioEE_free31 | * | FALSE
138 | ioEE_free32 | * | FALSE
139 | Cfg_exp1_AI1 | * | FALSE
140 | Cfg_exp1_AI2 | * | FALSE
141 | Cfg_exp1_AI3 | * | FALSE
142 | Cfg_exp1_AI4 | * | FALSE
143 | Cfg_exp2_AI1 | * | FALSE
144 | Cfg_exp2_AI2 | * | FALSE
145 | Cfg_exp2_AI3 | * | FALSE
146 | Cfg_exp2_AI4 | * | FALSE
147 | ioEE_free33 | * | FALSE
148 | ioEE_free34 | * | FALSE
149 | ioEE_free35 | * | FALSE
150 | ioEE_free36 | * | FALSE
151 | ioEE_free37 | * | FALSE
152 | ioEE_free38 | * | FALSE
153 | ioEE_free39 | * | FALSE
154 | ioEE_free40 | * | FALSE
155 | FullScaleMin_exp1_AI1 | * | FALSE
156 | FullScaleMax_exp1_AI1 | * | FALSE
157 | FullScaleMin_exp1_AI2 | * | FALSE
158 | FullScaleMax_exp1_AI2 | * | FALSE
159 | FullScaleMin_exp1_AI3 | * | FALSE
160 | FullScaleMax_exp1_AI3 | * | FALSE
161 | FullScaleMin_exp1_AI4 | * | FALSE
162 | FullScaleMax_exp1_AI4 | * | FALSE
163 | FullScaleMin_exp2_AI1 | * | FALSE
164 | FullScaleMax_exp2_AI1 | * | FALSE
165 | FullScaleMin_exp2_AI2 | * | FALSE
166 | FullScaleMax_exp2_AI2 | * | FALSE
167 | FullScaleMin_exp2_AI3 | * | FALSE
168 | FullScaleMax_exp2_AI3 | * | FALSE
169 | FullScaleMin_exp2_AI4 | * | FALSE
170 | FullScaleMax_exp2_AI4 | * | FALSE
171 | ioEE_free41 | * | FALSE
172 | ioEE_free42 | * | FALSE
173 | ioEE_free43 | * | FALSE
174 | ioEE_free44 | * | FALSE
175 | ioEE_free45 | * | FALSE
176 | ioEE_free46 | * | FALSE
177 | ioEE_free47 | * | FALSE
178 | ioEE_free48 | * | FALSE
179 | ioEE_free57 | * | FALSE
180 | ioEE_free58 | * | FALSE
181 | ioEE_free59 | * | FALSE
182 | ioEE_free60 | * | FALSE
183 | ioEE_free61 | * | FALSE
184 | ioEE_free62 | * | FALSE
185 | ioEE_free63 | * | FALSE
186 | ioEE_free64 | * | FALSE
187 | Calibration_exp1_AI1 | * | FALSE
188 | Calibration_exp1_AI2 | * | FALSE
189 | Calibration_exp1_AI3 | * | FALSE
190 | Calibration_exp1_AI4 | * | FALSE
191 | Calibration_exp2_AI1 | * | FALSE
192 | Calibration_exp2_AI2 | * | FALSE
193 | Calibration_exp2_AI3 | * | FALSE
194 | Calibration_exp2_AI4 | * | FALSE
195 | ioEE_free49 | * | FALSE
196 | ioEE_free50 | * | FALSE
197 | ioEE_free51 | * | FALSE
198 | ioEE_free52 | * | FALSE
199 | ioEE_free53 | * | FALSE
200 | ioEE_free54 | * | FALSE
201 | ioEE_free55 | * | FALSE
202 | ioEE_free56 | * | FALSE
203 | DI_Polarity_LogicIndex_0 | * | FALSE
204 | DI_Polarity_LogicIndex_1 | * | FALSE
205 | DI_Polarity_LogicIndex_2 | * | FALSE
206 | DI_Polarity_LogicIndex_3 | * | FALSE
207 | DI_Polarity_LogicIndex_4 | * | FALSE
208 | DI_Polarity_LogicIndex_5 | * | FALSE
209 | DI_Polarity_LogicIndex_6 | * | FALSE
210 | DI_Polarity_LogicIndex_7 | * | FALSE
211 | DI_Polarity_LogicIndex_8 | * | FALSE
212 | DI_Polarity_LogicIndex_9 | * | FALSE
213 | DI_Polarity_LogicIndex_10 | * | FALSE
214 | DI_Polarity_LogicIndex_11 | * | FALSE
215 | DI_Polarity_LogicIndex_12 | * | FALSE
216 | DI_Polarity_LogicIndex_13 | * | FALSE
217 | DI_Polarity_LogicIndex_14 | * | FALSE
218 | DI_Polarity_LogicIndex_15 | * | FALSE
219 | DI_Polarity_LogicIndex_16 | * | FALSE
220 | DI_Polarity_LogicIndex_17 | * | FALSE
221 | DI_Polarity_LogicIndex_18 | * | FALSE
222 | DI_Polarity_LogicIndex_19 | * | FALSE
223 | DI_Polarity_LogicIndex_20 | * | FALSE
224 | DI_Polarity_LogicIndex_21 | * | FALSE
225 | DI_Polarity_LogicIndex_22 | * | FALSE
226 | DI_Polarity_LogicIndex_26_29 | * | FALSE
227 | DI_Polarity_LogicIndex_30 | * | FALSE
228 | DI_Polarity_Free2 | * | FALSE
229 | DI_Polarity_Free3 | * | FALSE
230 | DI_Polarity_Free4 | * | FALSE
231 | DI_Polarity_Free5 | * | FALSE
232 | DO_Polarity_LogicIndex_0 | * | FALSE
233 | DO_Polarity_LogicIndex_1 | * | FALSE
234 | DO_Polarity_LogicIndex_2 | * | FALSE
235 | DO_Polarity_LogicIndex_3 | * | FALSE
236 | DO_Polarity_LogicIndex_4 | * | FALSE
237 | DO_Polarity_LogicIndex_5 | * | FALSE
238 | DO_Polarity_LogicIndex_6 | * | FALSE
239 | DO_Polarity_LogicIndex_7 | * | FALSE
240 | DO_Polarity_LogicIndex_8 | * | FALSE
241 | DO_Polarity_LogicIndex_9 | * | FALSE
242 | DO_Polarity_LogicIndex_10 | * | FALSE
243 | DO_Polarity_LogicIndex_11 | * | FALSE
244 | DO_Polarity_LogicIndex_12 | * | FALSE
245 | DO_Polarity_LogicIndex_13 | * | FALSE
246 | DO_Polarity_LogicIndex_14 | * | FALSE
247 | DO_Polarity_LogicIndex_15 | * | FALSE
248 | DO_Polarity_LogicIndex_16 | * | FALSE
249 | DO_Polarity_LogicIndex_17 | * | FALSE
250 | DO_Polarity_LogicIndex_18 | * | FALSE
251 | DO_Polarity_LogicIndex_19 | * | FALSE
252 | DO_Polarity_LogicIndex_20 | * | FALSE
253 | DO_Polarity_LogicIndex_21 | * | FALSE
254 | DO_Polarity_LogicIndex_22 | * | FALSE
255 | DO_Polarity_LogicIndex_23 | * | FALSE
256 | DO_Polarity_LogicIndex_24 | * | FALSE
257 | DO_Polarity_LogicIndex_25 | * | FALSE
258 | DO_Polarity_LogicIndex_26 | * | FALSE
259 | DO_Polarity_LogicIndex_27 | * | FALSE
260 | DO_Polarity_LogicIndex_28 | * | FALSE
261 | DO_Polarity_LogicIndex_29 | * | FALSE
262 | DO_Polarity_LogicIndex_30 | * | FALSE
263 | DO_Polarity_LogicIndex_31 | * | FALSE
264 | ioEE_free73 | * | FALSE
265 | ioEE_free74 | * | FALSE
266 | ioEE_free75 | * | FALSE
267 | ioEE_free76 | * | FALSE
268 | ioEE_free77 | * | FALSE
269 | ioEE_free78 | * | FALSE
270 | ioEE_free79 | * | FALSE
271 | ioEE_free80 | * | FALSE
272 | BACNET_ENABLE | * | FALSE
273 | BACNET_ID | * | FALSE
274 | BACNET_BBMD_Ip1 | * | FALSE
275 | BACNET_BBMD_Ip2 | * | FALSE
276 | BACNET_BBMD_Ip3 | * | FALSE
277 | BACNET_BBMD_Ip4 | * | FALSE
278 | BACNET_BBMD_TMO | * | FALSE
279 | BACNET_BBMD_PORT | * | FALSE
280 | WEB_User_E2 | * | FALSE
281 | WEB_PSW_E2 | * | FALSE
282 | DayLight_Region | * | FALSE
283 | DayLight_Enable | * | FALSE
284 | Unit_ForceOffAfterReboot | * | FALSE
285 | Unit_RegTempType | * | FALSE
286 | SP_T_MIN | * | FALSE
287 | SP_T_MAX | * | FALSE
288 | SP_T_Auto_E2 | * | FALSE
289 | DIFF_T_AutoChangeMode | * | FALSE
290 | DIFF_T_AutoEco | * | FALSE
291 | SP_T_FORCESUMMER | * | FALSE
292 | SP_T_FORCEWINTER | * | FALSE
293 | SP_T_Cool_E2 | * | FALSE
294 | SP_T_Heat_E2 | * | FALSE
295 | SP_T_CoolEco_E2 | * | FALSE
296 | SP_T_HeatEco_E2 | * | FALSE
297 | SP_RH_MinSetpoint | * | FALSE
298 | SP_RH_MaxSetpoint | * | FALSE
299 | SP_RH_DehumidificationSetpoint_E2 | * | FALSE
300 | SP_RH_DehumidificationSetpointEco_E2 | * | FALSE
301 | SP_RH_HumidificationSetpoint_E2 | * | FALSE
302 | SP_RH_HumidificationSetpointEco_E2 | * | FALSE
303 | SP_VOC_E2 | * | FALSE
304 | SP_CO2_E2 | * | FALSE
305 | cfgFreeCooling | * | FALSE
306 | cfgFreeHeating | * | FALSE
307 | FreeCHMinExtTemp | * | FALSE
308 | FreeCHBand | * | FALSE
309 | FreeCHTimeout | * | FALSE
310 | FreeCHDiff | * | FALSE
311 | FreeCHHyst | * | FALSE
312 | cfgFireAlarm | * | FALSE
313 | FireTempSet | * | FALSE
314 | Alm_MinHumiditySens | * | FALSE
315 | Alm_MinVOCSens | * | FALSE
316 | Alm_MinCO2Sens | * | FALSE
317 | Alm_MinPrSens | * | FALSE
318 | Alm_ActiveProbeBypass | * | FALSE
319 | AFset | * | FALSE
320 | AFdiff | * | FALSE
321 | AFphtime | * | FALSE
322 | ExtDamperOpenDelay | * | FALSE
323 | ExtDamperCloseDelay | * | FALSE
324 | ExtDamperMinOpen | * | FALSE
325 | ExtDamperMaxOpen | * | FALSE
326 | VOC_Bp | * | FALSE
327 | VOC_Ti | * | FALSE
328 | CO2_Bp | * | FALSE
329 | CO2_Ti | * | FALSE
330 | Fan_MinimumSpeed | * | FALSE
331 | Fan_LowSpeed | * | FALSE
332 | Fan_NominalSpeed | * | FALSE
333 | Fan_ReturnSpeedCorrection | * | FALSE
334 | Fan_PowerUp1_Time | * | FALSE
335 | Fan_PowerUp2_Time | * | FALSE
336 | Fan_Post_Time | * | FALSE
337 | Fan_PreHeating_Time | * | FALSE
338 | Fan_PreHeatOnSet | * | FALSE
339 | Fan_Swap_Time | * | FALSE
340 | Fan_SwapPolicy | * | FALSE
341 | Fan_SinglePressureReturn | * | FALSE
342 | Fan_AlrmPressBypass | * | FALSE
343 | Fan_SupplyAirflowAlrmByAi | * | FALSE
344 | Fan_ReturnAirflowAlrmByAi | * | FALSE
345 | Fan_SetMinAirflow | * | FALSE
346 | FAN_Supply_BpP | * | FALSE
347 | FAN_Supply_TiP | * | FALSE
348 | FAN_Supply_TdP | * | FALSE
349 | FAN_Return_BpP | * | FALSE
350 | FAN_Return_TiP | * | FALSE
351 | FAN_Return_TdP | * | FALSE
352 | Fan_K_Supply | * | FALSE
353 | Fan_K_Return | * | FALSE
354 | Fan_Supply_Pressure_Flow | * | FALSE
355 | Fan_Return_Pressure_Flow | * | FALSE
356 | Fan_Supply_SetMinPr | * | FALSE
357 | Fan_Return_SetMinPr | * | FALSE
358 | Fan_SetPrSupply | * | FALSE
359 | Fan_SetPrReturn | * | FALSE
360 | Fan_Supply_SetMaxPr | * | FALSE
361 | Fan_Return_SetMaxPr | * | FALSE
362 | Fan_Supply_SetMinFlow | * | FALSE
363 | Fan_Return_SetMinFlow | * | FALSE
364 | Fan_SetFlowSupply | * | FALSE
365 | Fan_SetFlowReturn | * | FALSE
366 | Fan_Supply_SetMaxFlow | * | FALSE
367 | Fan_Return_SetMaxFlow | * | FALSE
368 | SupplyDeltaUpHeating | * | FALSE
369 | SupplyDeltaDwHeating | * | FALSE
370 | SupplyDeltaUpCooling | * | FALSE
371 | SupplyDeltaDwCooling | * | FALSE
372 | Pb_Cooling | * | FALSE
373 | Pb_Heating | * | FALSE
374 | Ti_Cooling | * | FALSE
375 | Ti_Heating | * | FALSE
376 | Pb_ReturnCooling | * | FALSE
377 | Pb_ReturnHeating | * | FALSE
378 | Ti_ReturnCooling | * | FALSE
379 | Ti_ReturnHeating | * | FALSE
380 | Temp_HighSupplyEn | * | FALSE
381 | Temp_HighSupplySet | * | FALSE
382 | Temp_HighSupplyBand | * | FALSE
383 | Temp_LowSupplyEn | * | FALSE
384 | Temp_LowSupplySet | * | FALSE
385 | Temp_LowSupplyBand | * | FALSE
386 | FastHeatCoolEn | * | FALSE
387 | FastHeatSet | * | FALSE
388 | FastCoolSet | * | FALSE
389 | FastHCTimeout | * | FALSE
390 | FastHeatExitSet | * | FALSE
391 | FastCoolExitSet | * | FALSE
392 | Pump_AntiStickingRun | * | FALSE
393 | Pump_AntiStickingPeriod | * | FALSE
394 | Pump_Post_Time | * | FALSE
395 | Heater_Power_Analog | * | FALSE
396 | Heater_Power_Step1 | * | FALSE
397 | Heater_Power_Step2 | * | FALSE
398 | Heater_Power_Step3 | * | FALSE
399 | Heater_Power_Step4 | * | FALSE
400 | Heater_Power_Step5 | * | FALSE
401 | Heater_Power_Step6 | * | FALSE
402 | Heater_Hysteresis | * | FALSE
403 | Heater_PWM_Period | * | FALSE
404 | PreHeater_Power_Analog | * | FALSE
405 | PreHeater_Power_Step1 | * | FALSE
406 | PreHeater_Power_Step2 | * | FALSE
407 | PreHeater_Power_Step3 | * | FALSE
408 | PreHeater_Power_Step4 | * | FALSE
409 | PreHeater_Power_Step5 | * | FALSE
410 | PreHeater_Power_Step6 | * | FALSE
411 | PreHeater_Hysteresis | * | FALSE
412 | PreHeater_PWM_Period | * | FALSE
413 | PostHeater_Power_Analog | * | FALSE
414 | PostHeater_Power_Step1 | * | FALSE
415 | PostHeater_Power_Step2 | * | FALSE
416 | PostHeater_Power_Step3 | * | FALSE
417 | PostHeater_Power_Step4 | * | FALSE
418 | PostHeater_Power_Step5 | * | FALSE
419 | PostHeater_Power_Step6 | * | FALSE
420 | PostHeater_Hysteresis | * | FALSE
421 | PostHeater_PWM_Period | * | FALSE
422 | CondUnitS1_Req | * | FALSE
423 | CondUnitS2_Req | * | FALSE
424 | CondUnitS3_Req | * | FALSE
425 | CondUnitS4_Req | * | FALSE
426 | CondUnitSx_Hysteresis | * | FALSE
427 | CondUnit_Ton | * | FALSE
428 | CondUnit_Toff | * | FALSE
429 | CondUnit_Offset | * | FALSE
430 | CondUnit_FanSpeedDefrost | * | FALSE
431 | MultiCondUnit_CtrlMode | * | FALSE
432 | MultiCondUnit_RegHyst | * | FALSE
433 | MultiCondUnit_DelayOn | * | FALSE
434 | MultiCondUnit_DelayOff | * | FALSE
435 | PreHeaterSetpoint | * | FALSE
436 | Pb_PreHeating | * | FALSE
437 | Ti_PreHeating | * | FALSE
438 | RecoveryDiff_Band | * | FALSE
439 | RecoveryDeadZone | * | FALSE
440 | RecoveryPower | * | FALSE
441 | RecoveryDefrost_SetMaxReq | * | FALSE
442 | RecoveryDefrost_Band | * | FALSE
443 | RecoveryDefrost_Cutoff | * | FALSE
444 | RecoveryReqDuringFastHC | * | FALSE
445 | Hum_Band | * | FALSE
446 | Pb_Dehum | * | FALSE
447 | Ti_Dehum | * | FALSE
448 | Pb_Dewpoint | * | FALSE
449 | Ti_Dewpoint | * | FALSE
450 | Offset_Post | * | FALSE
451 | Dehum_WinterEn | * | FALSE
452 | Dehum_WinterHumHyst | * | FALSE
453 | Dehum_Req_Diff | * | FALSE
454 | Hum_HighSupplyEn | * | FALSE
455 | Hum_HighSupplySet | * | FALSE
456 | Hum_HighSupplyBand | * | FALSE
457 | DeHum_LowSupplyEn | * | FALSE
458 | DeHum_LowSupplySet | * | FALSE
459 | DeHum_LowSupplyBand | * | FALSE
460 | PostHeating4Integration | * | FALSE
461 | PostPower | * | FALSE
462 | Pb_Post | * | FALSE
463 | Ti_Post | * | FALSE
464 | LogEnable | * | FALSE
465 | LogCycle | * | FALSE
466 | LogErrorNumber | * | FALSE
467 | LoggedRecord | * | FALSE
468 | MinLogCycle | * | FALSE
469 | FirstDownload | * | FALSE
470 | microSDPresCount | * | FALSE
471 | tE00_TimeBandEnable | * | FALSE
472 | tE01_TimeProfileMonday | * | FALSE
473 | tE02_TimeProfileTuesday | * | FALSE
474 | tE03_TimeProfileWednesday | * | FALSE
475 | tE04_TimeProfileThursday | * | FALSE
476 | tE05_TimeProfileFriday | * | FALSE
477 | tE06_TimeProfileSaturday | * | FALSE
478 | tE07_TimeProfileSunday | * | FALSE
479 | tE10_TimeProfile1Event1 | * | FALSE
480 | tE11_ModeProfile1Event1 | * | FALSE
481 | tE12_TimeProfile1Event2 | * | FALSE
482 | tE13_ModeProfile1Event2 | * | FALSE
483 | tE14_TimeProfile1Event3 | * | FALSE
484 | tE15_ModeProfile1Event3 | * | FALSE
485 | tE16_TimeProfile1Event4 | * | FALSE
486 | tE17_ModeProfile1Event4 | * | FALSE
487 | tE20_TimeProfile2Event1 | * | FALSE
488 | tE21_ModeProfile2Event1 | * | FALSE
489 | tE22_TimeProfile2Event2 | * | FALSE
490 | tE23_ModeProfile2Event2 | * | FALSE
491 | tE24_TimeProfile2Event3 | * | FALSE
492 | tE25_ModeProfile2Event3 | * | FALSE
493 | tE26_TimeProfile2Event4 | * | FALSE
494 | tE27_ModeProfile2Event4 | * | FALSE
495 | TW00_EnableYearEvents | * | FALSE
496 | TW01_EventProfile01 | * | FALSE
497 | TW02_EventProfile02 | * | FALSE
498 | TW03_EventProfile03 | * | FALSE
499 | TW04_EventProfile04 | * | FALSE
500 | TW05_EventProfile05 | * | FALSE
501 | TW06_EventProfile06 | * | FALSE
502 | TW07_EventProfile07 | * | FALSE
503 | TW08_EventProfile08 | * | FALSE
504 | TW09_EventProfile09 | * | FALSE
505 | TW10_EventProfile10 | * | FALSE
506 | TW11_EventProfile11 | * | FALSE
507 | TW12_EventProfile12 | * | FALSE
508 | TW13_EventProfile13 | * | FALSE
509 | TW14_EventProfile14 | * | FALSE
510 | TW15_EventProfile15 | * | FALSE
511 | TW16_EnEvent01 | * | FALSE
512 | TW17_EnEvent02 | * | FALSE
513 | TW18_EnEvent03 | * | FALSE
514 | TW19_EnEvent04 | * | FALSE
515 | TW20_EnEvent05 | * | FALSE
516 | TW21_EnEvent06 | * | FALSE
517 | TW22_EnEvent07 | * | FALSE
518 | TW23_EnEvent08 | * | FALSE
519 | TW24_EnEvent09 | * | FALSE
520 | TW25_EnEvent10 | * | FALSE
521 | TW26_EnEvent11 | * | FALSE
522 | TW27_EnEvent12 | * | FALSE
523 | TW28_EnEvent13 | * | FALSE
524 | TW29_EnEvent14 | * | FALSE
525 | TW30_EnEvent15 | * | FALSE
526 | TW31_EventDDStart01 | * | FALSE
527 | TW32_EventDDStart02 | * | FALSE
528 | TW33_EventDDStart03 | * | FALSE
529 | TW34_EventDDStart04 | * | FALSE
530 | TW35_EventDDStart05 | * | FALSE
531 | TW36_EventDDStart06 | * | FALSE
532 | TW37_EventDDStart07 | * | FALSE
533 | TW38_EventDDStart08 | * | FALSE
534 | TW39_EventDDStart09 | * | FALSE
535 | TW40_EventDDStart10 | * | FALSE
536 | TW41_EventDDStart11 | * | FALSE
537 | TW42_EventDDStart12 | * | FALSE
538 | TW43_EventDDStart13 | * | FALSE
539 | TW44_EventDDStart14 | * | FALSE
540 | TW45_EventDDStart15 | * | FALSE
541 | TW46_EventMMStart01 | * | FALSE
542 | TW47_EventMMStart02 | * | FALSE
543 | TW48_EventMMStart03 | * | FALSE
544 | TW49_EventMMStart04 | * | FALSE
545 | TW50_EventMMStart05 | * | FALSE
546 | TW51_EventMMStart06 | * | FALSE
547 | TW52_EventMMStart07 | * | FALSE
548 | TW53_EventMMStart08 | * | FALSE
549 | TW54_EventMMStart09 | * | FALSE
550 | TW55_EventMMStart10 | * | FALSE
551 | TW56_EventMMStart11 | * | FALSE
552 | TW57_EventMMStart12 | * | FALSE
553 | TW58_EventMMStart13 | * | FALSE
554 | TW59_EventMMStart14 | * | FALSE
555 | TW60_EventMMStart15 | * | FALSE
556 | TW61_EventDDStop01 | * | FALSE
557 | TW62_EventDDStop02 | * | FALSE
558 | TW63_EventDDStop03 | * | FALSE
559 | TW64_EventDDStop04 | * | FALSE
560 | TW65_EventDDStop05 | * | FALSE
561 | TW66_EventDDStop06 | * | FALSE
562 | TW67_EventDDStop07 | * | FALSE
563 | TW68_EventDDStop08 | * | FALSE
564 | TW69_EventDDStop09 | * | FALSE
565 | TW70_EventDDStop10 | * | FALSE
566 | TW71_EventDDStop11 | * | FALSE
567 | TW72_EventDDStop12 | * | FALSE
568 | TW73_EventDDStop13 | * | FALSE
569 | TW74_EventDDStop14 | * | FALSE
570 | TW75_EventDDStop15 | * | FALSE
571 | TW76_EventMMStop01 | * | FALSE
572 | TW77_EventMMStop02 | * | FALSE
573 | TW78_EventMMStop03 | * | FALSE
574 | TW79_EventMMStop04 | * | FALSE
575 | TW80_EventMMStop05 | * | FALSE
576 | TW81_EventMMStop06 | * | FALSE
577 | TW82_EventMMStop07 | * | FALSE
578 | TW83_EventMMStop08 | * | FALSE
579 | TW84_EventMMStop09 | * | FALSE
580 | TW85_EventMMStop10 | * | FALSE
581 | TW86_EventMMStop11 | * | FALSE
582 | TW87_EventMMStop12 | * | FALSE
583 | TW88_EventMMStop13 | * | FALSE
584 | TW89_EventMMStop14 | * | FALSE
585 | TW90_EventMMStop15 | * | FALSE
586 | LASTCONFIGPARAM | * | FALSE
587 | LogData_NextEntry_Code | * | FALSE
588 | LogData_FULL_Code | * | FALSE
589 | LogData_NextEntry_Date | * | FALSE
590 | LogData_FULL_Date | * | FALSE
591 | LogData_NextEntry_Time | * | FALSE
592 | LogData_FULL_Time | * | FALSE
593 | LogData_NextEntry_SecStatus | * | FALSE
594 | LogData_FULL_SecStatus | * | FALSE
595 | LogDataE2_00 | * | FALSE
596 | LogDataE2_01 | * | FALSE
597 | LogDataE2_02 | * | FALSE
598 | LogDataE2_03 | * | FALSE
599 | LogDataE2_04 | * | FALSE
600 | LogDataE2_05 | * | FALSE
601 | LogDataE2_06 | * | FALSE
602 | LogDataE2_07 | * | FALSE
603 | LogDataE2_08 | * | FALSE
604 | LogDataE2_09 | * | FALSE
605 | LogDataE2_10 | * | FALSE
606 | LogDataE2_11 | * | FALSE
607 | LogDataE2_12 | * | FALSE
608 | LogDataE2_13 | * | FALSE
609 | LogDataE2_14 | * | FALSE
610 | LogDataE2_15 | * | FALSE
611 | LogDataE2_16 | * | FALSE
612 | LogDataE2_17 | * | FALSE
613 | LogDataE2_18 | * | FALSE
614 | LogDataE2_19 | * | FALSE
615 | LogDataE2_20 | * | FALSE
616 | LogDataE2_21 | * | FALSE
617 | LogDataE2_22 | * | FALSE
618 | LogDataE2_23 | * | FALSE
619 | LogDataE2_24 | * | FALSE
620 | LogDataE2_25 | * | FALSE
621 | LogDataE2_26 | * | FALSE
622 | LogDataE2_27 | * | FALSE
623 | LogDataE2_28 | * | FALSE
624 | LogDataE2_29 | * | FALSE
625 | LogDataE2_30 | * | FALSE
626 | LogDataE2_31 | * | FALSE
627 | LogDataE2_32 | * | FALSE
628 | LogDataE2_33 | * | FALSE
629 | LogDataE2_34 | * | FALSE
630 | LogDataE2_35 | * | FALSE
631 | LogDataE2_36 | * | FALSE
632 | LogDataE2_37 | * | FALSE
633 | LogDataE2_38 | * | FALSE
634 | LogDataE2_39 | * | FALSE
635 | LogDataE2_40 | * | FALSE
636 | LogDataE2_41 | * | FALSE
637 | LogDataE2_42 | * | FALSE
638 | LogDataE2_43 | * | FALSE
639 | LogDataE2_44 | * | FALSE
640 | LogDataE2_45 | * | FALSE
641 | LogDataE2_46 | * | FALSE
642 | LogDataE2_47 | * | FALSE
643 | LogDataE2_48 | * | FALSE
644 | LogDataE2_49 | * | FALSE
645 | LogDataE2_50 | * | FALSE
646 | LogDataE2_51 | * | FALSE
647 | LogDataE2_52 | * | FALSE
648 | LogDataE2_53 | * | FALSE
649 | LogDataE2_54 | * | FALSE
650 | LogDataE2_55 | * | FALSE
651 | LogDataE2_56 | * | FALSE
652 | LogDataE2_57 | * | FALSE
653 | LogDataE2_58 | * | FALSE
654 | LogDataE2_60 | * | FALSE
655 | LogDataE2_59 | * | FALSE
656 | LogDataE2_61 | * | FALSE
657 | LogDataE2_62 | * | FALSE
658 | LogDataE2_63 | * | FALSE
659 | LogDataE2_64 | * | FALSE
660 | LogDataE2_65 | * | FALSE
661 | LogDataE2_66 | * | FALSE
662 | LogDataE2_67 | * | FALSE
663 | LogDataE2_68 | * | FALSE
664 | LogDataE2_69 | * | FALSE
665 | LogDataE2_70 | * | FALSE
666 | LogDataE2_71 | * | FALSE
667 | LogDataE2_72 | * | FALSE
668 | LogDataE2_73 | * | FALSE
669 | LogDataE2_74 | * | FALSE
670 | LogDataE2_75 | * | FALSE
671 | LogDataE2_76 | * | FALSE
672 | LogDataE2_77 | * | FALSE
673 | LogDataE2_78 | * | FALSE
674 | LogDataE2_79 | * | FALSE
675 | LogDataE2_80 | * | FALSE
676 | LogDataE2_81 | * | FALSE
677 | LogDataE2_82 | * | FALSE
678 | LogDataE2_83 | * | FALSE
679 | LogDataE2_84 | * | FALSE
680 | LogDataE2_85 | * | FALSE
681 | LogDataE2_86 | * | FALSE
682 | LogDataE2_87 | * | FALSE
683 | LogDataE2_89 | * | FALSE
684 | LogDataE2_88 | * | FALSE
685 | LogDataE2_90 | * | FALSE
686 | LogDataE2_91 | * | FALSE
687 | LogDataE2_92 | * | FALSE
688 | LogDataE2_93 | * | FALSE
689 | LogDataE2_94 | * | FALSE
690 | LogDataE2_95 | * | FALSE
691 | LogDataE2_97 | * | FALSE
692 | LogDataE2_96 | * | FALSE
693 | LogDataE2_98 | * | FALSE
694 | LogDataE2_99 | * | FALSE
695 | LogDataE2_100 | * | FALSE
696 | LogDataE2_101 | * | FALSE
697 | LogDataE2_102 | * | FALSE
698 | LogDataE2_103 | * | FALSE
699 | LogDataE2_104 | * | FALSE
700 | LogDataE2_105 | * | FALSE
701 | LogDataE2_106 | * | FALSE
702 | LogDataE2_107 | * | FALSE
703 | LogDataE2_108 | * | FALSE
704 | LogDataE2_109 | * | FALSE
705 | LogDataE2_110 | * | FALSE
706 | LogDataE2_111 | * | FALSE
707 | LogDataE2_112 | * | FALSE
708 | LogDataE2_113 | * | FALSE
709 | LogDataE2_114 | * | FALSE
710 | LogDataE2_115 | * | FALSE
711 | LogDataE2_116 | * | FALSE
712 | LogDataE2_117 | * | FALSE
713 | LogDataE2_118 | * | FALSE
714 | LogDataE2_119 | * | FALSE
715 | LogDataE2_120 | * | FALSE
716 | LogDataE2_121 | * | FALSE
717 | LogDataE2_122 | * | FALSE
718 | LogDataE2_123 | * | FALSE
719 | LogDataE2_124 | * | FALSE
720 | LogDataE2_125 | * | FALSE
721 | LogDataE2_126 | * | FALSE
722 | LogDataE2_127 | * | FALSE
723 | LogDataE2_128 | * | FALSE
724 | LogDataE2_129 | * | FALSE
725 | LogDataE2_130 | * | FALSE
726 | LogDataE2_131 | * | FALSE
727 | LogDataE2_132 | * | FALSE
728 | LogDataE2_133 | * | FALSE
729 | LogDataE2_134 | * | FALSE
730 | LogDataE2_136 | * | FALSE
731 | LogDataE2_137 | * | FALSE
732 | LogDataE2_135 | * | FALSE
733 | LogDataE2_138 | * | FALSE
734 | LogDataE2_139 | * | FALSE
735 | LogDataE2_140 | * | FALSE
736 | LogDataE2_141 | * | FALSE
737 | LogDataE2_142 | * | FALSE
738 | LogDataE2_143 | * | FALSE
739 | LogDataE2_144 | * | FALSE
740 | LogDataE2_145 | * | FALSE
741 | LogDataE2_146 | * | FALSE
742 | LogDataE2_147 | * | FALSE
743 | LogDataE2_148 | * | FALSE
744 | LogDataE2_149 | * | FALSE
745 | LogDataE2_150 | * | FALSE
746 | LogDataE2_151 | * | FALSE
747 | LogDataE2_152 | * | FALSE
748 | LogDataE2_153 | * | FALSE
749 | LogDataE2_154 | * | FALSE
750 | LogDataE2_155 | * | FALSE
751 | LogDataE2_156 | * | FALSE
752 | LogDataE2_158 | * | FALSE
753 | LogDataE2_157 | * | FALSE
754 | LogDataE2_159 | * | FALSE
755 | LogDataE2_160 | * | FALSE
756 | LogDataE2_161 | * | FALSE
757 | LogDataE2_162 | * | FALSE
758 | LogDataE2_163 | * | FALSE
759 | LogDataE2_164 | * | FALSE
760 | LogDataE2_165 | * | FALSE
761 | LogDataE2_166 | * | FALSE
762 | LogDataE2_167 | * | FALSE
763 | LogDataE2_168 | * | FALSE
764 | LogDataE2_169 | * | FALSE
765 | LogDataE2_170 | * | FALSE
766 | LogDataE2_171 | * | FALSE
767 | LogDataE2_172 | * | FALSE
768 | LogDataE2_173 | * | FALSE
769 | LogDataE2_174 | * | FALSE
770 | LogDataE2_175 | * | FALSE
771 | LogDataE2_176 | * | FALSE
772 | LogDataE2_177 | * | FALSE
773 | LogDataE2_178 | * | FALSE
774 | LogDataE2_179 | * | FALSE
775 | LogDataE2_180 | * | FALSE
776 | LogDataE2_181 | * | FALSE
777 | LogDataE2_182 | * | FALSE
778 | LogDataE2_183 | * | FALSE
779 | LogDataE2_184 | * | FALSE
780 | LogDataE2_185 | * | FALSE
781 | LogDataE2_186 | * | FALSE
782 | LogDataE2_187 | * | FALSE
783 | LogDataE2_188 | * | FALSE
784 | LogDataE2_189 | * | FALSE
785 | LogDataE2_190 | * | FALSE
786 | LogDataE2_191 | * | FALSE
787 | LogDataE2_192 | * | FALSE
788 | LogDataE2_193 | * | FALSE
789 | LogDataE2_194 | * | FALSE
790 | LogDataE2_195 | * | FALSE
791 | LogDataE2_196 | * | FALSE
792 | LogDataE2_197 | * | FALSE
793 | LogDataE2_198 | * | FALSE
794 | LogDataE2_199 | * | FALSE
795 | UNIT_SERIAL_NUMBER1 | * | FALSE
796 | UNIT_SERIAL_NUMBER2 | * | FALSE
797 | ENDHISTORICAL | * | FALSE
798 | Unit_KbdOnOff | * | FALSE
799 | Unit_KbdMode_E2 | * | FALSE
800 | Unit_KbdEco_E2 | * | FALSE
801 | TW_ActiveEvent | * | FALSE
802 | EE_RTCerror | * | FALSE
803 | ENDINTERNAL | * | FALSE
804 | UnitHoursE2 | * | FALSE
805 | FanSupplyHoursE2 | * | FALSE
806 | FanReturnHoursE2 | * | FALSE
807 | FanSupplyBckHoursE2 | * | FALSE
808 | FanReturnBckHoursE2 | * | FALSE
809 | Fan_Maintenance_Supply | * | FALSE
810 | Fan_Maintenance_Return | * | FALSE
811 | Fan_Maintenance_SupplyBck | * | FALSE
812 | Fan_Maintenance_ReturnBck | * | FALSE
813 | Fan_Maintenance_Supply1b | * | FALSE
814 | Fan_Maintenance_Supply1c | * | FALSE
815 | Fan_Maintenance_Return1b | * | FALSE
816 | Fan_Maintenance_Return1c | * | FALSE
817 | Fan_Maintenance_Supply2b | * | FALSE
818 | Fan_Maintenance_Supply2c | * | FALSE
819 | Fan_Maintenance_Return2b | * | FALSE
820 | Fan_Maintenance_Return2c | * | FALSE
821 | Fan_Modbus_Configured_E2 | * | FALSE
822 | udhoursCU1E2 | * | FALSE
823 | udhoursCU2E2 | * | FALSE
824 | udhoursCU3E2 | * | FALSE
825 | udhoursCU4E2 | * | FALSE
826 | CU1_Maintenance | * | FALSE
827 | CU2_Maintenance | * | FALSE
828 | CU3_Maintenance | * | FALSE
829 | CU4_Maintenance | * | FALSE
830 | BACNET_SUBNET | * | FALSE
Note on B1: HELP: Try to keep the lenght to no more than 3 chars. Use ENGLISH abbreviations.

## Params
INDEX | LABEL | DESCRIPTION | DESCRIPTION_CODE | PROGRESSIVE | CATEGORY | GROUPS | LOW_LIMIT | HIGH_LIMIT | FORMAT | COMPLEMENTED | MEASUREMENT_UNIT | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER | R_W_RW | VISIBILITY_LEVEL | WORD_INDEX | WORD_FILTER | CUSTOM_MODEL | ID | TELEVIS_PROPERTIES | OPTIONS | MARCOMM_MANUAL | PARAMETER_TYPE
1 | PSW1 | Level 1 Password | CUS40000 | PSW1 | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16383 | HFFFF | RW
2 | PSW2 | Level 2 Password | CUS40000 | PSW2 | PH | PGR00000 | 0 | 65535 | %x |  | FIX(VMU00020) |  |  |  | P | 16384 | HFFFF | RW
3 | cfgFans | OEM: Fan Sections | CUS40000 | cfgFans | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16385 | HFFFF | RW
4 | cfgFanType | OEM: Fan Type | CUS40000 | cfgFanType | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16386 | HFFFF | RW
5 | cfgFanRegulation | OEM: Fan Regulator | CUS40000 | cfgFanRegulation | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16387 | HFFFF | RW
6 | cfgFanAlarm | OEM: Fan Alarm Selection | CUS40000 | cfgFanAlarm | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16388 | HFFFF | RW
7 | cfgCoolHeatModules | OEM: Heating Cooling Enable | CUS40000 | cfgCoolHeatModules | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16389 | HFFFF | RW
8 | cfgCooling | OEM: Cooling Actuator Selection | CUS40000 | cfgCooling | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16390 | HFFFF | RW
9 | cfgHeating | OEM: Heating Actuator Selection | CUS40000 | cfgHeating | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16391 | HFFFF | RW
10 | cfgCooling_Heating | OEM: Cooling+Heating Actuator Selection | CUS40000 | cfgCooling_Heating | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16392 | HFFFF | RW
11 | cfgPreHeating | OEM: Preheater Selection | CUS40000 | cfgPreHeating | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16393 | HFFFF | RW
12 | cfgPostHeating | OEM: Postheater Selection | CUS40000 | cfgPostHeating | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16394 | HFFFF | RW
13 | cfgAntifreeze | OEM: Antifreeze Selection | CUS40000 | cfgAntifreeze | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16395 | HFFFF | RW
14 | cfgHeatRecovery | OEM: Heat Recovery Selection | CUS40000 | cfgHeatRecovery | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16396 | HFFFF | RW
15 | cfgDefrostHeatRec | OEM: Defrost Regulation Selection | CUS40000 | cfgDefrostHeatRec | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16397 | HFFFF | RW
16 | cfgDampers | OEM: External Dampers Selection | CUS40000 | cfgDampers | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16398 | HFFFF | RW
17 | cfgHumidifier | OEM: Humidifier Selection | CUS40000 | cfgHumidifier | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16399 | HFFFF | RW
18 | cfgDeHumidifier | OEM: Dehumification Regulator | CUS40000 | cfgDeHumidifier | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16400 | HFFFF | RW
19 | cfgDampersForFans | OEM: Dampers for fam Selection | CUS40000 | cfgDampersForFans | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16401 | HFFFF | RW
20 | cfgAirQuality | OEM: Air Quality Probe Selection | CUS40000 | cfgAirQuality | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16402 | HFFFF | RW
21 | cfgFilterPressostat | OEM: Number of filter pressostat | CUS40000 | cfgFilterPressostat | PH | PGR00000 | 0 | 5 |  |  | FIX(VMU00020) |  |  |  | P | 16403 | HFFFF | RW
22 | cfgDoorDI | OEM: Door Input Enable | CUS40000 | cfgDoorDI | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16404 | HFFFF | RW
23 | cfgModeDI | OEM: Unit Mode Input Enable | CUS40000 | cfgModeDI | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16405 | HFFFF | RW
24 | cfgModeDO | OEM: Unit Mode Output Enable | CUS40000 | cfgModeDO | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16406 | HFFFF | RW
25 | cfgCoolHeat_NumSteps | OEM: Condensing Unit Steps | CUS40000 | cfgCoolHeat_NumSteps | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16407 | HFFFF | RW
26 | cfgHeat_NumSteps | OEM: Electric Heater Steps | CUS40000 | cfgHeat_NumSteps | PH | PGR00000 | 0 | 6 |  |  | FIX(VMU00020) |  |  |  | P | 16408 | HFFFF | RW
27 | cfgPreHeat_NumSteps | OEM: Electric Pre Heater Steps | CUS40000 | cfgPreHeat_NumSteps | PH | PGR00000 | 0 | 6 |  |  | FIX(VMU00020) |  |  |  | P | 16409 | HFFFF | RW
28 | cfgPostHeat_NumSteps | OEM: Electric Post Heater Steps | CUS40000 | cfgPostHeat_NumSteps | PH | PGR00000 | 0 | 6 |  |  | FIX(VMU00020) |  |  |  | P | 16410 | HFFFF | RW
29 | cfgMixChamberBeforePreHeat | OEM: If enabled dampers closed with PreAntifreeze and Defrost with PreHeating | CUS40000 | cfgMixChamberBeforePreHeat | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16411 | HFFFF | RW
30 | CfgParallelFans | OEM: Number of parallel fans (Ziehl only) | CUS40000 | CfgParallelFans | PH | PGR00000 | 1 | 3 |  |  | FIX(VMU00020) |  |  |  | P | 16412 | HFFFF | RW
31 | cfgEE_free3 |  | CUS40000 | cfgEE_free3 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16413 | HFFFF | RW
32 | cfgEE_free4 |  | CUS40000 | cfgEE_free4 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16414 | HFFFF | RW
33 | cfgEE_free5 |  | CUS40000 | cfgEE_free5 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16415 | HFFFF | RW
34 | cfgEE_free6 |  | CUS40000 | cfgEE_free6 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16416 | HFFFF | RW
35 | cfgEE_free7 |  | CUS40000 | cfgEE_free7 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16417 | HFFFF | RW
36 | cfgEE_free8 |  | CUS40000 | cfgEE_free8 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16418 | HFFFF | RW
37 | ioEE_base_AI_01 | Saved Logic Allocation of the physical input | CUS40000 | ioEE_base_AI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16419 | HFFFF | RW
38 | ioEE_base_AI_02 |  | CUS40000 | ioEE_base_AI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16420 | HFFFF | RW
39 | ioEE_base_AI_03 |  | CUS40000 | ioEE_base_AI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16421 | HFFFF | RW
40 | ioEE_base_AI_04 |  | CUS40000 | ioEE_base_AI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16422 | HFFFF | RW
41 | ioEE_base_AI_05 |  | CUS40000 | ioEE_base_AI_05 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16423 | HFFFF | RW
42 | ioEE_base_AI_06 |  | CUS40000 | ioEE_base_AI_06 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16424 | HFFFF | RW
43 | ioEE_base_AI_07 |  | CUS40000 | ioEE_base_AI_07 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16425 | HFFFF | RW
44 | ioEE_base_AI_08 |  | CUS40000 | ioEE_base_AI_08 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16426 | HFFFF | RW
45 | ioEE_base_AI_09 |  | CUS40000 | ioEE_base_AI_09 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16427 | HFFFF | RW
46 | ioEE_base_AI_10 |  | CUS40000 | ioEE_base_AI_10 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16428 | HFFFF | RW
47 | ioEE_base_AI_11 |  | CUS40000 | ioEE_base_AI_11 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16429 | HFFFF | RW
48 | ioEE_base_AI_12 |  | CUS40000 | ioEE_base_AI_12 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16430 | HFFFF | RW
49 | ioEE_exp1_AI_01 |  | CUS40000 | ioEE_exp1_AI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16431 | HFFFF | RW
50 | ioEE_exp1_AI_02 |  | CUS40000 | ioEE_exp1_AI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16432 | HFFFF | RW
51 | ioEE_exp1_AI_03 |  | CUS40000 | ioEE_exp1_AI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16433 | HFFFF | RW
52 | ioEE_exp1_AI_04 |  | CUS40000 | ioEE_exp1_AI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16434 | HFFFF | RW
53 | ioEE_exp2_AI_01 |  | CUS40000 | ioEE_exp2_AI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16435 | HFFFF | RW
54 | ioEE_exp2_AI_02 |  | CUS40000 | ioEE_exp2_AI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16436 | HFFFF | RW
55 | ioEE_exp2_AI_03 |  | CUS40000 | ioEE_exp2_AI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16437 | HFFFF | RW
56 | ioEE_exp2_AI_04 |  | CUS40000 | ioEE_exp2_AI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16438 | HFFFF | RW
57 | ioEE_free1 |  | CUS40000 | ioEE_free1 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16439 | HFFFF | RW
58 | ioEE_free2 |  | CUS40000 | ioEE_free2 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16440 | HFFFF | RW
59 | ioEE_free3 |  | CUS40000 | ioEE_free3 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16441 | HFFFF | RW
60 | ioEE_free4 |  | CUS40000 | ioEE_free4 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16442 | HFFFF | RW
61 | ioEE_free5 |  | CUS40000 | ioEE_free5 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16443 | HFFFF | RW
62 | ioEE_free6 |  | CUS40000 | ioEE_free6 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16444 | HFFFF | RW
63 | ioEE_free7 |  | CUS40000 | ioEE_free7 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16445 | HFFFF | RW
64 | ioEE_free8 |  | CUS40000 | ioEE_free8 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16446 | HFFFF | RW
65 | ioEE_base_DI_01 |  | CUS40000 | ioEE_base_DI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16447 | HFFFF | RW
66 | ioEE_base_DI_02 |  | CUS40000 | ioEE_base_DI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16448 | HFFFF | RW
67 | ioEE_base_DI_03 |  | CUS40000 | ioEE_base_DI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16449 | HFFFF | RW
68 | ioEE_base_DI_04 |  | CUS40000 | ioEE_base_DI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16450 | HFFFF | RW
69 | ioEE_base_DI_05 |  | CUS40000 | ioEE_base_DI_05 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16451 | HFFFF | RW
70 | ioEE_base_DI_06 |  | CUS40000 | ioEE_base_DI_06 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16452 | HFFFF | RW
71 | ioEE_base_DI_07 |  | CUS40000 | ioEE_base_DI_07 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16453 | HFFFF | RW
72 | ioEE_base_DI_08 |  | CUS40000 | ioEE_base_DI_08 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16454 | HFFFF | RW
73 | ioEE_base_DI_09 |  | CUS40000 | ioEE_base_DI_09 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16455 | HFFFF | RW
74 | ioEE_base_DI_10 |  | CUS40000 | ioEE_base_DI_10 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16456 | HFFFF | RW
75 | ioEE_base_DI_11 |  | CUS40000 | ioEE_base_DI_11 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16457 | HFFFF | RW
76 | ioEE_base_DI_12 |  | CUS40000 | ioEE_base_DI_12 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16458 | HFFFF | RW
77 | ioEE_exp1_DI_01 |  | CUS40000 | ioEE_exp1_DI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16459 | HFFFF | RW
78 | ioEE_exp1_DI_02 |  | CUS40000 | ioEE_exp1_DI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16460 | HFFFF | RW
79 | ioEE_exp1_DI_03 |  | CUS40000 | ioEE_exp1_DI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16461 | HFFFF | RW
80 | ioEE_exp1_DI_04 |  | CUS40000 | ioEE_exp1_DI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16462 | HFFFF | RW
81 | ioEE_exp2_DI_01 |  | CUS40000 | ioEE_exp2_DI_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16463 | HFFFF | RW
82 | ioEE_exp2_DI_02 |  | CUS40000 | ioEE_exp2_DI_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16464 | HFFFF | RW
83 | ioEE_exp2_DI_03 |  | CUS40000 | ioEE_exp2_DI_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16465 | HFFFF | RW
84 | ioEE_exp2_DI_04 |  | CUS40000 | ioEE_exp2_DI_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16466 | HFFFF | RW
85 | ioEE_free9 |  | CUS40000 | ioEE_free9 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16467 | HFFFF | RW
86 | ioEE_free10 |  | CUS40000 | ioEE_free10 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16468 | HFFFF | RW
87 | ioEE_free11 |  | CUS40000 | ioEE_free11 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16469 | HFFFF | RW
88 | ioEE_free12 |  | CUS40000 | ioEE_free12 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16470 | HFFFF | RW
89 | ioEE_free13 |  | CUS40000 | ioEE_free13 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16471 | HFFFF | RW
90 | ioEE_free14 |  | CUS40000 | ioEE_free14 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16472 | HFFFF | RW
91 | ioEE_free15 |  | CUS40000 | ioEE_free15 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16473 | HFFFF | RW
92 | ioEE_free16 |  | CUS40000 | ioEE_free16 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16474 | HFFFF | RW
93 | ioEE_base_DO_01 | Saved Logic Allocation of the physical output | CUS40000 | ioEE_base_DO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16475 | HFFFF | RW
94 | ioEE_base_DO_02 |  | CUS40000 | ioEE_base_DO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16476 | HFFFF | RW
95 | ioEE_base_DO_03 |  | CUS40000 | ioEE_base_DO_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16477 | HFFFF | RW
96 | ioEE_base_DO_04 |  | CUS40000 | ioEE_base_DO_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16478 | HFFFF | RW
97 | ioEE_base_DO_05 |  | CUS40000 | ioEE_base_DO_05 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16479 | HFFFF | RW
98 | ioEE_base_DO_06 |  | CUS40000 | ioEE_base_DO_06 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16480 | HFFFF | RW
99 | ioEE_base_DO_07 |  | CUS40000 | ioEE_base_DO_07 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16481 | HFFFF | RW
100 | ioEE_base_DO_08 |  | CUS40000 | ioEE_base_DO_08 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16482 | HFFFF | RW
101 | ioEE_base_DO_09 |  | CUS40000 | ioEE_base_DO_09 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16483 | HFFFF | RW
102 | ioEE_base_DO_10 |  | CUS40000 | ioEE_base_DO_10 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16484 | HFFFF | RW
103 | ioEE_base_DO_11 |  | CUS40000 | ioEE_base_DO_11 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16485 | HFFFF | RW
104 | ioEE_base_DO_12 |  | CUS40000 | ioEE_base_DO_12 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16486 | HFFFF | RW
105 | ioEE_exp1_DO_01 |  | CUS40000 | ioEE_exp1_DO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16487 | HFFFF | RW
106 | ioEE_exp1_DO_02 |  | CUS40000 | ioEE_exp1_DO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16488 | HFFFF | RW
107 | ioEE_exp1_DO_03 |  | CUS40000 | ioEE_exp1_DO_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16489 | HFFFF | RW
108 | ioEE_exp1_DO_04 |  | CUS40000 | ioEE_exp1_DO_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16490 | HFFFF | RW
109 | ioEE_exp2_DO_01 |  | CUS40000 | ioEE_exp2_DO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16491 | HFFFF | RW
110 | ioEE_exp2_DO_02 |  | CUS40000 | ioEE_exp2_DO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16492 | HFFFF | RW
111 | ioEE_exp2_DO_03 |  | CUS40000 | ioEE_exp2_DO_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16493 | HFFFF | RW
112 | ioEE_exp2_DO_04 |  | CUS40000 | ioEE_exp2_DO_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16494 | HFFFF | RW
113 | ioEE_free17 |  | CUS40000 | ioEE_free17 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16495 | HFFFF | RW
114 | ioEE_free18 |  | CUS40000 | ioEE_free18 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16496 | HFFFF | RW
115 | ioEE_free19 |  | CUS40000 | ioEE_free19 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16497 | HFFFF | RW
116 | ioEE_free20 |  | CUS40000 | ioEE_free20 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16498 | HFFFF | RW
117 | ioEE_free21 |  | CUS40000 | ioEE_free21 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16499 | HFFFF | RW
118 | ioEE_free22 |  | CUS40000 | ioEE_free22 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16500 | HFFFF | RW
119 | ioEE_free23 |  | CUS40000 | ioEE_free23 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16501 | HFFFF | RW
120 | ioEE_free24 |  | CUS40000 | ioEE_free24 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16502 | HFFFF | RW
121 | ioEE_base_AO_01 |  | CUS40000 | ioEE_base_AO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16503 | HFFFF | RW
122 | ioEE_base_AO_02 |  | CUS40000 | ioEE_base_AO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16504 | HFFFF | RW
123 | ioEE_base_AO_03 |  | CUS40000 | ioEE_base_AO_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16505 | HFFFF | RW
124 | ioEE_base_AO_04 |  | CUS40000 | ioEE_base_AO_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16506 | HFFFF | RW
125 | ioEE_base_AO_05 |  | CUS40000 | ioEE_base_AO_05 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16507 | HFFFF | RW
126 | ioEE_base_AO_06 |  | CUS40000 | ioEE_base_AO_06 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16508 | HFFFF | RW
127 | ioEE_exp1_AO_01 |  | CUS40000 | ioEE_exp1_AO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16509 | HFFFF | RW
128 | ioEE_exp1_AO_02 |  | CUS40000 | ioEE_exp1_AO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16510 | HFFFF | RW
129 | ioEE_exp2_AO_01 |  | CUS40000 | ioEE_exp2_AO_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16511 | HFFFF | RW
130 | ioEE_exp2_AO_02 |  | CUS40000 | ioEE_exp2_AO_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16512 | HFFFF | RW
131 | ioEE_free25 |  | CUS40000 | ioEE_free25 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16513 | HFFFF | RW
132 | ioEE_free26 |  | CUS40000 | ioEE_free26 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16514 | HFFFF | RW
133 | ioEE_free27 |  | CUS40000 | ioEE_free27 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16515 | HFFFF | RW
134 | ioEE_free28 |  | CUS40000 | ioEE_free28 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16516 | HFFFF | RW
135 | ioEE_free29 |  | CUS40000 | ioEE_free29 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16517 | HFFFF | RW
136 | ioEE_free30 |  | CUS40000 | ioEE_free30 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16518 | HFFFF | RW
137 | ioEE_free31 |  | CUS40000 | ioEE_free31 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16519 | HFFFF | RW
138 | ioEE_free32 |  | CUS40000 | ioEE_free32 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16520 | HFFFF | RW
139 | Cfg_exp1_AI1 | Static Configuration | CUS40000 | Cfg_exp1_AI1 | PH | PGR00000 | 2 | 2 |  |  | FIX(VMU00020) |  |  |  | P | 16521 | HFFFF | RW
140 | Cfg_exp1_AI2 | Static Configuration | CUS40000 | Cfg_exp1_AI2 | PH | PGR00000 | 2 | 2 |  |  | FIX(VMU00020) |  |  |  | P | 16522 | HFFFF | RW
141 | Cfg_exp1_AI3 | Static Configuration | CUS40000 | Cfg_exp1_AI3 | PH | PGR00000 | 4 | 4 |  |  | FIX(VMU00020) |  |  |  | P | 16523 | HFFFF | RW
142 | Cfg_exp1_AI4 | Static Configuration | CUS40000 | Cfg_exp1_AI4 | PH | PGR00000 | 4 | 4 |  |  | FIX(VMU00020) |  |  |  | P | 16524 | HFFFF | RW
143 | Cfg_exp2_AI1 | Static Configuration | CUS40000 | Cfg_exp2_AI1 | PH | PGR00000 | 2 | 2 |  |  | FIX(VMU00020) |  |  |  | P | 16525 | HFFFF | RW
144 | Cfg_exp2_AI2 | Static Configuration | CUS40000 | Cfg_exp2_AI2 | PH | PGR00000 | 2 | 2 |  |  | FIX(VMU00020) |  |  |  | P | 16526 | HFFFF | RW
145 | Cfg_exp2_AI3 | Static Configuration | CUS40000 | Cfg_exp2_AI3 | PH | PGR00000 | 4 | 4 |  |  | FIX(VMU00020) |  |  |  | P | 16527 | HFFFF | RW
146 | Cfg_exp2_AI4 | Static Configuration | CUS40000 | Cfg_exp2_AI4 | PH | PGR00000 | 4 | 4 |  |  | FIX(VMU00020) |  |  |  | P | 16528 | HFFFF | RW
147 | ioEE_free33 |  | CUS40000 | ioEE_free33 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16529 | HFFFF | RW
148 | ioEE_free34 |  | CUS40000 | ioEE_free34 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16530 | HFFFF | RW
149 | ioEE_free35 |  | CUS40000 | ioEE_free35 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16531 | HFFFF | RW
150 | ioEE_free36 |  | CUS40000 | ioEE_free36 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16532 | HFFFF | RW
151 | ioEE_free37 |  | CUS40000 | ioEE_free37 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16533 | HFFFF | RW
152 | ioEE_free38 |  | CUS40000 | ioEE_free38 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16534 | HFFFF | RW
153 | ioEE_free39 |  | CUS40000 | ioEE_free39 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16535 | HFFFF | RW
154 | ioEE_free40 |  | CUS40000 | ioEE_free40 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16536 | HFFFF | RW
155 | FullScaleMin_exp1_AI1 | Saved: AI probe configuration | CUS40000 | FullScaleMin_exp1_AI1 | PH | PGR00000 | -500 | -500 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16537 | HFFFF | RW
156 | FullScaleMax_exp1_AI1 |  | CUS40000 | FullScaleMax_exp1_AI1 | PH | PGR00000 | 1100 | 1100 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16538 | HFFFF | RW
157 | FullScaleMin_exp1_AI2 |  | CUS40000 | FullScaleMin_exp1_AI2 | PH | PGR00000 | -500 | -500 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16539 | HFFFF | RW
158 | FullScaleMax_exp1_AI2 |  | CUS40000 | FullScaleMax_exp1_AI2 | PH | PGR00000 | 1100 | 1100 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16540 | HFFFF | RW
159 | FullScaleMin_exp1_AI3 |  | CUS40000 | FullScaleMin_exp1_AI3 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16541 | HFFFF | RW
160 | FullScaleMax_exp1_AI3 |  | CUS40000 | FullScaleMax_exp1_AI3 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16542 | HFFFF | RW
161 | FullScaleMin_exp1_AI4 |  | CUS40000 | FullScaleMin_exp1_AI4 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16543 | HFFFF | RW
162 | FullScaleMax_exp1_AI4 |  | CUS40000 | FullScaleMax_exp1_AI4 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16544 | HFFFF | RW
163 | FullScaleMin_exp2_AI1 |  | CUS40000 | FullScaleMin_exp2_AI1 | PH | PGR00000 | -500 | -500 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16545 | HFFFF | RW
164 | FullScaleMax_exp2_AI1 |  | CUS40000 | FullScaleMax_exp2_AI1 | PH | PGR00000 | 1100 | 1100 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16546 | HFFFF | RW
165 | FullScaleMin_exp2_AI2 |  | CUS40000 | FullScaleMin_exp2_AI2 | PH | PGR00000 | -500 | -500 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16547 | HFFFF | RW
166 | FullScaleMax_exp2_AI2 |  | CUS40000 | FullScaleMax_exp2_AI2 | PH | PGR00000 | 1100 | 1100 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16548 | HFFFF | RW
167 | FullScaleMin_exp2_AI3 |  | CUS40000 | FullScaleMin_exp2_AI3 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16549 | HFFFF | RW
168 | FullScaleMax_exp2_AI3 |  | CUS40000 | FullScaleMax_exp2_AI3 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16550 | HFFFF | RW
169 | FullScaleMin_exp2_AI4 |  | CUS40000 | FullScaleMin_exp2_AI4 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16551 | HFFFF | RW
170 | FullScaleMax_exp2_AI4 |  | CUS40000 | FullScaleMax_exp2_AI4 | PH | PGR00000 | -9999 | 9999 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16552 | HFFFF | RW
171 | ioEE_free41 |  | CUS40000 | ioEE_free41 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16553 | HFFFF | RW
172 | ioEE_free42 |  | CUS40000 | ioEE_free42 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16554 | HFFFF | RW
173 | ioEE_free43 |  | CUS40000 | ioEE_free43 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16555 | HFFFF | RW
174 | ioEE_free44 |  | CUS40000 | ioEE_free44 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16556 | HFFFF | RW
175 | ioEE_free45 |  | CUS40000 | ioEE_free45 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16557 | HFFFF | RW
176 | ioEE_free46 |  | CUS40000 | ioEE_free46 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16558 | HFFFF | RW
177 | ioEE_free47 |  | CUS40000 | ioEE_free47 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16559 | HFFFF | RW
178 | ioEE_free48 |  | CUS40000 | ioEE_free48 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16560 | HFFFF | RW
179 | ioEE_free57 |  | CUS40000 | ioEE_free57 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16561 | HFFFF | RW
180 | ioEE_free58 |  | CUS40000 | ioEE_free58 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16562 | HFFFF | RW
181 | ioEE_free59 |  | CUS40000 | ioEE_free59 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16563 | HFFFF | RW
182 | ioEE_free60 |  | CUS40000 | ioEE_free60 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16564 | HFFFF | RW
183 | ioEE_free61 |  | CUS40000 | ioEE_free61 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16565 | HFFFF | RW
184 | ioEE_free62 |  | CUS40000 | ioEE_free62 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16566 | HFFFF | RW
185 | ioEE_free63 |  | CUS40000 | ioEE_free63 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16567 | HFFFF | RW
186 | ioEE_free64 |  | CUS40000 | ioEE_free64 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16568 | HFFFF | RW
187 | Calibration_exp1_AI1 | Offset of expansions AI | CUS40000 | Calibration_exp1_AI1 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16569 | HFFFF | RW
188 | Calibration_exp1_AI2 |  | CUS40000 | Calibration_exp1_AI2 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16570 | HFFFF | RW
189 | Calibration_exp1_AI3 |  | CUS40000 | Calibration_exp1_AI3 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16571 | HFFFF | RW
190 | Calibration_exp1_AI4 |  | CUS40000 | Calibration_exp1_AI4 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16572 | HFFFF | RW
191 | Calibration_exp2_AI1 |  | CUS40000 | Calibration_exp2_AI1 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16573 | HFFFF | RW
192 | Calibration_exp2_AI2 |  | CUS40000 | Calibration_exp2_AI2 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16574 | HFFFF | RW
193 | Calibration_exp2_AI3 |  | CUS40000 | Calibration_exp2_AI3 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16575 | HFFFF | RW
194 | Calibration_exp2_AI4 |  | CUS40000 | Calibration_exp2_AI4 | PH | PGR00000 | -1000 | 1000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16576 | HFFFF | RW
195 | ioEE_free49 |  | CUS40000 | ioEE_free49 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16577 | HFFFF | RW
196 | ioEE_free50 |  | CUS40000 | ioEE_free50 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16578 | HFFFF | RW
197 | ioEE_free51 |  | CUS40000 | ioEE_free51 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16579 | HFFFF | RW
198 | ioEE_free52 |  | CUS40000 | ioEE_free52 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16580 | HFFFF | RW
199 | ioEE_free53 |  | CUS40000 | ioEE_free53 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16581 | HFFFF | RW
200 | ioEE_free54 |  | CUS40000 | ioEE_free54 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16582 | HFFFF | RW
201 | ioEE_free55 |  | CUS40000 | ioEE_free55 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16583 | HFFFF | RW
202 | ioEE_free56 |  | CUS40000 | ioEE_free56 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16584 | HFFFF | RW
203 | DI_Polarity_LogicIndex_0 | Polarity - Supply Fan Thermal | CUS40000 | DI_Polarity_LogicIndex_0 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16585 | HFFFF | RW
204 | DI_Polarity_LogicIndex_1 | Polarity - Return Fan Thermal | CUS40000 | DI_Polarity_LogicIndex_1 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16586 | HFFFF | RW
205 | DI_Polarity_LogicIndex_2 | Polarity - On/Off Input | CUS40000 | DI_Polarity_LogicIndex_2 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16587 | HFFFF | RW
206 | DI_Polarity_LogicIndex_3 | Polarity - Fire Alarm | CUS40000 | DI_Polarity_LogicIndex_3 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16588 | HFFFF | RW
207 | DI_Polarity_LogicIndex_4 | Polarity - Mode Input | CUS40000 | DI_Polarity_LogicIndex_4 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16589 | HFFFF | RW
208 | DI_Polarity_LogicIndex_5 | Polarity - Door | CUS40000 | DI_Polarity_LogicIndex_5 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16590 | HFFFF | RW
209 | DI_Polarity_LogicIndex_6 | Polarity - Antifreeze | CUS40000 | DI_Polarity_LogicIndex_6 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16591 | HFFFF | RW
210 | DI_Polarity_LogicIndex_7 | Polarity - Supply Airflow | CUS40000 | DI_Polarity_LogicIndex_7 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16592 | HFFFF | RW
211 | DI_Polarity_LogicIndex_8 | Polarity - Return Airflow | CUS40000 | DI_Polarity_LogicIndex_8 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16593 | HFFFF | RW
212 | DI_Polarity_LogicIndex_9 | Polarity - Humidifier Alarm | CUS40000 | DI_Polarity_LogicIndex_9 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16594 | HFFFF | RW
213 | DI_Polarity_LogicIndex_10 | Polarity - Preheater Alarm | CUS40000 | DI_Polarity_LogicIndex_10 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16595 | HFFFF | RW
214 | DI_Polarity_LogicIndex_11 | Polarity - Postheater Alarm | CUS40000 | DI_Polarity_LogicIndex_11 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16596 | HFFFF | RW
215 | DI_Polarity_LogicIndex_12 | Polarity - Rotary Wheel Alarm | CUS40000 | DI_Polarity_LogicIndex_12 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16597 | HFFFF | RW
216 | DI_Polarity_LogicIndex_13 | Polarity - Filter 1 Alarm | CUS40000 | DI_Polarity_LogicIndex_13 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16598 | HFFFF | RW
217 | DI_Polarity_LogicIndex_14 | Polarity - Filter 2 Alarm | CUS40000 | DI_Polarity_LogicIndex_14 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16599 | HFFFF | RW
218 | DI_Polarity_LogicIndex_15 | Polarity - Filter 3 Alarm | CUS40000 | DI_Polarity_LogicIndex_15 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16600 | HFFFF | RW
219 | DI_Polarity_LogicIndex_16 | Polarity - Filter 4 Alarm | CUS40000 | DI_Polarity_LogicIndex_16 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16601 | HFFFF | RW
220 | DI_Polarity_LogicIndex_17 | Polarity - Supply 2 Fan Th. | CUS40000 | DI_Polarity_LogicIndex_17 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16602 | HFFFF | RW
221 | DI_Polarity_LogicIndex_18 | Polarity - Return 2 Fan Th. | CUS40000 | DI_Polarity_LogicIndex_18 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16603 | HFFFF | RW
222 | DI_Polarity_LogicIndex_19 | Polarity - Supply 2 Airflow | CUS40000 | DI_Polarity_LogicIndex_19 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16604 | HFFFF | RW
223 | DI_Polarity_LogicIndex_20 | Polarity - Return 2 Airflow | CUS40000 | DI_Polarity_LogicIndex_20 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16605 | HFFFF | RW
224 | DI_Polarity_LogicIndex_21 | Polarity - Cond. Unit Alarm | CUS40000 | DI_Polarity_LogicIndex_21 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16606 | HFFFF | RW
225 | DI_Polarity_LogicIndex_22 | Polarity - El. Heater Alarm | CUS40000 | DI_Polarity_LogicIndex_22 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16607 | HFFFF | RW
226 | DI_Polarity_LogicIndex_26_29 | Polarity - Cond. Unit Defrost | CUS40000 | DI_Polarity_LogicIndex_26_29 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16608 | HFFFF | RW
227 | DI_Polarity_LogicIndex_30 | Polarity - Filter 5 Alarm | CUS40000 | DI_Polarity_LogicIndex_30 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16609 | HFFFF | RW
228 | DI_Polarity_Free2 | Polarity - | CUS40000 | DI_Polarity_Free2 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16610 | HFFFF | RW
229 | DI_Polarity_Free3 | Polarity - | CUS40000 | DI_Polarity_Free3 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16611 | HFFFF | RW
230 | DI_Polarity_Free4 | Polarity - | CUS40000 | DI_Polarity_Free4 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16612 | HFFFF | RW
231 | DI_Polarity_Free5 | Polarity - | CUS40000 | DI_Polarity_Free5 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16613 | HFFFF | RW
232 | DO_Polarity_LogicIndex_0 | Supply Fan - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_0 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16614 | HFFFF | RW
233 | DO_Polarity_LogicIndex_1 | Return Fan - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_1 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16615 | HFFFF | RW
234 | DO_Polarity_LogicIndex_2 | On Off - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_2 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16616 | HFFFF | RW
235 | DO_Polarity_LogicIndex_3 | Alarm - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_3 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16617 | HFFFF | RW
236 | DO_Polarity_LogicIndex_4 | Mode - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_4 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16618 | HFFFF | RW
237 | DO_Polarity_LogicIndex_5 | Ext. Dampers - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_5 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16619 | HFFFF | RW
238 | DO_Polarity_LogicIndex_6 | Bypass Damper - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_6 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16620 | HFFFF | RW
239 | DO_Polarity_LogicIndex_7 | Supply Damper - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_7 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16621 | HFFFF | RW
240 | DO_Polarity_LogicIndex_8 | Return Damper - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_8 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16622 | HFFFF | RW
241 | DO_Polarity_LogicIndex_9 | Pump Preheat - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_9 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16623 | HFFFF | RW
242 | DO_Polarity_LogicIndex_10 | Pump Postheat - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_10 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16624 | HFFFF | RW
243 | DO_Polarity_LogicIndex_11 | Cool/CH Pump - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_11 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16625 | HFFFF | RW
244 | DO_Polarity_LogicIndex_12 | Cool/CH Step 1 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_12 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16626 | HFFFF | RW
245 | DO_Polarity_LogicIndex_13 | Cool/CH Step 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_13 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16627 | HFFFF | RW
246 | DO_Polarity_LogicIndex_14 | Cool/CH Step 3 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_14 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16628 | HFFFF | RW
247 | DO_Polarity_LogicIndex_15 | Cool/CH Step 4 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_15 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16629 | HFFFF | RW
248 | DO_Polarity_LogicIndex_16 | Pump heat - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_16 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16630 | HFFFF | RW
249 | DO_Polarity_LogicIndex_17 | El. Heater Step 1 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_17 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16631 | HFFFF | RW
250 | DO_Polarity_LogicIndex_18 | El. Heater Step 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_18 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16632 | HFFFF | RW
251 | DO_Polarity_LogicIndex_19 | El. Heater Step 3 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_19 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16633 | HFFFF | RW
252 | DO_Polarity_LogicIndex_20 | Pre Heater Step 1 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_20 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16634 | HFFFF | RW
253 | DO_Polarity_LogicIndex_21 | Pre Heater Step 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_21 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16635 | HFFFF | RW
254 | DO_Polarity_LogicIndex_22 | Pre Heater Step 3 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_22 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16636 | HFFFF | RW
255 | DO_Polarity_LogicIndex_23 | Post Heater Step 1 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_23 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16637 | HFFFF | RW
256 | DO_Polarity_LogicIndex_24 | Post Heater Step 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_24 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16638 | HFFFF | RW
257 | DO_Polarity_LogicIndex_25 | Post Heater Step 3 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_25 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16639 | HFFFF | RW
258 | DO_Polarity_LogicIndex_26 | Humidifier - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_26 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16640 | HFFFF | RW
259 | DO_Polarity_LogicIndex_27 | Recovery - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_27 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16641 | HFFFF | RW
260 | DO_Polarity_LogicIndex_28 | Supply Fan 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_28 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16642 | HFFFF | RW
261 | DO_Polarity_LogicIndex_29 | Return Fan 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_29 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16643 | HFFFF | RW
262 | DO_Polarity_LogicIndex_30 | Supply Damper 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_30 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16644 | HFFFF | RW
263 | DO_Polarity_LogicIndex_31 | Return Damper 2 - DO Polarity | CUS40000 | DO_Polarity_LogicIndex_31 | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16645 | HFFFF | RW
264 | ioEE_free73 |  | CUS40000 | ioEE_free73 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16646 | HFFFF | RW
265 | ioEE_free74 |  | CUS40000 | ioEE_free74 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16647 | HFFFF | RW
266 | ioEE_free75 |  | CUS40000 | ioEE_free75 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16648 | HFFFF | RW
267 | ioEE_free76 |  | CUS40000 | ioEE_free76 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16649 | HFFFF | RW
268 | ioEE_free77 |  | CUS40000 | ioEE_free77 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16650 | HFFFF | RW
269 | ioEE_free78 |  | CUS40000 | ioEE_free78 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16651 | HFFFF | RW
270 | ioEE_free79 |  | CUS40000 | ioEE_free79 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16652 | HFFFF | RW
271 | ioEE_free80 |  | CUS40000 | ioEE_free80 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16653 | HFFFF | RW
272 | BACNET_ENABLE | Bacnet Protocol Enable | CUS40000 | BACNET_ENABLE | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16699 | HFFFF | RW
273 | BACNET_ID | Bacnet Device ID | CUS40000 | BACNET_ID | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16700 | HFFFF | RW
274 | BACNET_BBMD_Ip1 | BBMD Service IP - Foreing Devices Handling | CUS40000 | BACNET_BBMD_Ip1 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16701 | HFFFF | RW
275 | BACNET_BBMD_Ip2 | BBMD Service IP - Foreing Devices Handling | CUS40000 | BACNET_BBMD_Ip2 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16702 | HFFFF | RW
276 | BACNET_BBMD_Ip3 | BBMD Service IP - Foreing Devices Handling | CUS40000 | BACNET_BBMD_Ip3 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16703 | HFFFF | RW
277 | BACNET_BBMD_Ip4 | BBMD Service IP - Foreing Devices Handling | CUS40000 | BACNET_BBMD_Ip4 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16704 | HFFFF | RW
278 | BACNET_BBMD_TMO | BBMD Timeout - Foreing Devices Handling | CUS40000 | BACNET_BBMD_TMO | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16705 | HFFFF | RW
279 | BACNET_BBMD_PORT | BBMD Port - Foreing Devices Handling | CUS40000 | BACNET_BBMD_PORT | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16706 | HFFFF | RW
280 | WEB_User_E2 | Web User ID | CUS40000 | WEB_User_E2 | PH | PGR00000 |  |  |  |  | FIX(VMU00021) |  |  |  | P | 16709 | S[9] | RW
281 | WEB_PSW_E2 | Web Psw ID | CUS40000 | WEB_PSW_E2 | PH | PGR00000 |  |  |  |  | FIX(VMU00021) |  |  |  | P | 16718 | S[9] | RW
282 | DayLight_Region | Day Light Region | CUS40000 | DayLight_Region | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16729 | HFFFF | RW
283 | DayLight_Enable | Day Light Enable | CUS40000 | DayLight_Enable | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16730 | HFFFF | RW
284 | Unit_ForceOffAfterReboot | Force Off keyboard after reboot | CUS40000 | Unit_ForceOffAfterReboot | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16739 | HFFFF | RW
285 | Unit_RegTempType | Temperature Regulation Probe | CUS40000 | Unit_RegTempType | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16740 | HFFFF | RW
286 | SP_T_MIN | Minimum Temperature Setpoint | CUS40000 | SP_T_MIN | PH | PGR00000 | -32768 | Params(SP_T_MAX) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16741 | HFFFF | RW
287 | SP_T_MAX | Maximum Temperature Setpoint | CUS40000 | SP_T_MAX | PH | PGR00000 | Params(SP_T_MIN) | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16742 | HFFFF | RW
288 | SP_T_Auto_E2 | Setpoint Auto | CUS40000 | SP_T_Auto_E2 | PH | PGR00000 | Params(SP_T_MIN) | Params(SP_T_MAX) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16743 | HFFFF | RW
289 | DIFF_T_AutoChangeMode | Differential Change season (AUTO) | CUS40000 | DIFF_T_AutoChangeMode | PH | PGR00000 | 5 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16744 | HFFFF | RW
290 | DIFF_T_AutoEco | Differential Economy Mode - Half Band (AUTO) | CUS40000 | DIFF_T_AutoEco | PH | PGR00000 | 0 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16745 | HFFFF | RW
291 | SP_T_FORCESUMMER | Force Summer Mode (AUTO) | CUS40000 | SP_T_FORCESUMMER | PH | PGR00000 | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16746 | HFFFF | RW
292 | SP_T_FORCEWINTER | Force Winter Mode (AUTO) | CUS40000 | SP_T_FORCEWINTER | PH | PGR00000 | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16747 | HFFFF | RW
293 | SP_T_Cool_E2 | Setpoint Cooling | CUS40000 | SP_T_Cool_E2 | PH | PGR00000 | Params(SP_T_MIN) | Params(SP_T_MAX) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16748 | HFFFF | RW
294 | SP_T_Heat_E2 | Setpoint Heating | CUS40000 | SP_T_Heat_E2 | PH | PGR00000 | Params(SP_T_MIN) | Params(SP_T_MAX) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16749 | HFFFF | RW
295 | SP_T_CoolEco_E2 | Setpoint Cooling Economy | CUS40000 | SP_T_CoolEco_E2 | PH | PGR00000 | Params(SP_T_Cool_E2) | Params(SP_T_MAX) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16750 | HFFFF | RW
296 | SP_T_HeatEco_E2 | Setpoint Heating Economy | CUS40000 | SP_T_HeatEco_E2 | PH | PGR00000 | Params(SP_T_MIN) | Params(SP_T_Heat_E2) | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16751 | HFFFF | RW
297 | SP_RH_MinSetpoint | Minimum relative humidity setpoint | CUS40000 | SP_RH_MinSetpoint | PH | PGR00000 | 20 | Params(SP_RH_MaxSetpoint) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16752 | HFFFF | RW
298 | SP_RH_MaxSetpoint | Maximum relative humidity setpoint | CUS40000 | SP_RH_MaxSetpoint | PH | PGR00000 | Params(SP_RH_MinSetpoint) | 100 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16753 | HFFFF | RW
299 | SP_RH_DehumidificationSetpoint_E2 | Dehumidication setpoint (comfort) | CUS40000 | SP_RH_DehumidificationSetpoint_E2 | PH | PGR00000 | Params(SP_RH_MinSetpoint) | Params(SP_RH_MaxSetpoint) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16754 | HFFFF | RW
300 | SP_RH_DehumidificationSetpointEco_E2 | Dehumidication setpoint (eco) | CUS40000 | SP_RH_DehumidificationSetpointEco_E2 | PH | PGR00000 | Params(SP_RH_MinSetpoint) | Params(SP_RH_MaxSetpoint) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16755 | HFFFF | RW
301 | SP_RH_HumidificationSetpoint_E2 | Humidification setpoint (comfort) | CUS40000 | SP_RH_HumidificationSetpoint_E2 | PH | PGR00000 | Params(SP_RH_MinSetpoint) | Params(SP_RH_MaxSetpoint) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16756 | HFFFF | RW
302 | SP_RH_HumidificationSetpointEco_E2 | Humidification setpoint (eco) | CUS40000 | SP_RH_HumidificationSetpointEco_E2 | PH | PGR00000 | Params(SP_RH_MinSetpoint) | Params(SP_RH_MaxSetpoint) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16757 | HFFFF | RW
303 | SP_VOC_E2 | VOC Air quality setpoint | CUS40000 | SP_VOC_E2 | PH | PGR00000 | 0 | 100 |  | TRUE | FIX(VMU00026) |  |  |  | P | 16758 | HFFFF | RW
304 | SP_CO2_E2 | CO2 Air quality setpoint | CUS40000 | SP_CO2_E2 | PH | PGR00000 | 0 | 2000 |  | TRUE | FIX(VMU00060) |  |  |  | P | 16759 | HFFFF | RW
305 | cfgFreeCooling | FreeCooling Enable | CUS40000 | cfgFreeCooling | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16769 | HFFFF | RW
306 | cfgFreeHeating | FreeHeating Enable | CUS40000 | cfgFreeHeating | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16770 | HFFFF | RW
307 | FreeCHMinExtTemp | Free Cooling/Heating Minimum External Temperature | CUS40000 | FreeCHMinExtTemp | PH | PGR00000 | -200 | 200 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16771 | HFFFF | RW
308 | FreeCHBand | Free Cooling/Heating Proportional Band (direct return reg) | CUS40000 | FreeCHBand | PH | PGR00000 | 10 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16772 | HFFFF | RW
309 | FreeCHTimeout | Free Cooling/Heating Timeout | CUS40000 | FreeCHTimeout | PH | PGR00000 | 0 | 180 |  |  | FIX(VMU00018) |  |  |  | P | 16773 | HFFFF | RW
310 | FreeCHDiff | Free Cooling/Heating Outside Regulation Differential | CUS40000 | FreeCHDiff | PH | PGR00000 | 10 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16774 | HFFFF | RW
311 | FreeCHHyst | Free Cooling/Heating Hysteresis | CUS40000 | FreeCHHyst | PH | PGR00000 | 2 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16775 | HFFFF | RW
312 | cfgFireAlarm | Fire Alarm Configuration | CUS40000 | cfgFireAlarm | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16779 | HFFFF | RW
313 | FireTempSet | Setpoint Temperature for Fire Alarm | CUS40000 | FireTempSet | PH | PGR00000 | 900 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16780 | HFFFF | RW
314 | Alm_MinHumiditySens | Minimum Valid Humidity Value | CUS40000 | Alm_MinHumiditySens | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16781 | HFFFF | RW
315 | Alm_MinVOCSens | Minimum Valid VOC Value | CUS40000 | Alm_MinVOCSens | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16782 | HFFFF | RW
316 | Alm_MinCO2Sens | Minimum Valid CO2 Value | CUS40000 | Alm_MinCO2Sens | PH | PGR00000 | 0 | 32767 |  | TRUE | FIX(VMU00060) |  |  |  | P | 16783 | HFFFF | RW
317 | Alm_MinPrSens | Minimum Valid Pr Value (Fans on) | CUS40000 | Alm_MinPrSens | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16784 | HFFFF | RW
318 | Alm_ActiveProbeBypass | Active Probe alarm bypass | CUS40000 | Alm_ActiveProbeBypass | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16785 | HFFFF | RW
319 | AFset | Antifreeze Setpoint | CUS40000 | AFset | PH | PGR00000 | -50 | 150 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16786 | HFFFF | RW
320 | AFdiff | Antifreeze Differential | CUS40000 | AFdiff | PH | PGR00000 | 1 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16787 | HFFFF | RW
321 | AFphtime | Antifreeze Preheater time | CUS40000 | AFphtime | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00018) |  |  |  | P | 16788 | HFFFF | RW
322 | ExtDamperOpenDelay | External/Fan Damper Open Time | CUS40000 | ExtDamperOpenDelay | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16799 | HFFFF | RW
323 | ExtDamperCloseDelay | External/Fan Damper Close Time | CUS40000 | ExtDamperCloseDelay | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16800 | HFFFF | RW
324 | ExtDamperMinOpen | External Damper Minimum Open | CUS40000 | ExtDamperMinOpen | PH | PGR00000 | 0 | 100 |  | TRUE | FIX(VMU00026) |  |  |  | P | 16801 | HFFFF | RW
325 | ExtDamperMaxOpen | External Damper Maximum Open | CUS40000 | ExtDamperMaxOpen | PH | PGR00000 | Params(ExtDamperMinOpen) | 100 |  | TRUE | FIX(VMU00026) |  |  |  | P | 16802 | HFFFF | RW
326 | VOC_Bp | VOC Regulator: Prop. Band | CUS40000 | VOC_Bp | PH | PGR00000 | 1 | 65535 | FIX(-1) |  | FIX(VMU00026) |  |  |  | P | 16819 | HFFFF | RW
327 | VOC_Ti | VOC Regulator: Integral Time | CUS40000 | VOC_Ti | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16820 | HFFFF | RW
328 | CO2_Bp | CO2 Regulator: Prop. Band | CUS40000 | CO2_Bp | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00060) |  |  |  | P | 16821 | HFFFF | RW
329 | CO2_Ti | CO2 Regulator: Integral Time | CUS40000 | CO2_Ti | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16822 | HFFFF | RW
330 | Fan_MinimumSpeed | Fan Minimum Speed (Pressure Regulation and limit for other speed) | CUS40000 | Fan_MinimumSpeed | PH | PGR00000 | 0 | 500 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16839 | HFFFF | RW
331 | Fan_LowSpeed | Fan Low Speed (Start Phase/Night/Min Air Q. and Defrost Speed) | CUS40000 | Fan_LowSpeed | PH | PGR00000 | Params(Fan_MinimumSpeed) | 800 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16840 | HFFFF | RW
332 | Fan_NominalSpeed | Fan Nominal/Maximum Speed | CUS40000 | Fan_NominalSpeed | PH | PGR00000 | Params(Fan_LowSpeed) | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16841 | HFFFF | RW
333 | Fan_ReturnSpeedCorrection | Fan Return Output correction (not used with 2 pressure probes) | CUS40000 | Fan_ReturnSpeedCorrection | PH | PGR00000 | -500 | 500 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16842 | HFFFF | RW
334 | Fan_PowerUp1_Time | Fan Power Up Time at Min Speed (with Heaters or Cond.Unit) | CUS40000 | Fan_PowerUp1_Time | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16843 | HFFFF | RW
335 | Fan_PowerUp2_Time | Fan Power Up Time at Nom Speed (with Heaters or Cond.Unit) | CUS40000 | Fan_PowerUp2_Time | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16844 | HFFFF | RW
336 | Fan_Post_Time | Fan Post Ventilation Time (with Heaters) | CUS40000 | Fan_Post_Time | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16845 | HFFFF | RW
337 | Fan_PreHeating_Time | Fan Preheating Time (with heating valves) | CUS40000 | Fan_PreHeating_Time | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16846 | HFFFF | RW
338 | Fan_PreHeatOnSet | External Temperature Set forcing preheating time | CUS40000 | Fan_PreHeatOnSet | PH | PGR00000 | -200 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16847 | HFFFF | RW
339 | Fan_Swap_Time | Fan swap time (0=Disabled) | CUS40000 | Fan_Swap_Time | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16848 | HFFFF | RW
340 | Fan_SwapPolicy | Fan swap policy | CUS40000 | Fan_SwapPolicy | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16849 | HFFFF | RW
341 | Fan_SinglePressureReturn | In case of a unique pressure probe mounted on return section and Supply+Return Fans | CUS40000 | Fan_SinglePressureReturn | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16850 | HFFFF | RW
342 | Fan_AlrmPressBypass | Flow Bypass | CUS40000 | Fan_AlrmPressBypass | PH | PGR00000 | 1 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16851 | HFFFF | RW
343 | Fan_SupplyAirflowAlrmByAi | Enable supply flow alarm by probe (pressure probe must be already enabled) | CUS40000 | Fan_SupplyAirflowAlrmByAi | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16852 | HFFFF | RW
344 | Fan_ReturnAirflowAlrmByAi | Enable return flow alarm by probe (pressure probe must be already enabled) | CUS40000 | Fan_ReturnAirflowAlrmByAi | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16853 | HFFFF | RW
345 | Fan_SetMinAirflow | Fan Airflow Alarm setpoint | CUS40000 | Fan_SetMinAirflow | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00005) |  |  |  | P | 16854 | HFFFF | RW
346 | FAN_Supply_BpP | Fan Supply Prop. Band Pressure | CUS40000 | FAN_Supply_BpP | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00005) |  |  |  | P | 16855 | HFFFF | RW
347 | FAN_Supply_TiP | Fan Supply Integral Time Pressure | CUS40000 | FAN_Supply_TiP | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16856 | HFFFF | RW
348 | FAN_Supply_TdP | Fan Supply Derivative Time Pressure | CUS40000 | FAN_Supply_TdP | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16857 | HFFFF | RW
349 | FAN_Return_BpP | Fan Return Prop. Band Pressure | CUS40000 | FAN_Return_BpP | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00005) |  |  |  | P | 16858 | HFFFF | RW
350 | FAN_Return_TiP | Fan Return Integral Time Pressure | CUS40000 | FAN_Return_TiP | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16859 | HFFFF | RW
351 | FAN_Return_TdP | Fan Return Derivative Time Pressure | CUS40000 | FAN_Return_TdP | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16860 | HFFFF | RW
352 | Fan_K_Supply | Fan K Supply | CUS40000 | Fan_K_Supply | PH | PGR00000 | 1 | 3000 |  |  | FIX(VMU00020) |  |  |  | P | 16861 | HFFFF | RW
353 | Fan_K_Return | Fan K Return | CUS40000 | Fan_K_Return | PH | PGR00000 | 1 | 3000 |  |  | FIX(VMU00020) |  |  |  | P | 16862 | HFFFF | RW
354 | Fan_Supply_Pressure_Flow | Fan Supply Regulation Unit | CUS40000 | Fan_Supply_Pressure_Flow | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16879 | HFFFF | RW
355 | Fan_Return_Pressure_Flow | Fan Return Regulation Unit | CUS40000 | Fan_Return_Pressure_Flow | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16880 | HFFFF | RW
356 | Fan_Supply_SetMinPr | Fan Supply Minimum/Night Pressure Setpoint | CUS40000 | Fan_Supply_SetMinPr | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00005) |  |  |  | P | 16881 | HFFFF | RW
357 | Fan_Return_SetMinPr | Fan Return Minimum/Night Pressure Setpoint | CUS40000 | Fan_Return_SetMinPr | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00005) |  |  |  | P | 16882 | HFFFF | RW
358 | Fan_SetPrSupply | Fan Supply Pressure Setpoint | CUS40000 | Fan_SetPrSupply | PH | PGR00000 | Params(Fan_Supply_SetMinPr) | Params(Fan_Supply_SetMaxPr) |  | TRUE | FIX(VMU00005) |  |  |  | P | 16883 | HFFFF | RW
359 | Fan_SetPrReturn | Fan Return Pressure Setpoint | CUS40000 | Fan_SetPrReturn | PH | PGR00000 | Params(Fan_Return_SetMinPr) | Params(Fan_Return_SetMaxPr) |  | TRUE | FIX(VMU00005) |  |  |  | P | 16884 | HFFFF | RW
360 | Fan_Supply_SetMaxPr | Fan Supply Maximum Pressure Setpoint | CUS40000 | Fan_Supply_SetMaxPr | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00005) |  |  |  | P | 16885 | HFFFF | RW
361 | Fan_Return_SetMaxPr | Fan Return Maximum Pressure Setpoint | CUS40000 | Fan_Return_SetMaxPr | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00005) |  |  |  | P | 16886 | HFFFF | RW
362 | Fan_Supply_SetMinFlow | Fan Supply Minimum/Night Flow Setpoint | CUS40000 | Fan_Supply_SetMinFlow | PH | PGR00000 | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16887 | HFFFFFFFF | RW
363 | Fan_Return_SetMinFlow | Fan Return Minimum/Night Flow Setpoint | CUS40000 | Fan_Return_SetMinFlow | PH | PGR00000 | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16889 | HFFFFFFFF | RW
364 | Fan_SetFlowSupply | Fan Supply Flow Setpoint | CUS40000 | Fan_SetFlowSupply | PH | PGR00000 | Params(Fan_Supply_SetMinFlow) | Params(Fan_Supply_SetMaxFlow) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16891 | HFFFFFFFF | RW
365 | Fan_SetFlowReturn | Fan Return Flow Setpoint | CUS40000 | Fan_SetFlowReturn | PH | PGR00000 | Params(Fan_Return_SetMinFlow) | Params(Fan_Return_SetMaxFlow) |  | TRUE | FIX(VMU00020) |  |  |  | P | 16893 | HFFFFFFFF | RW
366 | Fan_Supply_SetMaxFlow | Fan Supply Maximum Flow Setpoint | CUS40000 | Fan_Supply_SetMaxFlow | PH | PGR00000 | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16895 | HFFFFFFFF | RW
367 | Fan_Return_SetMaxFlow | Fan Return Maximum Flow Setpoint | CUS40000 | Fan_Return_SetMaxFlow | PH | PGR00000 | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16897 | HFFFFFFFF | RW
368 | SupplyDeltaUpHeating | Heating Max Supply =RegSet+SupplyDeltaUpHeating | CUS40000 | SupplyDeltaUpHeating | PH | PGR00000 | 5 | 400 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16909 | HFFFF | RW
369 | SupplyDeltaDwHeating | Heating Min Supply =RegSet-SupplyDeltaDwHeating | CUS40000 | SupplyDeltaDwHeating | PH | PGR00000 | 0 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16910 | HFFFF | RW
370 | SupplyDeltaUpCooling | Cooling Max Supply =RegSet+SupplyDeltaUpCooling | CUS40000 | SupplyDeltaUpCooling | PH | PGR00000 | 0 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16911 | HFFFF | RW
371 | SupplyDeltaDwCooling | Cooling Min Supply =RegSet-SupplyDeltaDwCooling | CUS40000 | SupplyDeltaDwCooling | PH | PGR00000 | 5 | 150 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16912 | HFFFF | RW
372 | Pb_Cooling | Cooling Proportional Band | CUS40000 | Pb_Cooling | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16913 | HFFFF | RW
373 | Pb_Heating | Heating Proportional Band | CUS40000 | Pb_Heating | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16914 | HFFFF | RW
374 | Ti_Cooling | Cooling Integral Time | CUS40000 | Ti_Cooling | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16915 | HFFFF | RW
375 | Ti_Heating | Heating Integral Time | CUS40000 | Ti_Heating | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16916 | HFFFF | RW
376 | Pb_ReturnCooling | Return Temp. Reg: Cooling Proportional Band (only Cascade) | CUS40000 | Pb_ReturnCooling | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16917 | HFFFF | RW
377 | Pb_ReturnHeating | Return Temp. Reg: Heating Proportional Band (only Cascade) | CUS40000 | Pb_ReturnHeating | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16918 | HFFFF | RW
378 | Ti_ReturnCooling | Return Temp. Reg: Cooling Integral Time (only Cascade) | CUS40000 | Ti_ReturnCooling | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16919 | HFFFF | RW
379 | Ti_ReturnHeating | Return Temp. Reg: Heating Integral Time (only Cascade) | CUS40000 | Ti_ReturnHeating | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16920 | HFFFF | RW
380 | Temp_HighSupplyEn | Temperature High Supply Limit Enable (Winter) | CUS40000 | Temp_HighSupplyEn | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 16929 | HFFFF | RW
381 | Temp_HighSupplySet | Temperature High Supply Limit Setpoint (Winter) | CUS40000 | Temp_HighSupplySet | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16930 | HFFFF | RW
382 | Temp_HighSupplyBand | Temperature High Supply Band (Winter) | CUS40000 | Temp_HighSupplyBand | PH | PGR00000 | 10 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16931 | HFFFF | RW
383 | Temp_LowSupplyEn | Temperature Low Supply Limit Enable (Summer) | CUS40000 | Temp_LowSupplyEn | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16932 | HFFFF | RW
384 | Temp_LowSupplySet | Temperature Low Supply Limit Setpoint (Summer) | CUS40000 | Temp_LowSupplySet | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16933 | HFFFF | RW
385 | Temp_LowSupplyBand | Temperature Low Supply Band (Summer) | CUS40000 | Temp_LowSupplyBand | PH | PGR00000 | 10 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16934 | HFFFF | RW
386 | FastHeatCoolEn | Fast Heating/Cooling Enable | CUS40000 | FastHeatCoolEn | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 16939 | HFFFF | RW
387 | FastHeatSet | Maximum outside temp for Power up Fast Heating | CUS40000 | FastHeatSet | PH | PGR00000 | -500 | 500 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16940 | HFFFF | RW
388 | FastCoolSet | Minimum outside temp for Power up Fast Cooling | CUS40000 | FastCoolSet | PH | PGR00000 | -500 | 500 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16941 | HFFFF | RW
389 | FastHCTimeout | Fast Heating/Cooling and StartUp timeout | CUS40000 | FastHCTimeout | PH | PGR00000 | 1 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16942 | HFFFF | RW
390 | FastHeatExitSet | Fast Heating Return temperature exit set in case of supply Regulation | CUS40000 | FastHeatExitSet | PH | PGR00000 | -500 | 500 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16943 | HFFFF | RW
391 | FastCoolExitSet | Fast Cooling Return temperature exit set in case of supply Regulation | CUS40000 | FastCoolExitSet | PH | PGR00000 | -500 | 500 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16944 | HFFFF | RW
392 | Pump_AntiStickingRun | Antisticking run time | CUS40000 | Pump_AntiStickingRun | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16949 | HFFFF | RW
393 | Pump_AntiStickingPeriod | Antisticking period (0=Disabled) | CUS40000 | Pump_AntiStickingPeriod | PH | PGR00000 | 0 | 30 |  |  | FIX(VMU00020) |  |  |  | P | 16950 | HFFFF | RW
394 | Pump_Post_Time | Pump Post Running Time | CUS40000 | Pump_Post_Time | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00018) |  |  |  | P | 16951 | HFFFF | RW
395 | Heater_Power_Analog | El. Heater Analog Power | CUS40000 | Heater_Power_Analog | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16952 | HFFFF | RW
396 | Heater_Power_Step1 | El. Heater Step 1 Power | CUS40000 | Heater_Power_Step1 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16953 | HFFFF | RW
397 | Heater_Power_Step2 | El. Heater Step 2 Additional Power | CUS40000 | Heater_Power_Step2 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16954 | HFFFF | RW
398 | Heater_Power_Step3 | El. Heater Step 3 Additional Power | CUS40000 | Heater_Power_Step3 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16955 | HFFFF | RW
399 | Heater_Power_Step4 | El. Heater Step 4 Additional Power | CUS40000 | Heater_Power_Step4 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16956 | HFFFF | RW
400 | Heater_Power_Step5 | El. Heater Step 5 Additional Power | CUS40000 | Heater_Power_Step5 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16957 | HFFFF | RW
401 | Heater_Power_Step6 | El. Heater Step 6 Additional Power | CUS40000 | Heater_Power_Step6 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16958 | HFFFF | RW
402 | Heater_Hysteresis | El. Heater Hysteresis [% of current step] | CUS40000 | Heater_Hysteresis | PH | PGR00000 | 1 | 100 |  |  | FIX(VMU00026) |  |  |  | P | 16959 | HFFFF | RW
403 | Heater_PWM_Period | El. Heater PWM Period | CUS40000 | Heater_PWM_Period | PH | PGR00000 | 10 | 3000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16960 | HFFFF | RW
404 | PreHeater_Power_Analog | PreHeater Analog Power | CUS40000 | PreHeater_Power_Analog | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16961 | HFFFF | RW
405 | PreHeater_Power_Step1 | PreHeater Step 1 Power | CUS40000 | PreHeater_Power_Step1 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16962 | HFFFF | RW
406 | PreHeater_Power_Step2 | PreHeater Step 2 Power | CUS40000 | PreHeater_Power_Step2 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16963 | HFFFF | RW
407 | PreHeater_Power_Step3 | PreHeater Step 3 Power | CUS40000 | PreHeater_Power_Step3 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16964 | HFFFF | RW
408 | PreHeater_Power_Step4 | PreHeater Step 4 Power | CUS40000 | PreHeater_Power_Step4 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16965 | HFFFF | RW
409 | PreHeater_Power_Step5 | PreHeater Step 5 Power | CUS40000 | PreHeater_Power_Step5 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16966 | HFFFF | RW
410 | PreHeater_Power_Step6 | PreHeater Step 6 Power | CUS40000 | PreHeater_Power_Step6 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16967 | HFFFF | RW
411 | PreHeater_Hysteresis | PreHeater Hysteresis [% of current step] | CUS40000 | PreHeater_Hysteresis | PH | PGR00000 | 1 | 100 |  |  | FIX(VMU00026) |  |  |  | P | 16968 | HFFFF | RW
412 | PreHeater_PWM_Period | PreHeater PWM Period | CUS40000 | PreHeater_PWM_Period | PH | PGR00000 | 10 | 3000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16969 | HFFFF | RW
413 | PostHeater_Power_Analog | PostHeater Analog Power | CUS40000 | PostHeater_Power_Analog | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16970 | HFFFF | RW
414 | PostHeater_Power_Step1 | PostHeater Step 1 Power | CUS40000 | PostHeater_Power_Step1 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16971 | HFFFF | RW
415 | PostHeater_Power_Step2 | PostHeater Step 2 Power | CUS40000 | PostHeater_Power_Step2 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16972 | HFFFF | RW
416 | PostHeater_Power_Step3 | PostHeater Step 3 Power | CUS40000 | PostHeater_Power_Step3 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16973 | HFFFF | RW
417 | PostHeater_Power_Step4 | PostHeater Step 4 Power | CUS40000 | PostHeater_Power_Step4 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16974 | HFFFF | RW
418 | PostHeater_Power_Step5 | PostHeater Step 5 Power | CUS40000 | PostHeater_Power_Step5 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16975 | HFFFF | RW
419 | PostHeater_Power_Step6 | PostHeater Step 6 Power | CUS40000 | PostHeater_Power_Step6 | PH | PGR00000 | 1 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 16976 | HFFFF | RW
420 | PostHeater_Hysteresis | PostHeater Hysteresis [% of current step] | CUS40000 | PostHeater_Hysteresis | PH | PGR00000 | 1 | 100 |  |  | FIX(VMU00026) |  |  |  | P | 16977 | HFFFF | RW
421 | PostHeater_PWM_Period | PreHeater PWM Period | CUS40000 | PostHeater_PWM_Period | PH | PGR00000 | 10 | 3000 |  | TRUE | FIX(VMU00020) |  |  |  | P | 16978 | HFFFF | RW
422 | CondUnitS1_Req | % CondUnit Step 1 | CUS40000 | CondUnitS1_Req | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16979 | HFFFF | RW
423 | CondUnitS2_Req | % CondUnit Step 2 | CUS40000 | CondUnitS2_Req | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16980 | HFFFF | RW
424 | CondUnitS3_Req | % CondUnit Step 3 | CUS40000 | CondUnitS3_Req | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16981 | HFFFF | RW
425 | CondUnitS4_Req | % CondUnit Step 4 | CUS40000 | CondUnitS4_Req | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16982 | HFFFF | RW
426 | CondUnitSx_Hysteresis | Cond. Unit Hysteresis % of current Step size | CUS40000 | CondUnitSx_Hysteresis | PH | PGR00000 | 10 | 100 |  | TRUE | FIX(VMU00026) |  |  |  | P | 16983 | HFFFF | RW
427 | CondUnit_Ton | Cond Unit or Step Minimum On Time | CUS40000 | CondUnit_Ton | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16984 | HFFFF | RW
428 | CondUnit_Toff | Cond Unit or Step Minimum Off Time | CUS40000 | CondUnit_Toff | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16985 | HFFFF | RW
429 | CondUnit_Offset | Cond Unit AO Offset | CUS40000 | CondUnit_Offset | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 16986 | HFFFF | RW
430 | CondUnit_FanSpeedDefrost | Condensing Unit: Fan Speed During Defrost | CUS40000 | CondUnit_FanSpeedDefrost | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16987 | HFFFF | RW
431 | MultiCondUnit_CtrlMode | Multi Condensing Unit: Control Mode | CUS40000 | MultiCondUnit_CtrlMode | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 16988 | HFFFF | RW
432 | MultiCondUnit_RegHyst | Multi Condensing Unit regulator hysteresis | CUS40000 | MultiCondUnit_RegHyst | PH | PGR00000 | 2 | 30 |  | TRUE | FIX(VMU00026) |  |  |  | P | 16989 | HFFFF | RW
433 | MultiCondUnit_DelayOn | Multi Cond Unit Delay On | CUS40000 | MultiCondUnit_DelayOn | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16990 | HFFFF | RW
434 | MultiCondUnit_DelayOff | Multi Cond Unit Delay Off | CUS40000 | MultiCondUnit_DelayOff | PH | PGR00000 | 0 | 600 |  |  | FIX(VMU00020) |  |  |  | P | 16991 | HFFFF | RW
435 | PreHeaterSetpoint | Setpoint Pre Heating | CUS40000 | PreHeaterSetpoint | PH | PGR00000 | -100 | 200 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 16999 | HFFFF | RW
436 | Pb_PreHeating | PreHeating Proportional Band | CUS40000 | Pb_PreHeating | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17000 | HFFFF | RW
437 | Ti_PreHeating | PreHeating Integral Time | CUS40000 | Ti_PreHeating | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 17001 | HFFFF | RW
438 | RecoveryDiff_Band | Recovery Diff (On/Off Case) Recovery Band (Mod Case with Direct Return control); | CUS40000 | RecoveryDiff_Band | PH | PGR00000 | 1 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17009 | HFFFF | RW
439 | RecoveryDeadZone | Recovery Dead Zone | CUS40000 | RecoveryDeadZone | PH | PGR00000 | 0 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17010 | HFFFF | RW
440 | RecoveryPower | % of PI out sent to recovery (Only for Cascade or Supply control) | CUS40000 | RecoveryPower | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 17011 | HFFFF | RW
441 | RecoveryDefrost_SetMaxReq | Recovery Defrost: Setpoint Expulsion Temperature | CUS40000 | RecoveryDefrost_SetMaxReq | PH | PGR00000 | -150 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17012 | HFFFF | RW
442 | RecoveryDefrost_Band | Recovery Defrost: Band Mix Chamber/PreHeater/Supply Fan | CUS40000 | RecoveryDefrost_Band | PH | PGR00000 | 1 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17013 | HFFFF | RW
443 | RecoveryDefrost_Cutoff | Recovery Defrost: CutOff Modulating Fan | CUS40000 | RecoveryDefrost_Cutoff | PH | PGR00000 | 0 | 100 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17014 | HFFFF | RW
444 | RecoveryReqDuringFastHC | Recovery request during Fast Heating/Cooling | CUS40000 | RecoveryReqDuringFastHC | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 17015 | HFFFF | RW
445 | Hum_Band | Humidification Band | CUS40000 | Hum_Band | PH | PGR00000 | 10 | 400 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17019 | HFFFF | RW
446 | Pb_Dehum | Dehum. Proportional Band | CUS40000 | Pb_Dehum | PH | PGR00000 | 2 | 200 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17020 | HFFFF | RW
447 | Ti_Dehum | Dehum. Integral Time | CUS40000 | Ti_Dehum | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 17021 | HFFFF | RW
448 | Pb_Dewpoint | Dewpoint Dehum. Proportional Band | CUS40000 | Pb_Dewpoint | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17022 | HFFFF | RW
449 | Ti_Dewpoint | Dewpoint Dehum. Integral Time | CUS40000 | Ti_Dewpoint | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 17023 | HFFFF | RW
450 | Offset_Post | PostHeating Setpoint offset with respect to current set | CUS40000 | Offset_Post | PH | PGR00000 | 4 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17024 | HFFFF | RW
451 | Dehum_WinterEn | Enable Winter Dehumidification | CUS40000 | Dehum_WinterEn | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 17025 | HFFFF | RW
452 | Dehum_WinterHumHyst | Winter Dehumidification Hysteresis | CUS40000 | Dehum_WinterHumHyst | PH | PGR00000 | 4 | 50 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17026 | HFFFF | RW
453 | Dehum_Req_Diff | Dehumidification Request Differential on Return Humidity for Winter and Dewpoint mode | CUS40000 | Dehum_Req_Diff | PH | PGR00000 | 1 | 150 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17027 | HFFFF | RW
454 | Hum_HighSupplyEn | Humidification High Supply Limit Enable | CUS40000 | Hum_HighSupplyEn | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 17028 | HFFFF | RW
455 | Hum_HighSupplySet | Humidification High Supply Limit Setpoint | CUS40000 | Hum_HighSupplySet | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17029 | HFFFF | RW
456 | Hum_HighSupplyBand | Humidification High Supply Band | CUS40000 | Hum_HighSupplyBand | PH | PGR00000 | 10 | 400 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17030 | HFFFF | RW
457 | DeHum_LowSupplyEn | DeHumidification Low Supply Limit Enable | CUS40000 | DeHum_LowSupplyEn | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 17031 | HFFFF | RW
458 | DeHum_LowSupplySet | DeHumidification Low Supply Limit Setpoint | CUS40000 | DeHum_LowSupplySet | PH | PGR00000 | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17032 | HFFFF | RW
459 | DeHum_LowSupplyBand | DeHumidification Low Supply Band | CUS40000 | DeHum_LowSupplyBand | PH | PGR00000 | 10 | 400 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17033 | HFFFF | RW
460 | PostHeating4Integration | Use the post heating also in the heating phase | CUS40000 | PostHeating4Integration | PH | PGR00000 | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 17039 | HFFFF | RW
461 | PostPower | % of PI out sent to post (if enabled as heat integration) | CUS40000 | PostPower | PH | PGR00000 | 1 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 17040 | HFFFF | RW
462 | Pb_Post | PostHeating Dehum. Proportional Band | CUS40000 | Pb_Post | PH | PGR00000 | 2 | 999 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 17041 | HFFFF | RW
463 | Ti_Post | PostHeating Dehum. Integral Time | CUS40000 | Ti_Post | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 17042 | HFFFF | RW
464 | LogEnable | Logger Enable | CUS40000 | LogEnable | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 17899 | HFFFF | RW
465 | LogCycle | Logger Period | CUS40000 | LogCycle | PH | PGR00000 | Params(MinLogCycle) | 1439 | HH:MM |  | FIX(VMU00020) |  |  |  | P | 17900 | HFFFF | RW
466 | LogErrorNumber | Error while try to oper or save to a file | CUS40000 | LogErrorNumber | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 17901 | HFFFFFFFF | RW
467 | LoggedRecord | Number of logged record (Rounded by 100) | CUS40000 | LoggedRecord | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 17903 | HFFFFFFFF | RW
468 | MinLogCycle | Minimum Log Cycle | CUS40000 | MinLogCycle | PH | PGR00000 | 0 | 1439 | HH:MM |  | FIX(VMU00020) |  |  |  | P | 17905 | HFFFF | RW
469 | FirstDownload |  | CUS40000 | FirstDownload | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 17906 | HFFFF | RW
470 | microSDPresCount | microSD Presence Counter | CUS40000 | microSDPresCount | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 17907 | HFFFF | RW
471 | tE00_TimeBandEnable | Time events Enable | CUS40000 | tE00_TimeBandEnable | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 17999 | HFFFF | RW
472 | tE01_TimeProfileMonday | Time events profile on Monday | CUS40000 | tE01_TimeProfileMonday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18000 | HFFFF | RW
473 | tE02_TimeProfileTuesday | Time events profile on Tuesday | CUS40000 | tE02_TimeProfileTuesday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18001 | HFFFF | RW
474 | tE03_TimeProfileWednesday | Time events profile on Wednesday | CUS40000 | tE03_TimeProfileWednesday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18002 | HFFFF | RW
475 | tE04_TimeProfileThursday | Time events profile on Thursday | CUS40000 | tE04_TimeProfileThursday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18003 | HFFFF | RW
476 | tE05_TimeProfileFriday | Time events profile on Friday | CUS40000 | tE05_TimeProfileFriday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18004 | HFFFF | RW
477 | tE06_TimeProfileSaturday | Time events profile on Saturday | CUS40000 | tE06_TimeProfileSaturday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18005 | HFFFF | RW
478 | tE07_TimeProfileSunday | Time events profile on Sunday | CUS40000 | tE07_TimeProfileSunday | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18006 | HFFFF | RW
479 | tE10_TimeProfile1Event1 | Time of event #1 of profile #1 | CUS40000 | tE10_TimeProfile1Event1 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18007 | HFFFF | RW
480 | tE11_ModeProfile1Event1 | Mode of event #1 of profile #1 | CUS40000 | tE11_ModeProfile1Event1 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18008 | HFFFF | RW
481 | tE12_TimeProfile1Event2 | Time of event #2 of profile #1 | CUS40000 | tE12_TimeProfile1Event2 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18009 | HFFFF | RW
482 | tE13_ModeProfile1Event2 | Mode of event #2 of profile #1 | CUS40000 | tE13_ModeProfile1Event2 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18010 | HFFFF | RW
483 | tE14_TimeProfile1Event3 | Time of event #3 of profile #1 | CUS40000 | tE14_TimeProfile1Event3 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18011 | HFFFF | RW
484 | tE15_ModeProfile1Event3 | Mode of event #3 of profile #1 | CUS40000 | tE15_ModeProfile1Event3 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18012 | HFFFF | RW
485 | tE16_TimeProfile1Event4 | Time of event #4 of profile #1 | CUS40000 | tE16_TimeProfile1Event4 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18013 | HFFFF | RW
486 | tE17_ModeProfile1Event4 | Mode of event #4 of profile #1 | CUS40000 | tE17_ModeProfile1Event4 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18014 | HFFFF | RW
487 | tE20_TimeProfile2Event1 | Time of event #1 of profile #2 | CUS40000 | tE20_TimeProfile2Event1 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18015 | HFFFF | RW
488 | tE21_ModeProfile2Event1 | Mode of event #1 of profile #2 | CUS40000 | tE21_ModeProfile2Event1 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18016 | HFFFF | RW
489 | tE22_TimeProfile2Event2 | Time of event #2 of profile #2 | CUS40000 | tE22_TimeProfile2Event2 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18017 | HFFFF | RW
490 | tE23_ModeProfile2Event2 | Mode of event #2 of profile #2 | CUS40000 | tE23_ModeProfile2Event2 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18018 | HFFFF | RW
491 | tE24_TimeProfile2Event3 | Time of event #3 of profile #2 | CUS40000 | tE24_TimeProfile2Event3 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18019 | HFFFF | RW
492 | tE25_ModeProfile2Event3 | Mode of event #3 of profile #2 | CUS40000 | tE25_ModeProfile2Event3 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18020 | HFFFF | RW
493 | tE26_TimeProfile2Event4 | Time of event #4 of profile #2 | CUS40000 | tE26_TimeProfile2Event4 | PH | PGR00000 | 0 | 1439 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 18021 | HFFFF | RW
494 | tE27_ModeProfile2Event4 | Mode of event #4 of profile #2 | CUS40000 | tE27_ModeProfile2Event4 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18022 | HFFFF | RW
495 | TW00_EnableYearEvents | Enable year events | CUS40000 | TW00_EnableYearEvents | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18199 | HFFFF | RW
496 | TW01_EventProfile01 | Year events profile 1 | CUS40000 | TW01_EventProfile01 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18200 | HFFFF | RW
497 | TW02_EventProfile02 | Year events profile 2 | CUS40000 | TW02_EventProfile02 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18201 | HFFFF | RW
498 | TW03_EventProfile03 | Year events profile 3 | CUS40000 | TW03_EventProfile03 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18202 | HFFFF | RW
499 | TW04_EventProfile04 | Year events profile 4 | CUS40000 | TW04_EventProfile04 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18203 | HFFFF | RW
500 | TW05_EventProfile05 | Year events profile 5 | CUS40000 | TW05_EventProfile05 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18204 | HFFFF | RW
501 | TW06_EventProfile06 | Year events profile 6 | CUS40000 | TW06_EventProfile06 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18205 | HFFFF | RW
502 | TW07_EventProfile07 | Year events profile 7 | CUS40000 | TW07_EventProfile07 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18206 | HFFFF | RW
503 | TW08_EventProfile08 | Year events profile 8 | CUS40000 | TW08_EventProfile08 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18207 | HFFFF | RW
504 | TW09_EventProfile09 | Year events profile 9 | CUS40000 | TW09_EventProfile09 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18208 | HFFFF | RW
505 | TW10_EventProfile10 | Year events profile 10 | CUS40000 | TW10_EventProfile10 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18209 | HFFFF | RW
506 | TW11_EventProfile11 | Year events profile 11 | CUS40000 | TW11_EventProfile11 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18210 | HFFFF | RW
507 | TW12_EventProfile12 | Year events profile 12 | CUS40000 | TW12_EventProfile12 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18211 | HFFFF | RW
508 | TW13_EventProfile13 | Year events profile 13 | CUS40000 | TW13_EventProfile13 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18212 | HFFFF | RW
509 | TW14_EventProfile14 | Year events profile 14 | CUS40000 | TW14_EventProfile14 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18213 | HFFFF | RW
510 | TW15_EventProfile15 | Year events profile 15 | CUS40000 | TW15_EventProfile15 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 18214 | HFFFF | RW
511 | TW16_EnEvent01 | Enable Year events 1 | CUS40000 | TW16_EnEvent01 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18215 | HFFFF | RW
512 | TW17_EnEvent02 | Enable Year events 2 | CUS40000 | TW17_EnEvent02 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18216 | HFFFF | RW
513 | TW18_EnEvent03 | Enable Year events 3 | CUS40000 | TW18_EnEvent03 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18217 | HFFFF | RW
514 | TW19_EnEvent04 | Enable Year events 4 | CUS40000 | TW19_EnEvent04 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18218 | HFFFF | RW
515 | TW20_EnEvent05 | Enable Year events 5 | CUS40000 | TW20_EnEvent05 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18219 | HFFFF | RW
516 | TW21_EnEvent06 | Enable Year events 6 | CUS40000 | TW21_EnEvent06 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18220 | HFFFF | RW
517 | TW22_EnEvent07 | Enable Year events 7 | CUS40000 | TW22_EnEvent07 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18221 | HFFFF | RW
518 | TW23_EnEvent08 | Enable Year events 8 | CUS40000 | TW23_EnEvent08 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18222 | HFFFF | RW
519 | TW24_EnEvent09 | Enable Year events 9 | CUS40000 | TW24_EnEvent09 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18223 | HFFFF | RW
520 | TW25_EnEvent10 | Enable Year events 10 | CUS40000 | TW25_EnEvent10 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18224 | HFFFF | RW
521 | TW26_EnEvent11 | Enable Year events 11 | CUS40000 | TW26_EnEvent11 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18225 | HFFFF | RW
522 | TW27_EnEvent12 | Enable Year events 12 | CUS40000 | TW27_EnEvent12 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18226 | HFFFF | RW
523 | TW28_EnEvent13 | Enable Year events 13 | CUS40000 | TW28_EnEvent13 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18227 | HFFFF | RW
524 | TW29_EnEvent14 | Enable Year events 14 | CUS40000 | TW29_EnEvent14 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18228 | HFFFF | RW
525 | TW30_EnEvent15 | Enable Year events 15 | CUS40000 | TW30_EnEvent15 | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18229 | HFFFF | RW
526 | TW31_EventDDStart01 | Start Day Year events 1 | CUS40000 | TW31_EventDDStart01 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18230 | HFFFF | RW
527 | TW32_EventDDStart02 | Start Day Year events 2 | CUS40000 | TW32_EventDDStart02 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18231 | HFFFF | RW
528 | TW33_EventDDStart03 | Start Day Year events 3 | CUS40000 | TW33_EventDDStart03 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18232 | HFFFF | RW
529 | TW34_EventDDStart04 | Start Day Year events 4 | CUS40000 | TW34_EventDDStart04 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18233 | HFFFF | RW
530 | TW35_EventDDStart05 | Start Day Year events 5 | CUS40000 | TW35_EventDDStart05 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18234 | HFFFF | RW
531 | TW36_EventDDStart06 | Start Day Year events 6 | CUS40000 | TW36_EventDDStart06 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18235 | HFFFF | RW
532 | TW37_EventDDStart07 | Start Day Year events 7 | CUS40000 | TW37_EventDDStart07 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18236 | HFFFF | RW
533 | TW38_EventDDStart08 | Start Day Year events 8 | CUS40000 | TW38_EventDDStart08 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18237 | HFFFF | RW
534 | TW39_EventDDStart09 | Start Day Year events 9 | CUS40000 | TW39_EventDDStart09 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18238 | HFFFF | RW
535 | TW40_EventDDStart10 | Start Day Year events 10 | CUS40000 | TW40_EventDDStart10 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18239 | HFFFF | RW
536 | TW41_EventDDStart11 | Start Day Year events 11 | CUS40000 | TW41_EventDDStart11 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18240 | HFFFF | RW
537 | TW42_EventDDStart12 | Start Day Year events 12 | CUS40000 | TW42_EventDDStart12 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18241 | HFFFF | RW
538 | TW43_EventDDStart13 | Start Day Year events 13 | CUS40000 | TW43_EventDDStart13 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18242 | HFFFF | RW
539 | TW44_EventDDStart14 | Start Day Year events 14 | CUS40000 | TW44_EventDDStart14 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18243 | HFFFF | RW
540 | TW45_EventDDStart15 | Start Day Year events 15 | CUS40000 | TW45_EventDDStart15 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18244 | HFFFF | RW
541 | TW46_EventMMStart01 | Start Month Year events 1 | CUS40000 | TW46_EventMMStart01 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18245 | HFFFF | RW
542 | TW47_EventMMStart02 | Start Month Year events 2 | CUS40000 | TW47_EventMMStart02 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18246 | HFFFF | RW
543 | TW48_EventMMStart03 | Start Month Year events 3 | CUS40000 | TW48_EventMMStart03 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18247 | HFFFF | RW
544 | TW49_EventMMStart04 | Start Month Year events 4 | CUS40000 | TW49_EventMMStart04 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18248 | HFFFF | RW
545 | TW50_EventMMStart05 | Start Month Year events 5 | CUS40000 | TW50_EventMMStart05 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18249 | HFFFF | RW
546 | TW51_EventMMStart06 | Start Month Year events 6 | CUS40000 | TW51_EventMMStart06 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18250 | HFFFF | RW
547 | TW52_EventMMStart07 | Start Month Year events 7 | CUS40000 | TW52_EventMMStart07 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18251 | HFFFF | RW
548 | TW53_EventMMStart08 | Start Month Year events 8 | CUS40000 | TW53_EventMMStart08 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18252 | HFFFF | RW
549 | TW54_EventMMStart09 | Start Month Year events 9 | CUS40000 | TW54_EventMMStart09 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18253 | HFFFF | RW
550 | TW55_EventMMStart10 | Start Month Year events 10 | CUS40000 | TW55_EventMMStart10 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18254 | HFFFF | RW
551 | TW56_EventMMStart11 | Start Month Year events 11 | CUS40000 | TW56_EventMMStart11 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18255 | HFFFF | RW
552 | TW57_EventMMStart12 | Start Month Year events 12 | CUS40000 | TW57_EventMMStart12 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18256 | HFFFF | RW
553 | TW58_EventMMStart13 | Start Month Year events 13 | CUS40000 | TW58_EventMMStart13 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18257 | HFFFF | RW
554 | TW59_EventMMStart14 | Start Month Year events 14 | CUS40000 | TW59_EventMMStart14 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18258 | HFFFF | RW
555 | TW60_EventMMStart15 | Start Month Year events 15 | CUS40000 | TW60_EventMMStart15 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18259 | HFFFF | RW
556 | TW61_EventDDStop01 | Stop Day Year events 1 | CUS40000 | TW61_EventDDStop01 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18260 | HFFFF | RW
557 | TW62_EventDDStop02 | Stop Day Year events 2 | CUS40000 | TW62_EventDDStop02 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18261 | HFFFF | RW
558 | TW63_EventDDStop03 | Stop Day Year events 3 | CUS40000 | TW63_EventDDStop03 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18262 | HFFFF | RW
559 | TW64_EventDDStop04 | Stop Day Year events 4 | CUS40000 | TW64_EventDDStop04 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18263 | HFFFF | RW
560 | TW65_EventDDStop05 | Stop Day Year events 5 | CUS40000 | TW65_EventDDStop05 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18264 | HFFFF | RW
561 | TW66_EventDDStop06 | Stop Day Year events 6 | CUS40000 | TW66_EventDDStop06 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18265 | HFFFF | RW
562 | TW67_EventDDStop07 | Stop Day Year events 7 | CUS40000 | TW67_EventDDStop07 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18266 | HFFFF | RW
563 | TW68_EventDDStop08 | Stop Day Year events 8 | CUS40000 | TW68_EventDDStop08 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18267 | HFFFF | RW
564 | TW69_EventDDStop09 | Stop Day Year events 9 | CUS40000 | TW69_EventDDStop09 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18268 | HFFFF | RW
565 | TW70_EventDDStop10 | Stop Day Year events 10 | CUS40000 | TW70_EventDDStop10 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18269 | HFFFF | RW
566 | TW71_EventDDStop11 | Stop Day Year events 11 | CUS40000 | TW71_EventDDStop11 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18270 | HFFFF | RW
567 | TW72_EventDDStop12 | Stop Day Year events 12 | CUS40000 | TW72_EventDDStop12 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18271 | HFFFF | RW
568 | TW73_EventDDStop13 | Stop Day Year events 13 | CUS40000 | TW73_EventDDStop13 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18272 | HFFFF | RW
569 | TW74_EventDDStop14 | Stop Day Year events 14 | CUS40000 | TW74_EventDDStop14 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18273 | HFFFF | RW
570 | TW75_EventDDStop15 | Stop Day Year events 15 | CUS40000 | TW75_EventDDStop15 | PH | PGR00000 | 1 | 31 |  |  | FIX(VMU00027) |  |  |  | P | 18274 | HFFFF | RW
571 | TW76_EventMMStop01 | Stop Month Year events 1 | CUS40000 | TW76_EventMMStop01 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18275 | HFFFF | RW
572 | TW77_EventMMStop02 | Stop Month Year events 1 | CUS40000 | TW77_EventMMStop02 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18276 | HFFFF | RW
573 | TW78_EventMMStop03 | Stop Month Year events 1 | CUS40000 | TW78_EventMMStop03 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18277 | HFFFF | RW
574 | TW79_EventMMStop04 | Stop Month Year events 1 | CUS40000 | TW79_EventMMStop04 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18278 | HFFFF | RW
575 | TW80_EventMMStop05 | Stop Month Year events 1 | CUS40000 | TW80_EventMMStop05 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18279 | HFFFF | RW
576 | TW81_EventMMStop06 | Stop Month Year events 1 | CUS40000 | TW81_EventMMStop06 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18280 | HFFFF | RW
577 | TW82_EventMMStop07 | Stop Month Year events 1 | CUS40000 | TW82_EventMMStop07 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18281 | HFFFF | RW
578 | TW83_EventMMStop08 | Stop Month Year events 1 | CUS40000 | TW83_EventMMStop08 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18282 | HFFFF | RW
579 | TW84_EventMMStop09 | Stop Month Year events 1 | CUS40000 | TW84_EventMMStop09 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18283 | HFFFF | RW
580 | TW85_EventMMStop10 | Stop Month Year events 1 | CUS40000 | TW85_EventMMStop10 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18284 | HFFFF | RW
581 | TW86_EventMMStop11 | Stop Month Year events 1 | CUS40000 | TW86_EventMMStop11 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18285 | HFFFF | RW
582 | TW87_EventMMStop12 | Stop Month Year events 1 | CUS40000 | TW87_EventMMStop12 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18286 | HFFFF | RW
583 | TW88_EventMMStop13 | Stop Month Year events 1 | CUS40000 | TW88_EventMMStop13 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18287 | HFFFF | RW
584 | TW89_EventMMStop14 | Stop Month Year events 1 | CUS40000 | TW89_EventMMStop14 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18288 | HFFFF | RW
585 | TW90_EventMMStop15 | Start Day Year events 1 | CUS40000 | TW90_EventMMStop15 | PH | PGR00000 | 1 | 12 |  |  | FIX(VMU00028) |  |  |  | P | 18289 | HFFFF | RW
586 | LASTCONFIGPARAM | Position Index where next data will be logged | CUS40000 | LASTCONFIGPARAM | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18498 | HFFFF | RW
587 | LogData_NextEntry_Code | Position Index where next data will be logged | CUS40000 | LogData_NextEntry_Code | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 18499 | HFFFF | RW
588 | LogData_FULL_Code | Full Queue Flag | CUS40000 | LogData_FULL_Code | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18500 | HFFFF | RW
589 | LogData_NextEntry_Date |  | CUS40000 | LogData_NextEntry_Date | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 18501 | HFFFF | RW
590 | LogData_FULL_Date |  | CUS40000 | LogData_FULL_Date | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18502 | HFFFF | RW
591 | LogData_NextEntry_Time |  | CUS40000 | LogData_NextEntry_Time | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 18503 | HFFFF | RW
592 | LogData_FULL_Time |  | CUS40000 | LogData_FULL_Time | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18504 | HFFFF | RW
593 | LogData_NextEntry_SecStatus |  | CUS40000 | LogData_NextEntry_SecStatus | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 18505 | HFFFF | RW
594 | LogData_FULL_SecStatus |  | CUS40000 | LogData_FULL_SecStatus | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 18506 | HFFFF | RW
595 | LogDataE2_00 | This Must Be always declared | CUS40000 | LogDataE2_00 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18507 | HFFFF | RW
596 | LogDataE2_01 |  | CUS40000 | LogDataE2_01 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18508 | HFFFF | RW
597 | LogDataE2_02 |  | CUS40000 | LogDataE2_02 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18509 | HFFFF | RW
598 | LogDataE2_03 |  | CUS40000 | LogDataE2_03 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18510 | HFFFF | RW
599 | LogDataE2_04 |  | CUS40000 | LogDataE2_04 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18511 | HFFFF | RW
600 | LogDataE2_05 |  | CUS40000 | LogDataE2_05 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18512 | HFFFF | RW
601 | LogDataE2_06 |  | CUS40000 | LogDataE2_06 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18513 | HFFFF | RW
602 | LogDataE2_07 |  | CUS40000 | LogDataE2_07 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18514 | HFFFF | RW
603 | LogDataE2_08 |  | CUS40000 | LogDataE2_08 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18515 | HFFFF | RW
604 | LogDataE2_09 |  | CUS40000 | LogDataE2_09 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18516 | HFFFF | RW
605 | LogDataE2_10 |  | CUS40000 | LogDataE2_10 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18517 | HFFFF | RW
606 | LogDataE2_11 |  | CUS40000 | LogDataE2_11 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18518 | HFFFF | RW
607 | LogDataE2_12 |  | CUS40000 | LogDataE2_12 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18519 | HFFFF | RW
608 | LogDataE2_13 |  | CUS40000 | LogDataE2_13 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18520 | HFFFF | RW
609 | LogDataE2_14 |  | CUS40000 | LogDataE2_14 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18521 | HFFFF | RW
610 | LogDataE2_15 |  | CUS40000 | LogDataE2_15 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18522 | HFFFF | RW
611 | LogDataE2_16 |  | CUS40000 | LogDataE2_16 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18523 | HFFFF | RW
612 | LogDataE2_17 |  | CUS40000 | LogDataE2_17 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18524 | HFFFF | RW
613 | LogDataE2_18 |  | CUS40000 | LogDataE2_18 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18525 | HFFFF | RW
614 | LogDataE2_19 |  | CUS40000 | LogDataE2_19 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18526 | HFFFF | RW
615 | LogDataE2_20 |  | CUS40000 | LogDataE2_20 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18527 | HFFFF | RW
616 | LogDataE2_21 |  | CUS40000 | LogDataE2_21 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18528 | HFFFF | RW
617 | LogDataE2_22 |  | CUS40000 | LogDataE2_22 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18529 | HFFFF | RW
618 | LogDataE2_23 |  | CUS40000 | LogDataE2_23 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18530 | HFFFF | RW
619 | LogDataE2_24 |  | CUS40000 | LogDataE2_24 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18531 | HFFFF | RW
620 | LogDataE2_25 |  | CUS40000 | LogDataE2_25 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18532 | HFFFF | RW
621 | LogDataE2_26 |  | CUS40000 | LogDataE2_26 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18533 | HFFFF | RW
622 | LogDataE2_27 |  | CUS40000 | LogDataE2_27 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18534 | HFFFF | RW
623 | LogDataE2_28 |  | CUS40000 | LogDataE2_28 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18535 | HFFFF | RW
624 | LogDataE2_29 |  | CUS40000 | LogDataE2_29 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18536 | HFFFF | RW
625 | LogDataE2_30 |  | CUS40000 | LogDataE2_30 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18537 | HFFFF | RW
626 | LogDataE2_31 |  | CUS40000 | LogDataE2_31 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18538 | HFFFF | RW
627 | LogDataE2_32 |  | CUS40000 | LogDataE2_32 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18539 | HFFFF | RW
628 | LogDataE2_33 |  | CUS40000 | LogDataE2_33 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18540 | HFFFF | RW
629 | LogDataE2_34 |  | CUS40000 | LogDataE2_34 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18541 | HFFFF | RW
630 | LogDataE2_35 |  | CUS40000 | LogDataE2_35 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18542 | HFFFF | RW
631 | LogDataE2_36 |  | CUS40000 | LogDataE2_36 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18543 | HFFFF | RW
632 | LogDataE2_37 |  | CUS40000 | LogDataE2_37 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18544 | HFFFF | RW
633 | LogDataE2_38 |  | CUS40000 | LogDataE2_38 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18545 | HFFFF | RW
634 | LogDataE2_39 |  | CUS40000 | LogDataE2_39 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18546 | HFFFF | RW
635 | LogDataE2_40 |  | CUS40000 | LogDataE2_40 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18547 | HFFFF | RW
636 | LogDataE2_41 |  | CUS40000 | LogDataE2_41 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18548 | HFFFF | RW
637 | LogDataE2_42 |  | CUS40000 | LogDataE2_42 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18549 | HFFFF | RW
638 | LogDataE2_43 |  | CUS40000 | LogDataE2_43 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18550 | HFFFF | RW
639 | LogDataE2_44 |  | CUS40000 | LogDataE2_44 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18551 | HFFFF | RW
640 | LogDataE2_45 |  | CUS40000 | LogDataE2_45 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18552 | HFFFF | RW
641 | LogDataE2_46 |  | CUS40000 | LogDataE2_46 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18553 | HFFFF | RW
642 | LogDataE2_47 |  | CUS40000 | LogDataE2_47 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18554 | HFFFF | RW
643 | LogDataE2_48 |  | CUS40000 | LogDataE2_48 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18555 | HFFFF | RW
644 | LogDataE2_49 |  | CUS40000 | LogDataE2_49 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18556 | HFFFF | RW
645 | LogDataE2_50 |  | CUS40000 | LogDataE2_50 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18557 | HFFFF | RW
646 | LogDataE2_51 |  | CUS40000 | LogDataE2_51 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18558 | HFFFF | RW
647 | LogDataE2_52 |  | CUS40000 | LogDataE2_52 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18559 | HFFFF | RW
648 | LogDataE2_53 |  | CUS40000 | LogDataE2_53 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18560 | HFFFF | RW
649 | LogDataE2_54 |  | CUS40000 | LogDataE2_54 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18561 | HFFFF | RW
650 | LogDataE2_55 |  | CUS40000 | LogDataE2_55 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18562 | HFFFF | RW
651 | LogDataE2_56 |  | CUS40000 | LogDataE2_56 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18563 | HFFFF | RW
652 | LogDataE2_57 |  | CUS40000 | LogDataE2_57 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18564 | HFFFF | RW
653 | LogDataE2_58 |  | CUS40000 | LogDataE2_58 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18565 | HFFFF | RW
654 | LogDataE2_60 |  | CUS40000 | LogDataE2_60 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18566 | HFFFF | RW
655 | LogDataE2_59 |  | CUS40000 | LogDataE2_59 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18567 | HFFFF | RW
656 | LogDataE2_61 |  | CUS40000 | LogDataE2_61 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18568 | HFFFF | RW
657 | LogDataE2_62 |  | CUS40000 | LogDataE2_62 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18569 | HFFFF | RW
658 | LogDataE2_63 |  | CUS40000 | LogDataE2_63 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18570 | HFFFF | RW
659 | LogDataE2_64 |  | CUS40000 | LogDataE2_64 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18571 | HFFFF | RW
660 | LogDataE2_65 |  | CUS40000 | LogDataE2_65 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18572 | HFFFF | RW
661 | LogDataE2_66 |  | CUS40000 | LogDataE2_66 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18573 | HFFFF | RW
662 | LogDataE2_67 |  | CUS40000 | LogDataE2_67 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18574 | HFFFF | RW
663 | LogDataE2_68 |  | CUS40000 | LogDataE2_68 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18575 | HFFFF | RW
664 | LogDataE2_69 |  | CUS40000 | LogDataE2_69 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18576 | HFFFF | RW
665 | LogDataE2_70 |  | CUS40000 | LogDataE2_70 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18577 | HFFFF | RW
666 | LogDataE2_71 |  | CUS40000 | LogDataE2_71 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18578 | HFFFF | RW
667 | LogDataE2_72 |  | CUS40000 | LogDataE2_72 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18579 | HFFFF | RW
668 | LogDataE2_73 |  | CUS40000 | LogDataE2_73 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18580 | HFFFF | RW
669 | LogDataE2_74 |  | CUS40000 | LogDataE2_74 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18581 | HFFFF | RW
670 | LogDataE2_75 |  | CUS40000 | LogDataE2_75 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18582 | HFFFF | RW
671 | LogDataE2_76 |  | CUS40000 | LogDataE2_76 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18583 | HFFFF | RW
672 | LogDataE2_77 |  | CUS40000 | LogDataE2_77 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18584 | HFFFF | RW
673 | LogDataE2_78 |  | CUS40000 | LogDataE2_78 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18585 | HFFFF | RW
674 | LogDataE2_79 |  | CUS40000 | LogDataE2_79 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18586 | HFFFF | RW
675 | LogDataE2_80 |  | CUS40000 | LogDataE2_80 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18587 | HFFFF | RW
676 | LogDataE2_81 |  | CUS40000 | LogDataE2_81 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18588 | HFFFF | RW
677 | LogDataE2_82 |  | CUS40000 | LogDataE2_82 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18589 | HFFFF | RW
678 | LogDataE2_83 |  | CUS40000 | LogDataE2_83 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18590 | HFFFF | RW
679 | LogDataE2_84 |  | CUS40000 | LogDataE2_84 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18591 | HFFFF | RW
680 | LogDataE2_85 |  | CUS40000 | LogDataE2_85 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18592 | HFFFF | RW
681 | LogDataE2_86 |  | CUS40000 | LogDataE2_86 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18593 | HFFFF | RW
682 | LogDataE2_87 |  | CUS40000 | LogDataE2_87 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18594 | HFFFF | RW
683 | LogDataE2_89 |  | CUS40000 | LogDataE2_89 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18595 | HFFFF | RW
684 | LogDataE2_88 |  | CUS40000 | LogDataE2_88 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18596 | HFFFF | RW
685 | LogDataE2_90 |  | CUS40000 | LogDataE2_90 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18597 | HFFFF | RW
686 | LogDataE2_91 |  | CUS40000 | LogDataE2_91 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18598 | HFFFF | RW
687 | LogDataE2_92 |  | CUS40000 | LogDataE2_92 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18599 | HFFFF | RW
688 | LogDataE2_93 |  | CUS40000 | LogDataE2_93 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18600 | HFFFF | RW
689 | LogDataE2_94 |  | CUS40000 | LogDataE2_94 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18601 | HFFFF | RW
690 | LogDataE2_95 |  | CUS40000 | LogDataE2_95 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18602 | HFFFF | RW
691 | LogDataE2_97 |  | CUS40000 | LogDataE2_97 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18603 | HFFFF | RW
692 | LogDataE2_96 |  | CUS40000 | LogDataE2_96 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18604 | HFFFF | RW
693 | LogDataE2_98 |  | CUS40000 | LogDataE2_98 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18605 | HFFFF | RW
694 | LogDataE2_99 |  | CUS40000 | LogDataE2_99 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18606 | HFFFF | RW
695 | LogDataE2_100 |  | CUS40000 | LogDataE2_100 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18607 | HFFFF | RW
696 | LogDataE2_101 |  | CUS40000 | LogDataE2_101 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18608 | HFFFF | RW
697 | LogDataE2_102 |  | CUS40000 | LogDataE2_102 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18609 | HFFFF | RW
698 | LogDataE2_103 |  | CUS40000 | LogDataE2_103 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18610 | HFFFF | RW
699 | LogDataE2_104 |  | CUS40000 | LogDataE2_104 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18611 | HFFFF | RW
700 | LogDataE2_105 |  | CUS40000 | LogDataE2_105 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18612 | HFFFF | RW
701 | LogDataE2_106 |  | CUS40000 | LogDataE2_106 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18613 | HFFFF | RW
702 | LogDataE2_107 |  | CUS40000 | LogDataE2_107 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18614 | HFFFF | RW
703 | LogDataE2_108 |  | CUS40000 | LogDataE2_108 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18615 | HFFFF | RW
704 | LogDataE2_109 |  | CUS40000 | LogDataE2_109 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18616 | HFFFF | RW
705 | LogDataE2_110 |  | CUS40000 | LogDataE2_110 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18617 | HFFFF | RW
706 | LogDataE2_111 |  | CUS40000 | LogDataE2_111 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18618 | HFFFF | RW
707 | LogDataE2_112 |  | CUS40000 | LogDataE2_112 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18619 | HFFFF | RW
708 | LogDataE2_113 |  | CUS40000 | LogDataE2_113 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18620 | HFFFF | RW
709 | LogDataE2_114 |  | CUS40000 | LogDataE2_114 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18621 | HFFFF | RW
710 | LogDataE2_115 |  | CUS40000 | LogDataE2_115 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18622 | HFFFF | RW
711 | LogDataE2_116 |  | CUS40000 | LogDataE2_116 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18623 | HFFFF | RW
712 | LogDataE2_117 |  | CUS40000 | LogDataE2_117 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18624 | HFFFF | RW
713 | LogDataE2_118 |  | CUS40000 | LogDataE2_118 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18625 | HFFFF | RW
714 | LogDataE2_119 |  | CUS40000 | LogDataE2_119 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18626 | HFFFF | RW
715 | LogDataE2_120 |  | CUS40000 | LogDataE2_120 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18627 | HFFFF | RW
716 | LogDataE2_121 |  | CUS40000 | LogDataE2_121 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18628 | HFFFF | RW
717 | LogDataE2_122 |  | CUS40000 | LogDataE2_122 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18629 | HFFFF | RW
718 | LogDataE2_123 |  | CUS40000 | LogDataE2_123 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18630 | HFFFF | RW
719 | LogDataE2_124 |  | CUS40000 | LogDataE2_124 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18631 | HFFFF | RW
720 | LogDataE2_125 |  | CUS40000 | LogDataE2_125 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18632 | HFFFF | RW
721 | LogDataE2_126 |  | CUS40000 | LogDataE2_126 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18633 | HFFFF | RW
722 | LogDataE2_127 |  | CUS40000 | LogDataE2_127 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18634 | HFFFF | RW
723 | LogDataE2_128 |  | CUS40000 | LogDataE2_128 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18635 | HFFFF | RW
724 | LogDataE2_129 |  | CUS40000 | LogDataE2_129 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18636 | HFFFF | RW
725 | LogDataE2_130 |  | CUS40000 | LogDataE2_130 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18637 | HFFFF | RW
726 | LogDataE2_131 |  | CUS40000 | LogDataE2_131 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18638 | HFFFF | RW
727 | LogDataE2_132 |  | CUS40000 | LogDataE2_132 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18639 | HFFFF | RW
728 | LogDataE2_133 |  | CUS40000 | LogDataE2_133 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18640 | HFFFF | RW
729 | LogDataE2_134 |  | CUS40000 | LogDataE2_134 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18641 | HFFFF | RW
730 | LogDataE2_136 |  | CUS40000 | LogDataE2_136 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18642 | HFFFF | RW
731 | LogDataE2_137 |  | CUS40000 | LogDataE2_137 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18643 | HFFFF | RW
732 | LogDataE2_135 |  | CUS40000 | LogDataE2_135 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18644 | HFFFF | RW
733 | LogDataE2_138 |  | CUS40000 | LogDataE2_138 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18645 | HFFFF | RW
734 | LogDataE2_139 |  | CUS40000 | LogDataE2_139 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18646 | HFFFF | RW
735 | LogDataE2_140 |  | CUS40000 | LogDataE2_140 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18647 | HFFFF | RW
736 | LogDataE2_141 |  | CUS40000 | LogDataE2_141 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18648 | HFFFF | RW
737 | LogDataE2_142 |  | CUS40000 | LogDataE2_142 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18649 | HFFFF | RW
738 | LogDataE2_143 |  | CUS40000 | LogDataE2_143 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18650 | HFFFF | RW
739 | LogDataE2_144 |  | CUS40000 | LogDataE2_144 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18651 | HFFFF | RW
740 | LogDataE2_145 |  | CUS40000 | LogDataE2_145 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18652 | HFFFF | RW
741 | LogDataE2_146 |  | CUS40000 | LogDataE2_146 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18653 | HFFFF | RW
742 | LogDataE2_147 |  | CUS40000 | LogDataE2_147 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18654 | HFFFF | RW
743 | LogDataE2_148 |  | CUS40000 | LogDataE2_148 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18655 | HFFFF | RW
744 | LogDataE2_149 |  | CUS40000 | LogDataE2_149 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18656 | HFFFF | RW
745 | LogDataE2_150 |  | CUS40000 | LogDataE2_150 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18657 | HFFFF | RW
746 | LogDataE2_151 |  | CUS40000 | LogDataE2_151 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18658 | HFFFF | RW
747 | LogDataE2_152 |  | CUS40000 | LogDataE2_152 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18659 | HFFFF | RW
748 | LogDataE2_153 |  | CUS40000 | LogDataE2_153 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18660 | HFFFF | RW
749 | LogDataE2_154 |  | CUS40000 | LogDataE2_154 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18661 | HFFFF | RW
750 | LogDataE2_155 |  | CUS40000 | LogDataE2_155 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18662 | HFFFF | RW
751 | LogDataE2_156 |  | CUS40000 | LogDataE2_156 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18663 | HFFFF | RW
752 | LogDataE2_158 |  | CUS40000 | LogDataE2_158 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18664 | HFFFF | RW
753 | LogDataE2_157 |  | CUS40000 | LogDataE2_157 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18665 | HFFFF | RW
754 | LogDataE2_159 |  | CUS40000 | LogDataE2_159 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18666 | HFFFF | RW
755 | LogDataE2_160 |  | CUS40000 | LogDataE2_160 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18667 | HFFFF | RW
756 | LogDataE2_161 |  | CUS40000 | LogDataE2_161 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18668 | HFFFF | RW
757 | LogDataE2_162 |  | CUS40000 | LogDataE2_162 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18669 | HFFFF | RW
758 | LogDataE2_163 |  | CUS40000 | LogDataE2_163 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18670 | HFFFF | RW
759 | LogDataE2_164 |  | CUS40000 | LogDataE2_164 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18671 | HFFFF | RW
760 | LogDataE2_165 |  | CUS40000 | LogDataE2_165 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18672 | HFFFF | RW
761 | LogDataE2_166 |  | CUS40000 | LogDataE2_166 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18673 | HFFFF | RW
762 | LogDataE2_167 |  | CUS40000 | LogDataE2_167 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18674 | HFFFF | RW
763 | LogDataE2_168 |  | CUS40000 | LogDataE2_168 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18675 | HFFFF | RW
764 | LogDataE2_169 |  | CUS40000 | LogDataE2_169 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18676 | HFFFF | RW
765 | LogDataE2_170 |  | CUS40000 | LogDataE2_170 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18677 | HFFFF | RW
766 | LogDataE2_171 |  | CUS40000 | LogDataE2_171 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18678 | HFFFF | RW
767 | LogDataE2_172 |  | CUS40000 | LogDataE2_172 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18679 | HFFFF | RW
768 | LogDataE2_173 |  | CUS40000 | LogDataE2_173 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18680 | HFFFF | RW
769 | LogDataE2_174 |  | CUS40000 | LogDataE2_174 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18681 | HFFFF | RW
770 | LogDataE2_175 |  | CUS40000 | LogDataE2_175 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18682 | HFFFF | RW
771 | LogDataE2_176 |  | CUS40000 | LogDataE2_176 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18683 | HFFFF | RW
772 | LogDataE2_177 |  | CUS40000 | LogDataE2_177 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18684 | HFFFF | RW
773 | LogDataE2_178 |  | CUS40000 | LogDataE2_178 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18685 | HFFFF | RW
774 | LogDataE2_179 |  | CUS40000 | LogDataE2_179 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18686 | HFFFF | RW
775 | LogDataE2_180 |  | CUS40000 | LogDataE2_180 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18687 | HFFFF | RW
776 | LogDataE2_181 |  | CUS40000 | LogDataE2_181 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18688 | HFFFF | RW
777 | LogDataE2_182 |  | CUS40000 | LogDataE2_182 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18689 | HFFFF | RW
778 | LogDataE2_183 |  | CUS40000 | LogDataE2_183 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18690 | HFFFF | RW
779 | LogDataE2_184 |  | CUS40000 | LogDataE2_184 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18691 | HFFFF | RW
780 | LogDataE2_185 |  | CUS40000 | LogDataE2_185 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18692 | HFFFF | RW
781 | LogDataE2_186 |  | CUS40000 | LogDataE2_186 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18693 | HFFFF | RW
782 | LogDataE2_187 |  | CUS40000 | LogDataE2_187 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18694 | HFFFF | RW
783 | LogDataE2_188 |  | CUS40000 | LogDataE2_188 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18695 | HFFFF | RW
784 | LogDataE2_189 |  | CUS40000 | LogDataE2_189 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18696 | HFFFF | RW
785 | LogDataE2_190 |  | CUS40000 | LogDataE2_190 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18697 | HFFFF | RW
786 | LogDataE2_191 |  | CUS40000 | LogDataE2_191 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18698 | HFFFF | RW
787 | LogDataE2_192 |  | CUS40000 | LogDataE2_192 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18699 | HFFFF | RW
788 | LogDataE2_193 |  | CUS40000 | LogDataE2_193 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18700 | HFFFF | RW
789 | LogDataE2_194 |  | CUS40000 | LogDataE2_194 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18701 | HFFFF | RW
790 | LogDataE2_195 |  | CUS40000 | LogDataE2_195 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18702 | HFFFF | RW
791 | LogDataE2_196 |  | CUS40000 | LogDataE2_196 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18703 | HFFFF | RW
792 | LogDataE2_197 |  | CUS40000 | LogDataE2_197 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18704 | HFFFF | RW
793 | LogDataE2_198 |  | CUS40000 | LogDataE2_198 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18705 | HFFFF | RW
794 | LogDataE2_199 |  | CUS40000 | LogDataE2_199 | PH | PGR00000 | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 18706 | HFFFF | RW
795 | UNIT_SERIAL_NUMBER1 | Unit Serial Number 1 | CUS40000 | UNIT_SERIAL_NUMBER1 | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 19496 | HFFFF | RW
796 | UNIT_SERIAL_NUMBER2 | Unit Serial Number 2 | CUS40000 | UNIT_SERIAL_NUMBER2 | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 19497 | HFFFF | RW
797 | ENDHISTORICAL |  | CUS40000 | ENDHISTORICAL | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19498 | HFFFF | RW
798 | Unit_KbdOnOff | On/Off status from keyboard | CUS40000 | Unit_KbdOnOff | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19499 | HFFFF | RW
799 | Unit_KbdMode_E2 | Mode status from keyboard | CUS40000 | Unit_KbdMode_E2 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 19500 | HFFFF | RW
800 | Unit_KbdEco_E2 | Comfort/Economy/Night status from keyboard | CUS40000 | Unit_KbdEco_E2 | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 19501 | HFFFF | RW
801 | TW_ActiveEvent | Current Event | CUS40000 | TW_ActiveEvent | PH | PGR00000 | 0 | 15 |  |  | FIX(VMU00020) |  |  |  | P | 19502 | HFFFF | RW
802 | EE_RTCerror |  | CUS40000 | EE_RTCerror | PH | PGR00000 | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 19503 | HFFFF | RW
803 | ENDINTERNAL |  | CUS40000 | ENDINTERNAL | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19798 | HFFFF | RW
804 | UnitHoursE2 | Unit Hours | CUS40000 | UnitHoursE2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19799 | HFFFFFFFF | RW
805 | FanSupplyHoursE2 | Fan Supply Running Hours | CUS40000 | FanSupplyHoursE2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19801 | HFFFFFFFF | RW
806 | FanReturnHoursE2 | Fan Return Running Hours | CUS40000 | FanReturnHoursE2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19803 | HFFFFFFFF | RW
807 | FanSupplyBckHoursE2 | Fan Supply Backup Running Hours | CUS40000 | FanSupplyBckHoursE2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19805 | HFFFFFFFF | RW
808 | FanReturnBckHoursE2 | Fan Return Backup Running Hours | CUS40000 | FanReturnBckHoursE2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19807 | HFFFFFFFF | RW
809 | Fan_Maintenance_Supply | Fan Main Supply Forced Off for maintenance | CUS40000 | Fan_Maintenance_Supply | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19809 | HFFFF | RW
810 | Fan_Maintenance_Return | Fan Main Return Forced Off for maintenance | CUS40000 | Fan_Maintenance_Return | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19810 | HFFFF | RW
811 | Fan_Maintenance_SupplyBck | Fan Supply 2 Forced Off for maintenance | CUS40000 | Fan_Maintenance_SupplyBck | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19811 | HFFFF | RW
812 | Fan_Maintenance_ReturnBck | Fan Return 2 Forced Off for maintenance | CUS40000 | Fan_Maintenance_ReturnBck | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19812 | HFFFF | RW
813 | Fan_Maintenance_Supply1b | Fan Main Supply b Forced Off for maintenance | CUS40000 | Fan_Maintenance_Supply1b | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19813 | HFFFF | RW
814 | Fan_Maintenance_Supply1c | Fan Main Supply c Forced Off for maintenance | CUS40000 | Fan_Maintenance_Supply1c | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19814 | HFFFF | RW
815 | Fan_Maintenance_Return1b | Fan Main Return b Forced Off for maintenance | CUS40000 | Fan_Maintenance_Return1b | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19815 | HFFFF | RW
816 | Fan_Maintenance_Return1c | Fan Main Return c Forced Off for maintenance | CUS40000 | Fan_Maintenance_Return1c | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19816 | HFFFF | RW
817 | Fan_Maintenance_Supply2b | Fan Supply 2b Forced Off for maintenance | CUS40000 | Fan_Maintenance_Supply2b | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19817 | HFFFF | RW
818 | Fan_Maintenance_Supply2c | Fan Supply 2c Forced Off for maintenance | CUS40000 | Fan_Maintenance_Supply2c | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19818 | HFFFF | RW
819 | Fan_Maintenance_Return2b | Fan Return 2b Forced Off for maintenance | CUS40000 | Fan_Maintenance_Return2b | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19819 | HFFFF | RW
820 | Fan_Maintenance_Return2c | Fan Return 2c Forced Off for maintenance | CUS40000 | Fan_Maintenance_Return2c | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19820 | HFFFF | RW
821 | Fan_Modbus_Configured_E2 | Modbus Fan have been configured | CUS40000 | Fan_Modbus_Configured_E2 | PH | PGR00000 | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 19821 | HFFFF | RW
822 | udhoursCU1E2 | Condensing Unit 1 Running Hours | CUS40000 | udhoursCU1E2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19822 | HFFFFFFFF | RW
823 | udhoursCU2E2 | Condensing Unit 2 Running Hours | CUS40000 | udhoursCU2E2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19824 | HFFFFFFFF | RW
824 | udhoursCU3E2 | Condensing Unit 3 Running Hours | CUS40000 | udhoursCU3E2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19826 | HFFFFFFFF | RW
825 | udhoursCU4E2 | Condensing Unit 4 Running Hours | CUS40000 | udhoursCU4E2 | PH | PGR00000 | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 19828 | HFFFFFFFF | RW
826 | CU1_Maintenance | Condensing Unit 1 Forced Off for maintenance | CUS40000 | CU1_Maintenance | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19830 | HFFFF | RW
827 | CU2_Maintenance | Condensing Unit 2 Forced Off for maintenance | CUS40000 | CU2_Maintenance | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19831 | HFFFF | RW
828 | CU3_Maintenance | Condensing Unit 3 Forced Off for maintenance | CUS40000 | CU3_Maintenance | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19832 | HFFFF | RW
829 | CU4_Maintenance | Condensing Unit 4 Forced Off for maintenance | CUS40000 | CU4_Maintenance | PH | PGR00000 | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 19833 | HFFFF | RW
830 | BACNET_SUBNET | Bacnet Device Subnet | CUS40000 | BACNET_SUBNET | PH | PGR00000 | 0 | 63 |  |  | FIX(VMU00020) |  |  |  | P | 16707 | HFFFF | RW
Note on B1: HELP: Try to keep the lenght to no more than 3 chars. Use ENGLISH abbreviations.
Note on D1: HELP: Description code (ex: PCR00050)
Note on E1: HELP: Possible values (input => output): 1) numerical => "string {numerical}" 2) string code => string {actual string from string code} 3) blank
Note on F1: HELP: 1) SP: Setpoint 2) PR: Visible paramiter 3) PH: Hidden parameter 4) VC: Folder parameter visibility 5) VP: Parameter visibility 6) VD: Dynamic visibility 7) TA: Calibration Parameters
Note on G1: HELP: Group or groups the given parameter belongs to. Use ";" to separate the group code.
Note on H1: HELP: lower limit: 1) numerical value: ex. 200; 2) parameter value: ex. Param(LSE)
Note on I1: HELP: lower limit: 1) numerical value: ex. 200; 2) parameter value: ex. Param(LSE)
Note on J1: HELP: 1) blank 2) FIX(+/- num): VALUE*10^(+/- num)
Note on K1: HELP: 1) BLANK: absolute value 2) TRUE: signed value
Note on L1: HELP: Measurement unit string: 1) FIX(VMU00018) => Measurement unit is fixed 2) INT({0=VMU00018,1=VMU00020},PARAM(dro)) => Measurement unit is parametrized
Note on M1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on N1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence and writing sequence separated by a semicolon ";". The value format are: a) 122; b) H2002 (Hex value)
Note on O1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on P1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) W: 0x04 and 0x16 Modbus Command
Note on Q1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on R1: HELP: Micronet and Modbus filter: 1) If the resource is a numeric value, then this cell contains the bitmask to be applied to the value (e.g. H01 or HFFFF) and the information about the value endiannes (e.g. REV(HFFFF) for a little endian or HFFFF for a big endian value). 2) If the resource is an array of bytes or a string, then this cell contains the length of the array, in the format A[x] (e.g. use A[10] for a 10 bytes string). If an odd value is provided, the value will be rounded up to the next even value when the modbus protocol is used.
Note on S1: HELP: Resource can be one of: 1) R: only read value; 2) W: only write value; 3) RW: Read and Write value
Note on T1: HELP: PARAMETERS (LABEL): 1) BLANK: the "parameter" has visibility 2) "NONE": the "parameter" has no visibility PARAMETERS VISIBILITY (vis_LABEL): 1) Params(LABEL): LABEL is the parameter to which this visibility applies to. 2) Params(NONE): the "parameter visibility" is not linked to any parameter
Note on U1: HELP: Position of the parameter in the EEPROM map. The position is the index of the corresponding starting word.
Note on V1: HELP: Filter to be applied to the EEPROM map memory area (at WORD_INDEX position) to get/set the given parameter.
Note on W1: HELP: 1) TRUE: item visible into custom model;
Note on X1: HELP: Reserved use
Note on Y1: HELP: Possible values are: 1) ADDRESS 2) PASSWORD
Note on Z1: HELP: Combine the numerical value with a description string. Examples: 0 -> "NO", 1-> "YES" 0 -> "OFF", 1 -> "ON 0 -> "COMPRESSOR HOURS", 1 -> "DEVICE HOURS", 2 -> "RTC" Field separator is the ";" character
Note on AA1: HELP: 1) blank: do not insert this item into product manual 2) TRUE: insert this item into product manual
Note on AB1: HELP: Possible values: 1) blank: the new value is effective immediately 2) RESET: the new value is running after instrument reset

## Client
INDEX | LABEL | DESCRIPTION | DESCRIPTION_CODE | PROGRESSIVE | GROUPS | LOW_LIMIT | HIGH_LIMIT | FORMAT | COMPLEMENTED | MEASUREMENT_UNIT | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER | EXISTENCE | TYPE | VALUE_CONDITION | TEST_CONDITION | TYPE_CODE | WRITE_SEQUENCE | OPTIONS | MARCOMM_MANUAL | EXCLUSION
1 | AllocationCmdSet | Allocation command | CUS40000 | AllocationCmdSet |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 8959 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
2 | AllocationNextResReq | Used by HMI to get the next available logic resource | CUS40000 | AllocationNextResReq |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8960 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
3 | ioSV_base_AI_01 | Temporary: Logic Allocation of the physical input | CUS40000 | ioSV_base_AI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8961 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
4 | ioSV_base_AI_02 | Save command required to be effective | CUS40000 | ioSV_base_AI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8962 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
5 | ioSV_base_AI_03 |  | CUS40000 | ioSV_base_AI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8963 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
6 | ioSV_base_AI_04 |  | CUS40000 | ioSV_base_AI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8964 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
7 | ioSV_base_AI_05 |  | CUS40000 | ioSV_base_AI_05 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8965 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
8 | ioSV_base_AI_06 |  | CUS40000 | ioSV_base_AI_06 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8966 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
9 | ioSV_base_AI_07 |  | CUS40000 | ioSV_base_AI_07 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8967 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
10 | ioSV_base_AI_08 |  | CUS40000 | ioSV_base_AI_08 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8968 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
11 | ioSV_base_AI_09 |  | CUS40000 | ioSV_base_AI_09 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8969 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
12 | ioSV_base_AI_10 |  | CUS40000 | ioSV_base_AI_10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8970 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
13 | ioSV_base_AI_11 |  | CUS40000 | ioSV_base_AI_11 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8971 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
14 | ioSV_base_AI_12 |  | CUS40000 | ioSV_base_AI_12 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8972 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
15 | ioSV_exp1_AI_01 |  | CUS40000 | ioSV_exp1_AI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8973 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
16 | ioSV_exp1_AI_02 |  | CUS40000 | ioSV_exp1_AI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8974 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
17 | ioSV_exp1_AI_03 |  | CUS40000 | ioSV_exp1_AI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8975 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
18 | ioSV_exp1_AI_04 |  | CUS40000 | ioSV_exp1_AI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8976 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
19 | ioSV_exp2_AI_01 |  | CUS40000 | ioSV_exp2_AI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8977 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
20 | ioSV_exp2_AI_02 |  | CUS40000 | ioSV_exp2_AI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8978 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
21 | ioSV_exp2_AI_03 |  | CUS40000 | ioSV_exp2_AI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8979 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
22 | ioSV_exp2_AI_04 |  | CUS40000 | ioSV_exp2_AI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8980 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
23 | ioSV_free1 |  | CUS40000 | ioSV_free1 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8981 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
24 | ioSV_free2 |  | CUS40000 | ioSV_free2 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8982 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
25 | ioSV_free3 |  | CUS40000 | ioSV_free3 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8983 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
26 | ioSV_free4 |  | CUS40000 | ioSV_free4 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8984 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
27 | ioSV_free5 |  | CUS40000 | ioSV_free5 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8985 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
28 | ioSV_free6 |  | CUS40000 | ioSV_free6 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8986 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
29 | ioSV_free7 |  | CUS40000 | ioSV_free7 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8987 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
30 | ioSV_free8 |  | CUS40000 | ioSV_free8 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8988 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
31 | ioSV_base_DI_01 |  | CUS40000 | ioSV_base_DI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8989 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
32 | ioSV_base_DI_02 |  | CUS40000 | ioSV_base_DI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8990 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
33 | ioSV_base_DI_03 |  | CUS40000 | ioSV_base_DI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8991 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
34 | ioSV_base_DI_04 |  | CUS40000 | ioSV_base_DI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8992 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
35 | ioSV_base_DI_05 |  | CUS40000 | ioSV_base_DI_05 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8993 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
36 | ioSV_base_DI_06 |  | CUS40000 | ioSV_base_DI_06 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8994 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
37 | ioSV_base_DI_07 |  | CUS40000 | ioSV_base_DI_07 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8995 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
38 | ioSV_base_DI_08 |  | CUS40000 | ioSV_base_DI_08 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8996 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
39 | ioSV_base_DI_09 |  | CUS40000 | ioSV_base_DI_09 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8997 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
40 | ioSV_base_DI_10 |  | CUS40000 | ioSV_base_DI_10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8998 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
41 | ioSV_base_DI_11 |  | CUS40000 | ioSV_base_DI_11 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 8999 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
42 | ioSV_base_DI_12 |  | CUS40000 | ioSV_base_DI_12 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9000 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
43 | ioSV_exp1_DI_01 |  | CUS40000 | ioSV_exp1_DI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9001 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
44 | ioSV_exp1_DI_02 |  | CUS40000 | ioSV_exp1_DI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9002 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
45 | ioSV_exp1_DI_03 |  | CUS40000 | ioSV_exp1_DI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9003 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
46 | ioSV_exp1_DI_04 |  | CUS40000 | ioSV_exp1_DI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9004 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
47 | ioSV_exp2_DI_01 |  | CUS40000 | ioSV_exp2_DI_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9005 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
48 | ioSV_exp2_DI_02 |  | CUS40000 | ioSV_exp2_DI_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9006 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
49 | ioSV_exp2_DI_03 |  | CUS40000 | ioSV_exp2_DI_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9007 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
50 | ioSV_exp2_DI_04 |  | CUS40000 | ioSV_exp2_DI_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9008 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
51 | ioSV_free9 |  | CUS40000 | ioSV_free9 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9009 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
52 | ioSV_free10 |  | CUS40000 | ioSV_free10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9010 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
53 | ioSV_free11 |  | CUS40000 | ioSV_free11 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9011 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
54 | ioSV_free12 |  | CUS40000 | ioSV_free12 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9012 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
55 | ioSV_free13 |  | CUS40000 | ioSV_free13 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9013 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
56 | ioSV_free14 |  | CUS40000 | ioSV_free14 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9014 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
57 | ioSV_free15 |  | CUS40000 | ioSV_free15 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9015 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
58 | ioSV_free16 |  | CUS40000 | ioSV_free16 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9016 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
59 | ioSV_base_DO_01 | Temporary: Logic Allocation of the physical output | CUS40000 | ioSV_base_DO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9017 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
60 | ioSV_base_DO_02 | Save command required to be effective | CUS40000 | ioSV_base_DO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9018 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
61 | ioSV_base_DO_03 |  | CUS40000 | ioSV_base_DO_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9019 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
62 | ioSV_base_DO_04 |  | CUS40000 | ioSV_base_DO_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9020 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
63 | ioSV_base_DO_05 |  | CUS40000 | ioSV_base_DO_05 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9021 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
64 | ioSV_base_DO_06 |  | CUS40000 | ioSV_base_DO_06 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9022 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
65 | ioSV_base_DO_07 |  | CUS40000 | ioSV_base_DO_07 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9023 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
66 | ioSV_base_DO_08 |  | CUS40000 | ioSV_base_DO_08 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9024 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
67 | ioSV_base_DO_09 |  | CUS40000 | ioSV_base_DO_09 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9025 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
68 | ioSV_base_DO_10 |  | CUS40000 | ioSV_base_DO_10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9026 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
69 | ioSV_base_DO_11 |  | CUS40000 | ioSV_base_DO_11 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9027 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
70 | ioSV_base_DO_12 |  | CUS40000 | ioSV_base_DO_12 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9028 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
71 | ioSV_exp1_DO_01 |  | CUS40000 | ioSV_exp1_DO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9029 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
72 | ioSV_exp1_DO_02 |  | CUS40000 | ioSV_exp1_DO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9030 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
73 | ioSV_exp1_DO_03 |  | CUS40000 | ioSV_exp1_DO_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9031 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
74 | ioSV_exp1_DO_04 |  | CUS40000 | ioSV_exp1_DO_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9032 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
75 | ioSV_exp2_DO_01 |  | CUS40000 | ioSV_exp2_DO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9033 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
76 | ioSV_exp2_DO_02 |  | CUS40000 | ioSV_exp2_DO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9034 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
77 | ioSV_exp2_DO_03 |  | CUS40000 | ioSV_exp2_DO_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9035 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
78 | ioSV_exp2_DO_04 |  | CUS40000 | ioSV_exp2_DO_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9036 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
79 | ioSV_free18 |  | CUS40000 | ioSV_free18 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9038 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
80 | ioSV_free17 |  | CUS40000 | ioSV_free17 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9037 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
81 | ioSV_free19 |  | CUS40000 | ioSV_free19 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9039 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
82 | ioSV_free20 |  | CUS40000 | ioSV_free20 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9040 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
83 | ioSV_free21 |  | CUS40000 | ioSV_free21 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9041 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
84 | ioSV_free22 |  | CUS40000 | ioSV_free22 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9042 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
85 | ioSV_free23 |  | CUS40000 | ioSV_free23 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9043 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
86 | ioSV_free24 |  | CUS40000 | ioSV_free24 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9044 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
87 | ioSV_base_AO_01 |  | CUS40000 | ioSV_base_AO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9045 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
88 | ioSV_base_AO_02 |  | CUS40000 | ioSV_base_AO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9046 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
89 | ioSV_base_AO_03 |  | CUS40000 | ioSV_base_AO_03 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9047 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
90 | ioSV_base_AO_04 |  | CUS40000 | ioSV_base_AO_04 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9048 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
91 | ioSV_base_AO_05 |  | CUS40000 | ioSV_base_AO_05 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9049 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
92 | ioSV_base_AO_06 |  | CUS40000 | ioSV_base_AO_06 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9050 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
93 | ioSV_exp1_AO_01 |  | CUS40000 | ioSV_exp1_AO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9051 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
94 | ioSV_exp1_AO_02 |  | CUS40000 | ioSV_exp1_AO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9052 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
95 | ioSV_exp2_AO_01 |  | CUS40000 | ioSV_exp2_AO_01 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9053 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
96 | ioSV_exp2_AO_02 |  | CUS40000 | ioSV_exp2_AO_02 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9054 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
97 | ioSV_free25 |  | CUS40000 | ioSV_free25 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9055 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
98 | ioSV_free26 |  | CUS40000 | ioSV_free26 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9056 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
99 | ioSV_free27 |  | CUS40000 | ioSV_free27 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9057 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
100 | ioSV_free28 |  | CUS40000 | ioSV_free28 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9058 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
101 | ioSV_free29 |  | CUS40000 | ioSV_free29 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9059 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
102 | ioSV_free30 |  | CUS40000 | ioSV_free30 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9060 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
103 | ioSV_free31 |  | CUS40000 | ioSV_free31 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9061 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
104 | ioSV_free32 |  | CUS40000 | ioSV_free32 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9062 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
105 | ioSV_base_AI_0102 | Temporary: AI probe configuration | CUS40000 | ioSV_base_AI_0102 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9063 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
106 | ioSV_base_AI_0304 | Save command required to be effective | CUS40000 | ioSV_base_AI_0304 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9064 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
107 | ioSV_base_AI_0506 |  | CUS40000 | ioSV_base_AI_0506 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9065 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
108 | ioSV_base_AI_0708 |  | CUS40000 | ioSV_base_AI_0708 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9066 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
109 | ioSV_base_AI_0910 |  | CUS40000 | ioSV_base_AI_0910 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9067 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
110 | ioSV_base_AI_1112 |  | CUS40000 | ioSV_base_AI_1112 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9068 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
111 | ioSV_exp1_AI_0102 |  | CUS40000 | ioSV_exp1_AI_0102 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9069 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
112 | ioSV_exp1_AI_0304 |  | CUS40000 | ioSV_exp1_AI_0304 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9070 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
113 | ioSV_exp2_AI_0102 |  | CUS40000 | ioSV_exp2_AI_0102 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9071 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
114 | ioSV_exp2_AI_0304 |  | CUS40000 | ioSV_exp2_AI_0304 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9072 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
115 | ioSV_free33 |  | CUS40000 | ioSV_free33 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9073 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
116 | ioSV_free34 |  | CUS40000 | ioSV_free34 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9074 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
117 | ioSV_free35 |  | CUS40000 | ioSV_free35 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9075 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
118 | ioSV_free36 |  | CUS40000 | ioSV_free36 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9076 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
119 | ioSV_free37 |  | CUS40000 | ioSV_free37 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9077 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
120 | ioSV_free38 |  | CUS40000 | ioSV_free38 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9078 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
121 | ioSV_free39 |  | CUS40000 | ioSV_free39 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9079 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
122 | ioSV_free40 |  | CUS40000 | ioSV_free40 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9080 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
123 | ioSV_base_AI01_min | Temporary: AI ranges | CUS40000 | ioSV_base_AI01_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9081 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
124 | ioSV_base_AI01_max | Save command required to be effective | CUS40000 | ioSV_base_AI01_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9082 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
125 | ioSV_base_AI02_min |  | CUS40000 | ioSV_base_AI02_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9083 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
126 | ioSV_base_AI02_max |  | CUS40000 | ioSV_base_AI02_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9084 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
127 | ioSV_base_AI03_min |  | CUS40000 | ioSV_base_AI03_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9085 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
128 | ioSV_base_AI03_max |  | CUS40000 | ioSV_base_AI03_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9086 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
129 | ioSV_base_AI04_min |  | CUS40000 | ioSV_base_AI04_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9087 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
130 | ioSV_base_AI04_max |  | CUS40000 | ioSV_base_AI04_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9088 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
131 | ioSV_base_AI05_min |  | CUS40000 | ioSV_base_AI05_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9089 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
132 | ioSV_base_AI05_max |  | CUS40000 | ioSV_base_AI05_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9090 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
133 | ioSV_base_AI06_min |  | CUS40000 | ioSV_base_AI06_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9091 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
134 | ioSV_base_AI06_max |  | CUS40000 | ioSV_base_AI06_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9092 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
135 | ioSV_base_AI07_min |  | CUS40000 | ioSV_base_AI07_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9093 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
136 | ioSV_base_AI07_max |  | CUS40000 | ioSV_base_AI07_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9094 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
137 | ioSV_base_AI08_min |  | CUS40000 | ioSV_base_AI08_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9095 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
138 | ioSV_base_AI08_max |  | CUS40000 | ioSV_base_AI08_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9096 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
139 | ioSV_base_AI09_min |  | CUS40000 | ioSV_base_AI09_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9097 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
140 | ioSV_base_AI09_max |  | CUS40000 | ioSV_base_AI09_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9098 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
141 | ioSV_base_AI10_min |  | CUS40000 | ioSV_base_AI10_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9099 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
142 | ioSV_base_AI10_max |  | CUS40000 | ioSV_base_AI10_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9100 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
143 | ioSV_base_AI11_min |  | CUS40000 | ioSV_base_AI11_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9101 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
144 | ioSV_base_AI11_max |  | CUS40000 | ioSV_base_AI11_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9102 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
145 | ioSV_base_AI12_min |  | CUS40000 | ioSV_base_AI12_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9103 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
146 | ioSV_base_AI12_max |  | CUS40000 | ioSV_base_AI12_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9104 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
147 | ioSV_exp1_AI01_min |  | CUS40000 | ioSV_exp1_AI01_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9105 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
148 | ioSV_exp1_AI01_max |  | CUS40000 | ioSV_exp1_AI01_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9106 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
149 | ioSV_exp1_AI02_max |  | CUS40000 | ioSV_exp1_AI02_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9108 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
150 | ioSV_exp1_AI02_min |  | CUS40000 | ioSV_exp1_AI02_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9107 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
151 | ioSV_exp1_AI03_min |  | CUS40000 | ioSV_exp1_AI03_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9109 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
152 | ioSV_exp1_AI03_max |  | CUS40000 | ioSV_exp1_AI03_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9110 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
153 | ioSV_exp1_AI04_min |  | CUS40000 | ioSV_exp1_AI04_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9111 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
154 | ioSV_exp1_AI04_max |  | CUS40000 | ioSV_exp1_AI04_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9112 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
155 | ioSV_exp2_AI01_min |  | CUS40000 | ioSV_exp2_AI01_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9113 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
156 | ioSV_exp2_AI01_max |  | CUS40000 | ioSV_exp2_AI01_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9114 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
157 | ioSV_exp2_AI02_min |  | CUS40000 | ioSV_exp2_AI02_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9115 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
158 | ioSV_exp2_AI02_max |  | CUS40000 | ioSV_exp2_AI02_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9116 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
159 | ioSV_exp2_AI03_min |  | CUS40000 | ioSV_exp2_AI03_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9117 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
160 | ioSV_exp2_AI03_max |  | CUS40000 | ioSV_exp2_AI03_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9118 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
161 | ioSV_exp2_AI04_min |  | CUS40000 | ioSV_exp2_AI04_min |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9119 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
162 | ioSV_exp2_AI04_max |  | CUS40000 | ioSV_exp2_AI04_max |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9120 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
163 | ioSV_free41 |  | CUS40000 | ioSV_free41 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9121 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
164 | ioSV_free42 |  | CUS40000 | ioSV_free42 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9122 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
165 | ioSV_free43 |  | CUS40000 | ioSV_free43 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9123 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
166 | ioSV_free44 |  | CUS40000 | ioSV_free44 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9124 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
167 | ioSV_free45 |  | CUS40000 | ioSV_free45 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9125 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
168 | ioSV_free46 |  | CUS40000 | ioSV_free46 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9126 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
169 | ioSV_free47 |  | CUS40000 | ioSV_free47 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9127 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
170 | ioSV_free48 |  | CUS40000 | ioSV_free48 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9128 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
171 | ioSV_free49 |  | CUS40000 | ioSV_free49 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9129 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
172 | ioSV_free50 |  | CUS40000 | ioSV_free50 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9130 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
173 | ioSV_free51 |  | CUS40000 | ioSV_free51 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9131 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
174 | ioSV_free52 |  | CUS40000 | ioSV_free52 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9132 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
175 | ioSV_free53 |  | CUS40000 | ioSV_free53 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9133 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
176 | ioSV_free54 |  | CUS40000 | ioSV_free54 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9134 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
177 | ioSV_free55 |  | CUS40000 | ioSV_free55 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9135 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
178 | ioSV_free56 |  | CUS40000 | ioSV_free56 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9136 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
179 | EnableTestOutput | Enable test output | CUS40000 | EnableTestOutput |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9137 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
180 | aoTst_Visibility1 | Test AO visibility bit - Word 1 | CUS40000 | aoTst_Visibility1 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9138 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
181 | aoTst_Visibility2 | Test AO visibility bit - Word 2 | CUS40000 | aoTst_Visibility2 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9139 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
182 | aoTst_Visibility3 | Test AO visibility bit - Word 3 | CUS40000 | aoTst_Visibility3 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9140 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
183 | aoTst_EnManual1 | Test AO Force/Auto bit - Word 1 | CUS40000 | aoTst_EnManual1 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9141 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
184 | aoTst_EnManual2 | Test AO Force/Auto bit - Word 2 | CUS40000 | aoTst_EnManual2 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9142 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
185 | aoTst_EnManual3 | Test AO Force/Auto bit - Word 3 | CUS40000 | aoTst_EnManual3 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9143 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
186 | aoTst_LogicIndex_0 | Test AO - Supply Fan | CUS40000 | aoTst_LogicIndex_0 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9144 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
187 | aoTst_LogicIndex_1 | Test AO - Return Fan | CUS40000 | aoTst_LogicIndex_1 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9145 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
188 | aoTst_LogicIndex_2 | Test AO - Ext. Dampers | CUS40000 | aoTst_LogicIndex_2 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9146 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
189 | aoTst_LogicIndex_3 | Test AO - Bypass Damper | CUS40000 | aoTst_LogicIndex_3 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9147 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
190 | aoTst_LogicIndex_4 | Test AO - Modulating Cool - C/H | CUS40000 | aoTst_LogicIndex_4 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9148 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
191 | aoTst_LogicIndex_5 | Test AO - Modulating Heat | CUS40000 | aoTst_LogicIndex_5 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9149 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
192 | aoTst_LogicIndex_6 | Test AO - Pre Heater | CUS40000 | aoTst_LogicIndex_6 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9150 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
193 | aoTst_LogicIndex_7 | Test AO - Post Heater | CUS40000 | aoTst_LogicIndex_7 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9151 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
194 | aoTst_LogicIndex_8 | Test AO - Rotary Wheel / Exchanger | CUS40000 | aoTst_LogicIndex_8 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9152 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
195 | aoTst_LogicIndex_9 | Test AO - Humidifier | CUS40000 | aoTst_LogicIndex_9 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9153 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
196 | aoTst_LogicIndex_10 | Test AO - Cond. Unit 1 | CUS40000 | aoTst_LogicIndex_10 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9154 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
197 | aoTst_LogicIndex_11 | Test AO - Cond. Unit 2 | CUS40000 | aoTst_LogicIndex_11 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9155 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
198 | aoTst_LogicIndex_12 | Test AO - Cond. Unit 3 | CUS40000 | aoTst_LogicIndex_12 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9156 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
199 | aoTst_LogicIndex_13 | Test AO - Cond. Unit 4 | CUS40000 | aoTst_LogicIndex_13 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9157 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
200 | aoTst_free5 |  | CUS40000 | aoTst_free5 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9158 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
201 | aoTst_free6 |  | CUS40000 | aoTst_free6 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9159 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
202 | aoTst_free7 |  | CUS40000 | aoTst_free7 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9160 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
203 | aoTst_free8 |  | CUS40000 | aoTst_free8 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9161 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
204 | aoTst_free9 |  | CUS40000 | aoTst_free9 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9162 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
205 | aoTst_free10 |  | CUS40000 | aoTst_free10 |  | 0 | 1000 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9163 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
206 | doTst_Visibility1 | Test DO visibility bit - Word 1 | CUS40000 | doTst_Visibility1 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9164 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
207 | doTst_Visibility2 | Test DO visibility bit - Word 2 | CUS40000 | doTst_Visibility2 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9165 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
208 | doTst_Visibility3 | Test DO visibility bit - Word 3 | CUS40000 | doTst_Visibility3 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9166 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
209 | doTst_EnManual1 | Test DO Force/Auto bit - Word 1 | CUS40000 | doTst_EnManual1 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9167 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
210 | doTst_EnManual2 | Test DO Force/Auto bit - Word 2 | CUS40000 | doTst_EnManual2 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9168 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
211 | doTst_EnManual3 | Test DO Force/Auto bit - Word 3 | CUS40000 | doTst_EnManual3 |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 9169 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
212 | doTst_LogicIndex_0 | Test DO - Supply Fan | CUS40000 | doTst_LogicIndex_0 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9170 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
213 | doTst_LogicIndex_1 | Test DO - Return Fan | CUS40000 | doTst_LogicIndex_1 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9171 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
214 | doTst_LogicIndex_2 | Test DO - On Off | CUS40000 | doTst_LogicIndex_2 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9172 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
215 | doTst_LogicIndex_3 | Test DO - Alarm | CUS40000 | doTst_LogicIndex_3 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9173 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
216 | doTst_LogicIndex_4 | Test DO - Mode | CUS40000 | doTst_LogicIndex_4 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9174 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
217 | doTst_LogicIndex_5 | Test DO - Ext. Dampers | CUS40000 | doTst_LogicIndex_5 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9175 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
218 | doTst_LogicIndex_6 | Test DO - Bypass Damper | CUS40000 | doTst_LogicIndex_6 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9176 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
219 | doTst_LogicIndex_7 | Test DO - Supply Damper | CUS40000 | doTst_LogicIndex_7 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9177 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
220 | doTst_LogicIndex_8 | Test DO - Return Damper | CUS40000 | doTst_LogicIndex_8 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9178 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
221 | doTst_LogicIndex_9 | Test DO - Pump Preheat | CUS40000 | doTst_LogicIndex_9 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9179 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
222 | doTst_LogicIndex_10 | Test DO - Pump Postheat | CUS40000 | doTst_LogicIndex_10 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9180 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
223 | doTst_LogicIndex_11 | Test DO - Cool/CH Pump | CUS40000 | doTst_LogicIndex_11 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9181 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
224 | doTst_LogicIndex_12 | Test DO - C/CH Step - Condensing Unit 1 | CUS40000 | doTst_LogicIndex_12 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9182 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
225 | doTst_LogicIndex_13 | Test DO - C/CH Step - Condensing Unit 2 | CUS40000 | doTst_LogicIndex_13 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9183 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
226 | doTst_LogicIndex_14 | Test DO - C/CH Step - Condensing Unit 3 | CUS40000 | doTst_LogicIndex_14 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9184 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
227 | doTst_LogicIndex_15 | Test DO - C/CH Step - Condensing Unit 4 | CUS40000 | doTst_LogicIndex_15 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9185 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
228 | doTst_LogicIndex_16 | Test DO - Heat Pump | CUS40000 | doTst_LogicIndex_16 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9186 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
229 | doTst_LogicIndex_17 | Test DO - Heater Step 1 | CUS40000 | doTst_LogicIndex_17 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9187 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
230 | doTst_LogicIndex_18 | Test DO - Heater Step 2 | CUS40000 | doTst_LogicIndex_18 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9188 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
231 | doTst_LogicIndex_19 | Test DO - Heater Step 3 | CUS40000 | doTst_LogicIndex_19 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9189 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
232 | doTst_LogicIndex_20 | Test DO - Pre Heater Step 1 | CUS40000 | doTst_LogicIndex_20 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9190 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
233 | doTst_LogicIndex_21 | Test DO - Pre Heater Step 2 | CUS40000 | doTst_LogicIndex_21 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9191 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
234 | doTst_LogicIndex_22 | Test DO - Pre Heater Step 3 | CUS40000 | doTst_LogicIndex_22 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9192 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
235 | doTst_LogicIndex_23 | Test DO - Post Heater Step 1 | CUS40000 | doTst_LogicIndex_23 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9193 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
236 | doTst_LogicIndex_24 | Test DO - Post Heater Step 2 | CUS40000 | doTst_LogicIndex_24 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9194 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
237 | doTst_LogicIndex_25 | Test DO - Post Heater Step 3 | CUS40000 | doTst_LogicIndex_25 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9195 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
238 | doTst_LogicIndex_26 | Test DO - Humidifier | CUS40000 | doTst_LogicIndex_26 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9196 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
239 | doTst_LogicIndex_27 | Test DO - Rotary Wheel / Exchanger | CUS40000 | doTst_LogicIndex_27 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9197 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
240 | doTst_LogicIndex_28 | Test DO - Supply Fan 2 | CUS40000 | doTst_LogicIndex_28 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9198 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
241 | doTst_LogicIndex_29 | Test DO - Return Fan 2 | CUS40000 | doTst_LogicIndex_29 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9199 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
242 | doTst_LogicIndex_30 | Test DO - Supply Damper 2 | CUS40000 | doTst_LogicIndex_30 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9200 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
243 | doTst_LogicIndex_31 | Test DO - Return Damper 2 | CUS40000 | doTst_LogicIndex_31 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9201 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
244 | doTst_free1 |  | CUS40000 | doTst_free1 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9202 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
245 | doTst_free2 |  | CUS40000 | doTst_free2 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9203 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
246 | doTst_free3 |  | CUS40000 | doTst_free3 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9204 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
247 | doTst_free4 |  | CUS40000 | doTst_free4 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9205 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
248 | doTst_free5 |  | CUS40000 | doTst_free5 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9206 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
249 | doTst_free6 |  | CUS40000 | doTst_free6 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9207 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
250 | doTst_free7 |  | CUS40000 | doTst_free7 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9208 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
251 | doTst_free8 |  | CUS40000 | doTst_free8 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9209 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
252 | doTst_free9 |  | CUS40000 | doTst_free9 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9210 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
253 | doTst_free10 |  | CUS40000 | doTst_free10 |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9211 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
254 | PSWEntry | Password Entry: | CUS40000 | PSWEntry |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9212 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
255 | PSWLevel | Current password level | CUS40000 | PSWLevel |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9213 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
256 | PSWreset | Password Level Reset Request | CUS40000 | PSWreset |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9214 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
257 | sysClock_seconds_WR | Second value to update | CUS40000 | sysClock_seconds_WR |  | 0 | 59 |  |  | FIX(VMU00020) |  |  |  | P | 9215 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
258 | sysClock_minutes_WR | Minute value to update | CUS40000 | sysClock_minutes_WR |  | 0 | 59 |  |  | FIX(VMU00020) |  |  |  | P | 9216 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
259 | sysClock_hours_WR | Hour value to update | CUS40000 | sysClock_hours_WR |  | 0 | 23 |  |  | FIX(VMU00020) |  |  |  | P | 9217 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
260 | sysClock_dayweek_WR | Day of the week value to update | CUS40000 | sysClock_dayweek_WR |  | 0 | 6 |  |  | FIX(VMU00020) |  |  |  | P | 9218 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
261 | sysClock_daymonth_WR | Day of the month value to update | CUS40000 | sysClock_daymonth_WR |  | 1 | 31 |  |  | FIX(VMU00020) |  |  |  | P | 9219 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
262 | sysClock_month_WR | Month value to update | CUS40000 | sysClock_month_WR |  | 1 | 12 |  |  | FIX(VMU00020) |  |  |  | P | 9220 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
263 | sysClock_year_WR | Year value to update | CUS40000 | sysClock_year_WR |  | 10 | 99 |  |  | FIX(VMU00020) |  |  |  | P | 9221 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
264 | sysClock_update | Confirm update | CUS40000 | sysClock_update |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9222 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
265 | sv_sysUsbStatus | Usb status code | CUS40000 | sv_sysUsbStatus |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9223 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
266 | sv_sysUsbCommand | Usb status code | CUS40000 | sv_sysUsbCommand |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9224 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
267 | SaveFactoryStatus | Save Factory Settings Status | CUS40000 | SaveFactoryStatus |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9225 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
268 | SaveFactoryCommand | Save Factory Settings Request | CUS40000 | SaveFactoryCommand |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9226 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
269 | RestoreFactoryStatus | Restore Factory Settings Status | CUS40000 | RestoreFactoryStatus |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9227 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
270 | RestoreFactoryCommand | Restore Factory Settings Request | CUS40000 | RestoreFactoryCommand |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9228 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
271 | Unit_ApplicationCode | Unit Application Code | CUS40000 | Unit_ApplicationCode |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9298 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
272 | Unit_Version | Unit Application Version | CUS40000 | Unit_Version |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00020) |  |  |  | P | 9299 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
273 | Unit_BMS_OnOff | Unit On/Off via Modbus | CUS40000 | Unit_BMS_OnOff |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9300 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
274 | Unit_Status | Unit Status | CUS40000 | Unit_Status |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9301 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
275 | Unit_Mode_Status | Unit Mode | CUS40000 | Unit_Mode_Status |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9302 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
276 | Unit_EcoCmfNight_Status | Unit Mode | CUS40000 | Unit_EcoCmfNight_Status |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9303 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
277 | Unit_Alarm | Unit Alarm | CUS40000 | Unit_Alarm |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9304 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
278 | T_RegulationProbe | Temperature Regulation Probe | CUS40000 | T_RegulationProbe |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9305 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
279 | T_CurrentSetpointByPar | Current Setpoint by parameter based on selected mode | CUS40000 | T_CurrentSetpointByPar |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9306 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
280 | T_CurrentSupplySetpoint | Current Supply Setpoint | CUS40000 | T_CurrentSupplySetpoint |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9307 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
281 | T_CurrentReturnSetpoint | Current Return Setpoint | CUS40000 | T_CurrentReturnSetpoint |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9308 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
282 | T_DewPointSetPoint | Current Dewpoint Setpoint | CUS40000 | T_DewPointSetPoint |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9309 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
283 | RH_CurrentSetpoint | Current Return Setpoint | CUS40000 | RH_CurrentSetpoint |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9310 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
284 | AirQ_CurrentSetpointVOC | Current Setpoint VOC | CUS40000 | AirQ_CurrentSetpointVOC |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 9311 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
285 | AirQ_CurrentSetpointCO2 | Current Setpoint CO2 | CUS40000 | AirQ_CurrentSetpointCO2 |  | -32768 | 32767 |  | TRUE | FIX(VMU00060) |  |  |  | P | 9312 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
286 | Pr_CurrentSupplySetpoint | Current Fan Supply Setpoint - Units depends on Fan_Supply_Pressure_Flow | CUS40000 | Pr_CurrentSupplySetpoint |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9313 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
287 | Pr_CurrentReturnSetpoint | Current Fan Return Setpoint - Units depends on Fan_Return_Pressure_Flow | CUS40000 | Pr_CurrentReturnSetpoint |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9315 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
288 | RH_RegulationProbe | Humdity Regulation Probe | CUS40000 | RH_RegulationProbe |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9317 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
289 | AirQ_RegulationProbe | Air Quality Regulation Probe | CUS40000 | AirQ_RegulationProbe |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9318 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
290 | Pr_Flow_Supply | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow | CUS40000 | Pr_Flow_Supply |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9319 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
291 | Pr_Flow_Return | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow | CUS40000 | Pr_Flow_Return |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9321 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
292 | OnOffRequestFromWeb | Unit On/Off via request via Web/Modbus | CUS40000 | OnOffRequestFromWeb |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 9349 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
293 | ChangeSeasonRequestFromWeb | Unit Season Change request via Web/Modbus | CUS40000 | ChangeSeasonRequestFromWeb |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 9350 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
294 | ComfortEcoNightRequestFromWeb | Unit Comfort/Eco/Night request via Web/Modbus | CUS40000 | ComfortEcoNightRequestFromWeb |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 9351 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
295 | History000 | Most recent value | CUS40000 | History000 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9479 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
296 | History001 | Most recent value | CUS40000 | History001 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9480 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
297 | History002 | Most recent value | CUS40000 | History002 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9481 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
298 | History003 | Most recent value | CUS40000 | History003 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9482 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
299 | HistoricalPosition | Historical Postion Required | CUS40000 | HistoricalPosition |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9483 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
300 | Historical_Value_Code | Historical: Alarm Code | CUS40000 | Historical_Value_Code |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9484 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
301 | Historical_Value_Date | Historical: Alarm Date | CUS40000 | Historical_Value_Date |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00020) |  |  |  | P | 9485 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
302 | Historical_Value_Time | Historical: Alarm Time | CUS40000 | Historical_Value_Time |  | -32768 | 32767 | HH:MM | TRUE | FIX(VMU00020) |  |  |  | P | 9486 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
303 | Historical_Value_SecStatus | Historical: Alarm Seconds and Status: 100x+seconds (x=0 restored, x=1 active, x=2 wait for reset) | CUS40000 | Historical_Value_SecStatus |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00020) |  |  |  | P | 9487 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
304 | Historical_Number_alarms | Historical: Number of stored alarms | CUS40000 | Historical_Number_alarms |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9488 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
305 | Historical_Reset | Historical: Reset Request | CUS40000 | Historical_Reset |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 9489 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
306 | Historical_Value_Sec | Historical: Alarm Time Seconds | CUS40000 | Historical_Value_Sec |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9490 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
307 | Historical_Value_Status | Historical: Alarm Status | CUS40000 | Historical_Value_Status |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9491 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
308 | HMI_PackAlarm1 |  | CUS40000 | HMI_PackAlarm1 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9499 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
309 | HMI_PackAlarm2 |  | CUS40000 | HMI_PackAlarm2 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9501 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
310 | HMI_PackAlarm3 |  | CUS40000 | HMI_PackAlarm3 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9503 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
311 | HMI_PackAlarm4 |  | CUS40000 | HMI_PackAlarm4 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9505 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
312 | HMI_PackAlarm5 |  | CUS40000 | HMI_PackAlarm5 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9507 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
313 | HMI_PackAlarm6 |  | CUS40000 | HMI_PackAlarm6 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9509 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
314 | HMI_PackAlarm7 |  | CUS40000 | HMI_PackAlarm7 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9511 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
315 | HMI_PackAlarm8 |  | CUS40000 | HMI_PackAlarm8 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9513 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
316 | HMI_PackAlarm9 |  | CUS40000 | HMI_PackAlarm9 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9515 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
317 | HMI_PackAlarm10 |  | CUS40000 | HMI_PackAlarm10 |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 9517 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
318 | Alxx_Reset | Alarm reset request command via Modbus | CUS40000 | Alxx_Reset |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9519 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
319 | Al01_SupplyProbe | Al01-Supply Temperature Probe Error | CUS40000 | Al01_SupplyProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9520 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
320 | Al02_ReturnProbe | A02-Return Temperature Probe Error | CUS40000 | Al02_ReturnProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9521 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
321 | Al03_ExternalProbe | A03-External Temperature Probe Error | CUS40000 | Al03_ExternalProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9522 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
322 | Al04_ExpulsionProbe | A04-Expulsion Temperature Probe Error | CUS40000 | Al04_ExpulsionProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9523 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
323 | Al05_PreHeatingProbe | A05-Preheating Temperature Probe Error | CUS40000 | Al05_PreHeatingProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9524 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
324 | Al06_SaturationProbe | A06-Saturation Temperature Probe Error | CUS40000 | Al06_SaturationProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9525 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
325 | Al07_AntifreezeProbe | A07-Antifreeze Temperature Probe Error | CUS40000 | Al07_AntifreezeProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9526 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
326 | Al08_AirQualityProbe_CO2 | A08-CO2 Probe Error | CUS40000 | Al08_AirQualityProbe_CO2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9527 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
327 | Al09_SupplyPressureProbe | A09-Supply Pressure Probe Error | CUS40000 | Al09_SupplyPressureProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9528 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
328 | Al10_ReturnPressureProbe | A10-Return Pressure Probe Error | CUS40000 | Al10_ReturnPressureProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9529 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
329 | Al11_SupplyHumidityProbe | A11-Hum. Supply Probe Error | CUS40000 | Al11_SupplyHumidityProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9530 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
330 | Al12_ReturnHumidityProbe | A12-Hum. Return Probe Error | CUS40000 | Al12_ReturnHumidityProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9531 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
331 | Al13_AirQualityProbe_VOC | A13-VOC Probe Error | CUS40000 | Al13_AirQualityProbe_VOC |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9532 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
332 | Al14_ExternalHumidityProbe | A14-Hum. External Probe Error | CUS40000 | Al14_ExternalHumidityProbe |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9533 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
333 | Al15_ |  | CUS40000 | Al15_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9534 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
334 | Al16_ |  | CUS40000 | Al16_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9535 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
335 | Al17_ |  | CUS40000 | Al17_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9536 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
336 | Al18_ |  | CUS40000 | Al18_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9537 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
337 | Al19_ |  | CUS40000 | Al19_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9538 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
338 | Al20_ |  | CUS40000 | Al20_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9539 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
339 | Al21_ |  | CUS40000 | Al21_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9540 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
340 | Al22_ |  | CUS40000 | Al22_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9541 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
341 | Al23_ |  | CUS40000 | Al23_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9542 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
342 | Al24_ |  | CUS40000 | Al24_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9543 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
343 | Al25_ |  | CUS40000 | Al25_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9544 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
344 | Al26_SensAirFlowSupply | A26-Supply Airflow by Probe | CUS40000 | Al26_SensAirFlowSupply |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9545 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
345 | Al27_SensAirFlowReturn | A27-Return Airflow by Probe | CUS40000 | Al27_SensAirFlowReturn |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9546 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
346 | Al28_SensAirFlowSupplyBck | A28-Airflow Prb Sup.2 | CUS40000 | Al28_SensAirFlowSupplyBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9547 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
347 | Al29_SensAirFlowReturnBck | A29-Airflow Prb Ret.2 | CUS40000 | Al29_SensAirFlowReturnBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9548 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
348 | Al30_FanThermalSupply | A30-Fan Supply | CUS40000 | Al30_FanThermalSupply |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9549 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
349 | Al31_FanThermalReturn | A31-Fan Return | CUS40000 | Al31_FanThermalReturn |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9550 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
350 | Al32_Fire | A32-Fire | CUS40000 | Al32_Fire |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9551 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
351 | Al33_Door | A33-Door | CUS40000 | Al33_Door |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9552 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
352 | Al34_Antifreeze | A34-Antifreeze | CUS40000 | Al34_Antifreeze |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9553 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
353 | Al35_AirFlowSupply | A35-Airflow Supply | CUS40000 | Al35_AirFlowSupply |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9554 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
354 | Al36_AirFlowReturn | A36-Airflow Return | CUS40000 | Al36_AirFlowReturn |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9555 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
355 | Al37_Humidifier | A37-Humidifier | CUS40000 | Al37_Humidifier |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9556 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
356 | Al38_PreHeater | A38-Preheater | CUS40000 | Al38_PreHeater |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9557 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
357 | Al39_Heater | A39-Heater | CUS40000 | Al39_Heater |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9558 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
358 | Al40_PostHeater | A40-Postheater | CUS40000 | Al40_PostHeater |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9559 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
359 | Al41_RotaryWheel | A41-Recovery | CUS40000 | Al41_RotaryWheel |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9560 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
360 | Al42_Filter1 | A42-Filter 1 | CUS40000 | Al42_Filter1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9561 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
361 | Al43_Filter2 | A43-Filter 2 | CUS40000 | Al43_Filter2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9562 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
362 | Al44_Filter3 | A44-Filter 3 | CUS40000 | Al44_Filter3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9563 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
363 | Al45_Filter4 | A45-Filter 4 | CUS40000 | Al45_Filter4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9564 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
364 | Al46_FanThermalSupplyBck | A46-Fan Supply 2 | CUS40000 | Al46_FanThermalSupplyBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9565 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
365 | Al47_FanThermalReturnBck | A47-Fan Return 2 | CUS40000 | Al47_FanThermalReturnBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9566 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
366 | Al48_AirFlowSupplyBck | A48-Airflow Supply 2 | CUS40000 | Al48_AirFlowSupplyBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9567 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
367 | Al49_AirFlowReturnBck | A49-Airflow Return 2 | CUS40000 | Al49_AirFlowReturnBck |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9568 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
368 | Al50_CondUnit | A50-Cond. Unit | CUS40000 | Al50_CondUnit |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9569 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
369 | Al51_RTC | A51-Real Time Clock | CUS40000 | Al51_RTC |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9570 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
370 | Al52_FanMaintenance | A52-Fan Maintenance | CUS40000 | Al52_FanMaintenance |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9571 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
371 | Al53_ModbusFanCfg | A53-Modbus Fan Config. Timeout | CUS40000 | Al53_ModbusFanCfg |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9572 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
372 | Al54_FanSupplyCom | A54-Modbus Fan Supply Communication | CUS40000 | Al54_FanSupplyCom |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9573 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
373 | Al55_FanReturnCom | A55-Modbus Fan Return Communication | CUS40000 | Al55_FanReturnCom |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9574 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
374 | Al56_FanSupplyBckCom | A56-Modbus Fan Supply 2 Communication | CUS40000 | Al56_FanSupplyBckCom |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9575 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
375 | Al57_FanReturnBckCom | A57-Modbus Fan Return 2 Communication | CUS40000 | Al57_FanReturnBckCom |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9576 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
376 | Al58_Filter5 | A58-Filter 5 | CUS40000 | Al58_Filter5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9577 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
377 | Al59_ |  | CUS40000 | Al59_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9578 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
378 | Al60_LogError | A60-Log Error | CUS40000 | Al60_LogError |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9579 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
379 | Al61_Exp1 | A61-Can Expansion 1 | CUS40000 | Al61_Exp1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9580 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
380 | Al62_Exp2 | A62-Can Expansion 2 | CUS40000 | Al62_Exp2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9581 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
381 | Al63_Exp3 | A63-Can Expansion 3 | CUS40000 | Al63_Exp3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9582 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
382 | Al64_Exp4 | A64-Can Expansion 4 | CUS40000 | Al64_Exp4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9583 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
383 | Al65_Exp5 | A65-Can Expansion 5 | CUS40000 | Al65_Exp5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9584 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
384 | Al66_CondUnit2 | A66-Cond. Unit 2 | CUS40000 | Al66_CondUnit2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9585 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
385 | Al67_CondUnit3 | A67-Cond. Unit 3 | CUS40000 | Al67_CondUnit3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9586 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
386 | Al68_CondUnit4 | A68-Cond. Unit 4 | CUS40000 | Al68_CondUnit4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9587 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
387 | Al69_ |  | CUS40000 | Al69_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9588 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
388 | Al70_ |  | CUS40000 | Al70_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9589 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
389 | Al71_ |  | CUS40000 | Al71_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9590 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
390 | Al72_ |  | CUS40000 | Al72_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9591 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
391 | Al73_ |  | CUS40000 | Al73_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9592 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
392 | Al74_ |  | CUS40000 | Al74_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9593 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
393 | Al75_ |  | CUS40000 | Al75_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9594 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
394 | Al76_ |  | CUS40000 | Al76_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9595 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
395 | Al77_ |  | CUS40000 | Al77_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9596 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
396 | Al78_ |  | CUS40000 | Al78_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9597 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
397 | Al79_ |  | CUS40000 | Al79_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9598 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
398 | Al80_ |  | CUS40000 | Al80_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9599 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
399 | Al81_ |  | CUS40000 | Al81_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9600 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
400 | Al82_ |  | CUS40000 | Al82_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9601 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
401 | Al83_ |  | CUS40000 | Al83_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9602 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
402 | Al84_ |  | CUS40000 | Al84_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9603 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
403 | Al85_ |  | CUS40000 | Al85_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9604 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
404 | Al86_ |  | CUS40000 | Al86_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9605 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
405 | Al87_ |  | CUS40000 | Al87_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9606 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
406 | Al88_ |  | CUS40000 | Al88_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9607 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
407 | Al89_ |  | CUS40000 | Al89_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9608 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
408 | Al90_ |  | CUS40000 | Al90_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9609 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
409 | Al91_ |  | CUS40000 | Al91_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9610 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
410 | Al92_ |  | CUS40000 | Al92_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9611 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
411 | Al93_ |  | CUS40000 | Al93_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9612 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
412 | Al94_ |  | CUS40000 | Al94_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9613 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
413 | Al95_ |  | CUS40000 | Al95_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9614 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
414 | Al96_ |  | CUS40000 | Al96_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9615 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
415 | Al97_ |  | CUS40000 | Al97_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9616 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
416 | Al98_ |  | CUS40000 | Al98_ |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9617 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
417 | Al99_FanSupply_1b_Com | Al99-Fan Supply 1b Com Alarm | CUS40000 | Al99_FanSupply_1b_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9618 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
418 | Al100_FanSupply_1c_Com | Al100-Fan Supply 1c Com Alarm | CUS40000 | Al100_FanSupply_1c_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9619 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
419 | Al101_FanReturn_1b_Com | Al101-Fan Return 1b Com Alarm | CUS40000 | Al101_FanReturn_1b_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9620 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
420 | Al102_FanReturn_1c_Com | Al102-Fan Return 1c Com Alarm | CUS40000 | Al102_FanReturn_1c_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9621 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
421 | Al103_FanSupply_2b_Com | Al103-Fan Supply 2b Com Alarm | CUS40000 | Al103_FanSupply_2b_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9622 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
422 | Al104_FanSupply_2c_Com | Al104-Fan Supply 2c Com Alarm | CUS40000 | Al104_FanSupply_2c_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9623 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
423 | Al105_FanReturn_2b_Com | Al105-Fan Return 2b Com Alarm | CUS40000 | Al105_FanReturn_2b_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9624 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
424 | Al106_FanReturn_2c_Com | Al106-Fan Return 2c Com Alarm | CUS40000 | Al106_FanReturn_2c_Com |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9625 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
425 | AI_Exp1_1 | Physical Input 1 Exp1 | CUS40000 | AI_Exp1_1 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9669 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
426 | AI_Exp1_2 | Physical Input 2 Exp1 | CUS40000 | AI_Exp1_2 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9670 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
427 | AI_Exp1_3 | Physical Input 3 Exp1 | CUS40000 | AI_Exp1_3 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9671 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
428 | AI_Exp1_4 | Physical Input 4 Exp1 | CUS40000 | AI_Exp1_4 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9672 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
429 | AI_Exp2_1 | Physical Input 1 Exp2 | CUS40000 | AI_Exp2_1 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9673 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
430 | AI_Exp2_2 | Physical Input 2 Exp2 | CUS40000 | AI_Exp2_2 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9674 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
431 | AI_Exp2_3 | Physical Input 3 Exp2 | CUS40000 | AI_Exp2_3 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9675 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
432 | AI_Exp2_4 | Physical Input 4 Exp2 | CUS40000 | AI_Exp2_4 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9676 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
433 | HMI_word1 | Word with info for HMI | CUS40000 | HMI_word1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 12999 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
434 | HMI_word2 | Word with info for HMI | CUS40000 | HMI_word2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13000 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
435 | HMI_word3 | Word with info for HMI | CUS40000 | HMI_word3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13001 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
436 | HMI_word4 | Word with info for HMI | CUS40000 | HMI_word4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13002 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
437 | HMI_word5 | Word with info for HMI | CUS40000 | HMI_word5 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13003 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
438 | HMI_word6 | Word with info for HMI | CUS40000 | HMI_word6 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13004 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
439 | HMI_word7 | Word with info from HMI | CUS40000 | HMI_word7 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13005 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
440 | HMI_word8 | Word with info from HMI | CUS40000 | HMI_word8 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13006 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
441 | HMI_word9 | Word with info from HMI | CUS40000 | HMI_word9 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13007 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
442 | HMI_word10 | Word with info from HMI | CUS40000 | HMI_word10 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 13008 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
443 | HMI_PackVis1 | Used to display I/O allocated status | CUS40000 | HMI_PackVis1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9699 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
444 | HMI_PackVis2 |  | CUS40000 | HMI_PackVis2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9700 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
445 | HMI_PackVis3 |  | CUS40000 | HMI_PackVis3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9701 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
446 | HMI_PackVis4 |  | CUS40000 | HMI_PackVis4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9702 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
447 | HMI_PackVis6 |  | CUS40000 | HMI_PackVis6 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9704 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
448 | HMI_PackVis5 |  | CUS40000 | HMI_PackVis5 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9703 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
449 | HMI_PackVis7 |  | CUS40000 | HMI_PackVis7 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9705 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
450 | HMI_PackVis8 |  | CUS40000 | HMI_PackVis8 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9706 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
451 | HMI_PackVis9 |  | CUS40000 | HMI_PackVis9 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9707 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
452 | HMI_PackVis10 |  | CUS40000 | HMI_PackVis10 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9708 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
453 | HMI_PackVis11 | Used to display I/O allocated status | CUS40000 | HMI_PackVis11 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9709 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
454 | HMI_PackVis12 |  | CUS40000 | HMI_PackVis12 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9710 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
455 | HMI_PackVis13 |  | CUS40000 | HMI_PackVis13 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9711 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
456 | HMI_PackVis14 |  | CUS40000 | HMI_PackVis14 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9712 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
457 | HMI_PackVis15 |  | CUS40000 | HMI_PackVis15 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9713 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
458 | HMI_PackVis16 |  | CUS40000 | HMI_PackVis16 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9714 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
459 | HMI_PackVis17 |  | CUS40000 | HMI_PackVis17 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9715 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
460 | HMI_PackVis18 |  | CUS40000 | HMI_PackVis18 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9716 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
461 | HMI_PackVis19 |  | CUS40000 | HMI_PackVis19 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9717 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
462 | HMI_PackVis20 |  | CUS40000 | HMI_PackVis20 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9718 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
463 | AI_LogicIndex_0 | Supply Temperature | CUS40000 | AI_LogicIndex_0 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9719 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
464 | AI_LogicIndex_1 | Return Temperature | CUS40000 | AI_LogicIndex_1 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9720 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
465 | AI_LogicIndex_2 | External Temperature | CUS40000 | AI_LogicIndex_2 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9721 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
466 | AI_LogicIndex_3 | Expulsion Temperature | CUS40000 | AI_LogicIndex_3 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9722 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
467 | AI_LogicIndex_4 | Preheating Temp, | CUS40000 | AI_LogicIndex_4 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9723 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
468 | AI_LogicIndex_5 | Saturation Temperature | CUS40000 | AI_LogicIndex_5 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9724 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
469 | AI_LogicIndex_6 | Antifreeze Temperature | CUS40000 | AI_LogicIndex_6 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 9725 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
470 | AI_LogicIndex_7 | Air Quality - CO2 | CUS40000 | AI_LogicIndex_7 |  | -32768 | 32767 |  | TRUE | FIX(VMU00060) |  |  |  | P | 9726 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
471 | AI_LogicIndex_8 | Air Quality - VOC | CUS40000 | AI_LogicIndex_8 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9727 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
472 | AI_LogicIndex_9 | Supply Pressure | CUS40000 | AI_LogicIndex_9 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9728 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
473 | AI_LogicIndex_10 | Return Pressure | CUS40000 | AI_LogicIndex_10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9729 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
474 | AI_LogicIndex_11 | Supply Humidity | CUS40000 | AI_LogicIndex_11 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9730 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
475 | AI_LogicIndex_12 | Return Humidity | CUS40000 | AI_LogicIndex_12 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9731 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
476 | AI_LogicIndex_13 | External Humidity | CUS40000 | AI_LogicIndex_13 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9732 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
477 | AI_LogicIndex_14 | Supply Flow Testing | CUS40000 | AI_LogicIndex_14 |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9733 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
478 | AI_LogicIndex_15 | Return Flow Testing | CUS40000 | AI_LogicIndex_15 |  | -2147483648 | 2147483647 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9735 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
479 | AI_free4 |  | CUS40000 | AI_free4 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9737 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
480 | AI_free5 |  | CUS40000 | AI_free5 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9738 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
481 | AI_free6 |  | CUS40000 | AI_free6 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9739 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
482 | AI_free7 |  | CUS40000 | AI_free7 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9740 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
483 | AI_free8 |  | CUS40000 | AI_free8 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9741 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
484 | AI_free9 |  | CUS40000 | AI_free9 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9742 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
485 | AI_free10 |  | CUS40000 | AI_free10 |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 9743 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
486 | DI_Voltage_LogicIndex_0 | Supply Fan Thermal - Physical Status | CUS40000 | DI_Voltage_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9744 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
487 | DI_Voltage_LogicIndex_1 | Return Fan Thermal - Physical Status | CUS40000 | DI_Voltage_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9745 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
488 | DI_Voltage_LogicIndex_2 | On/Off Input - Physical Status | CUS40000 | DI_Voltage_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9746 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
489 | DI_Voltage_LogicIndex_3 | Fire Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9747 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
490 | DI_Voltage_LogicIndex_4 | Mode Input - Physical Status | CUS40000 | DI_Voltage_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9748 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
491 | DI_Voltage_LogicIndex_5 | Door - Physical Status | CUS40000 | DI_Voltage_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9749 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
492 | DI_Voltage_LogicIndex_6 | Antifreeze - Physical Status | CUS40000 | DI_Voltage_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9750 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
493 | DI_Voltage_LogicIndex_7 | Supply Airflow - Physical Status | CUS40000 | DI_Voltage_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9751 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
494 | DI_Voltage_LogicIndex_8 | Return Airflow - Physical Status | CUS40000 | DI_Voltage_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9752 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
495 | DI_Voltage_LogicIndex_9 | Humidifier Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9753 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
496 | DI_Voltage_LogicIndex_10 | Preheater Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9754 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
497 | DI_Voltage_LogicIndex_11 | Postheater Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9755 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
498 | DI_Voltage_LogicIndex_12 | Rotary Wheel Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9756 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
499 | DI_Voltage_LogicIndex_13 | Filter 1 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9757 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
500 | DI_Voltage_LogicIndex_14 | Filter 2 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_14 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9758 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
501 | DI_Voltage_LogicIndex_15 | Filter 3 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_15 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9759 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
502 | DI_Voltage_LogicIndex_16 | Filter 4 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_16 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9760 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
503 | DI_Voltage_LogicIndex_17 | Supply Fan 2 Th. - Physical Status | CUS40000 | DI_Voltage_LogicIndex_17 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9761 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
504 | DI_Voltage_LogicIndex_18 | Return Fan 2 Th. - Physical Status | CUS40000 | DI_Voltage_LogicIndex_18 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9762 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
505 | DI_Voltage_LogicIndex_19 | Supply Fan 2 Airflow - Physical Status | CUS40000 | DI_Voltage_LogicIndex_19 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9763 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
506 | DI_Voltage_LogicIndex_20 | Return Fan 2 Airflow - Physical Status | CUS40000 | DI_Voltage_LogicIndex_20 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9764 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
507 | DI_Voltage_LogicIndex_21 | Cond. Unit Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_21 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9765 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
508 | DI_Voltage_LogicIndex_22 | El. Heater Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_22 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9766 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
509 | DI_Voltage_LogicIndex_23 | Cond. Unit 2 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_23 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9767 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
510 | DI_Voltage_LogicIndex_24 | Cond. Unit 3 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_24 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9768 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
511 | DI_Voltage_LogicIndex_25 | Cond. Unit 4 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_25 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9769 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
512 | DI_Voltage_LogicIndex_26 | Cond. Unit 1 Defrost - Physical Status | CUS40000 | DI_Voltage_LogicIndex_26 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9770 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
513 | DI_Voltage_LogicIndex_27 | Cond. Unit 2 Defrost - Physical Status | CUS40000 | DI_Voltage_LogicIndex_27 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9771 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
514 | DI_Voltage_LogicIndex_28 | Cond. Unit 3 Defrost - Physical Status | CUS40000 | DI_Voltage_LogicIndex_28 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9772 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
515 | DI_Voltage_LogicIndex_29 | Cond. Unit 4 Defrost - Physical Status | CUS40000 | DI_Voltage_LogicIndex_29 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9773 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
516 | DI_Voltage_LogicIndex_30 | Filter 5 Alarm - Physical Status | CUS40000 | DI_Voltage_LogicIndex_30 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9774 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
517 | DI_free9 |  | CUS40000 | DI_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9775 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
518 | DI_free10 |  | CUS40000 | DI_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9776 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
519 | DO_LogicIndex_0 | Supply Fan - Logic Status | CUS40000 | DO_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9777 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
520 | DO_LogicIndex_1 | Return Fan - Logic Status | CUS40000 | DO_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9778 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
521 | DO_LogicIndex_2 | On Off - Logic Status | CUS40000 | DO_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9779 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
522 | DO_LogicIndex_3 | Alarm - Logic Status | CUS40000 | DO_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9780 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
523 | DO_LogicIndex_4 | Mode - Logic Status | CUS40000 | DO_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9781 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
524 | DO_LogicIndex_5 | Ext. Dampers - Logic Status | CUS40000 | DO_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9782 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
525 | DO_LogicIndex_6 | Bypass Damper - Logic Status | CUS40000 | DO_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9783 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
526 | DO_LogicIndex_7 | Supply Damper - Logic Status | CUS40000 | DO_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9784 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
527 | DO_LogicIndex_8 | Return Damper - Logic Status | CUS40000 | DO_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9785 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
528 | DO_LogicIndex_9 | Pump Preheat - Logic Status | CUS40000 | DO_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9786 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
529 | DO_LogicIndex_10 | Pump Postheat - Logic Status | CUS40000 | DO_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9787 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
530 | DO_LogicIndex_11 | Cool/CH Pump - Logic Status | CUS40000 | DO_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9788 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
531 | DO_LogicIndex_12 | C/CH Step - Condensing Unit 1 - Logic Status | CUS40000 | DO_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9789 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
532 | DO_LogicIndex_13 | C/CH Step - Condensing Unit 2 - Logic Status | CUS40000 | DO_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9790 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
533 | DO_LogicIndex_14 | Cl/CH Step - Condensing Unit 3 - Logic Status | CUS40000 | DO_LogicIndex_14 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9791 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
534 | DO_LogicIndex_15 | C/CH Step - Condensing Unit 4 - Logic Status | CUS40000 | DO_LogicIndex_15 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9792 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
535 | DO_LogicIndex_16 | Heat Pump - Logic Status | CUS40000 | DO_LogicIndex_16 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9793 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
536 | DO_LogicIndex_17 | Heater Step 1 - Logic Status | CUS40000 | DO_LogicIndex_17 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9794 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
537 | DO_LogicIndex_18 | Heater Step 2 - Logic Status | CUS40000 | DO_LogicIndex_18 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9795 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
538 | DO_LogicIndex_19 | Heater Step 3 - Logic Status | CUS40000 | DO_LogicIndex_19 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9796 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
539 | DO_LogicIndex_20 | Pre Heater Step 1 - Logic Status | CUS40000 | DO_LogicIndex_20 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9797 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
540 | DO_LogicIndex_21 | Pre Heater Step 2 - Logic Status | CUS40000 | DO_LogicIndex_21 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9798 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
541 | DO_LogicIndex_22 | Pre Heater Step 3 - Logic Status | CUS40000 | DO_LogicIndex_22 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9799 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
542 | DO_LogicIndex_23 | Post Heater Step 1 - Logic Status | CUS40000 | DO_LogicIndex_23 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9800 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
543 | DO_LogicIndex_24 | Post Heater Step 2 - Logic Status | CUS40000 | DO_LogicIndex_24 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9801 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
544 | DO_LogicIndex_25 | Post Heater Step 3 - Logic Status | CUS40000 | DO_LogicIndex_25 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9802 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
545 | DO_LogicIndex_26 | Humidifier - Logic Status | CUS40000 | DO_LogicIndex_26 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9803 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
546 | DO_LogicIndex_27 | Rotary Wheel / Exchanger - Logic Status | CUS40000 | DO_LogicIndex_27 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9804 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
547 | DO_LogicIndex_28 | Supply Fan 2 - Logic Status | CUS40000 | DO_LogicIndex_28 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9805 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
548 | DO_LogicIndex_29 | Return Fan 2 - Logic Status | CUS40000 | DO_LogicIndex_29 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9806 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
549 | DO_LogicIndex_30 | Supply Damper 2 - Logic Status | CUS40000 | DO_LogicIndex_30 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9807 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
550 | DO_LogicIndex_31 | Return Damper 2 - Logic Status | CUS40000 | DO_LogicIndex_31 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9808 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
551 | DO_free1 | - Logic Status | CUS40000 | DO_free1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9809 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
552 | DO_free2 | - Logic Status | CUS40000 | DO_free2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9810 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
553 | DO_free3 | - Logic Status | CUS40000 | DO_free3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9811 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
554 | DO_free4 | - Logic Status | CUS40000 | DO_free4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9812 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
555 | DO_free5 | - Logic Status | CUS40000 | DO_free5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9813 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
556 | DO_free6 | - Logic Status | CUS40000 | DO_free6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9814 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
557 | DO_free7 | - Logic Status | CUS40000 | DO_free7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9815 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
558 | DO_free8 | - Logic Status | CUS40000 | DO_free8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9816 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
559 | DO_free9 | - Logic Status | CUS40000 | DO_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9817 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
560 | DO_free10 | - Logic Status | CUS40000 | DO_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9818 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
561 | AO_LogicIndex_0 | Supply Fan | CUS40000 | AO_LogicIndex_0 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9819 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
562 | AO_LogicIndex_1 | Return Fan | CUS40000 | AO_LogicIndex_1 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9820 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
563 | AO_LogicIndex_2 | Ext. Dampers | CUS40000 | AO_LogicIndex_2 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9821 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
564 | AO_LogicIndex_3 | Bypass Damper | CUS40000 | AO_LogicIndex_3 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9822 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
565 | AO_LogicIndex_4 | Modulating Cool - C/H | CUS40000 | AO_LogicIndex_4 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9823 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
566 | AO_LogicIndex_5 | Modulating Heat | CUS40000 | AO_LogicIndex_5 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9824 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
567 | AO_LogicIndex_6 | Pre Heater | CUS40000 | AO_LogicIndex_6 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9825 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
568 | AO_LogicIndex_7 | Post Heater | CUS40000 | AO_LogicIndex_7 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9826 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
569 | AO_LogicIndex_8 | Rotary Wheel / Exchanger | CUS40000 | AO_LogicIndex_8 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9827 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
570 | AO_LogicIndex_9 | Humidifier | CUS40000 | AO_LogicIndex_9 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9828 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
571 | AO_LogicIndex_10 | Condensing Unit 1 | CUS40000 | AO_LogicIndex_10 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9829 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
572 | AO_LogicIndex_11 | Condensing Unit 2 | CUS40000 | AO_LogicIndex_11 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9830 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
573 | AO_LogicIndex_12 | Condensing Unit 3 | CUS40000 | AO_LogicIndex_12 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9831 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
574 | AO_LogicIndex_13 | Condensing Unit 4 | CUS40000 | AO_LogicIndex_13 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9832 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
575 | AO_free5 |  | CUS40000 | AO_free5 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9833 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
576 | AO_free6 |  | CUS40000 | AO_free6 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9834 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
577 | AO_free7 |  | CUS40000 | AO_free7 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9835 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
578 | AO_free8 |  | CUS40000 | AO_free8 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9836 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
579 | AO_free9 |  | CUS40000 | AO_free9 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9837 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
580 | AO_free10 |  | CUS40000 | AO_free10 |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 9838 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
581 | AI_Map_LogicIndex_0 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9839 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
582 | AI_Map_LogicIndex_1 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9840 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
583 | AI_Map_LogicIndex_2 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9841 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
584 | AI_Map_LogicIndex_3 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9842 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
585 | AI_Map_LogicIndex_4 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9843 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
586 | AI_Map_LogicIndex_5 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9844 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
587 | AI_Map_LogicIndex_6 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9845 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
588 | AI_Map_LogicIndex_7 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9846 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
589 | AI_Map_LogicIndex_8 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9847 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
590 | AI_Map_LogicIndex_9 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9848 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
591 | AI_Map_LogicIndex_10 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9849 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
592 | AI_Map_LogicIndex_11 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9850 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
593 | AI_Map_LogicIndex_12 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9851 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
594 | AI_Map_LogicIndex_13 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9852 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
595 | AI_Map_LogicIndex_14 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_14 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9853 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
596 | AI_Map_LogicIndex_15 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_15 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9854 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
597 | AI_Map_LogicIndex_free4 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9855 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
598 | AI_Map_LogicIndex_free5 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9856 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
599 | AI_Map_LogicIndex_free6 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9857 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
600 | AI_Map_LogicIndex_free7 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9858 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
601 | AI_Map_LogicIndex_free8 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9859 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
602 | AI_Map_LogicIndex_free9 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9860 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
603 | AI_Map_LogicIndex_free10 | Physical mapping of logic index i | CUS40000 | AI_Map_LogicIndex_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9861 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
604 | DI_Map_LogicIndex_0 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9862 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
605 | DI_Map_LogicIndex_1 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9863 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
606 | DI_Map_LogicIndex_2 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9864 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
607 | DI_Map_LogicIndex_3 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9865 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
608 | DI_Map_LogicIndex_4 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9866 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
609 | DI_Map_LogicIndex_5 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9867 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
610 | DI_Map_LogicIndex_6 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9868 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
611 | DI_Map_LogicIndex_7 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9869 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
612 | DI_Map_LogicIndex_8 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9870 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
613 | DI_Map_LogicIndex_9 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9871 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
614 | DI_Map_LogicIndex_10 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9872 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
615 | DI_Map_LogicIndex_11 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9873 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
616 | DI_Map_LogicIndex_12 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9874 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
617 | DI_Map_LogicIndex_13 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9875 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
618 | DI_Map_LogicIndex_14 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_14 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9876 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
619 | DI_Map_LogicIndex_15 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_15 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9877 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
620 | DI_Map_LogicIndex_16 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_16 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9878 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
621 | DI_Map_LogicIndex_17 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_17 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9879 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
622 | DI_Map_LogicIndex_18 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_18 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9880 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
623 | DI_Map_LogicIndex_19 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_19 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9881 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
624 | DI_Map_LogicIndex_20 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_20 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9882 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
625 | DI_Map_LogicIndex_21 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_21 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9883 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
626 | DI_Map_LogicIndex_22 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_22 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9884 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
627 | DI_Map_LogicIndex_23 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_23 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9885 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
628 | DI_Map_LogicIndex_24 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_24 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9886 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
629 | DI_Map_LogicIndex_25 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_25 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9887 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
630 | DI_Map_LogicIndex_26 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_26 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9888 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
631 | DI_Map_LogicIndex_27 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_27 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9889 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
632 | DI_Map_LogicIndex_28 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_28 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9890 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
633 | DI_Map_LogicIndex_29 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_29 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9891 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
634 | DI_Map_LogicIndex_30 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_30 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9892 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
635 | DI_Map_LogicIndex_free9 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9893 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
636 | DI_Map_LogicIndex_free10 | Physical mapping of logic index i | CUS40000 | DI_Map_LogicIndex_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9894 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
637 | DO_Map_LogicIndex_0 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9895 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
638 | DO_Map_LogicIndex_1 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9896 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
639 | DO_Map_LogicIndex_2 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9897 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
640 | DO_Map_LogicIndex_3 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9898 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
641 | DO_Map_LogicIndex_4 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9899 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
642 | DO_Map_LogicIndex_6 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9900 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
643 | DO_Map_LogicIndex_5 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9901 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
644 | DO_Map_LogicIndex_7 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9902 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
645 | DO_Map_LogicIndex_8 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9903 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
646 | DO_Map_LogicIndex_9 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9904 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
647 | DO_Map_LogicIndex_10 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9905 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
648 | DO_Map_LogicIndex_11 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9906 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
649 | DO_Map_LogicIndex_12 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9907 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
650 | DO_Map_LogicIndex_13 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9908 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
651 | DO_Map_LogicIndex_14 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_14 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9909 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
652 | DO_Map_LogicIndex_15 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_15 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9910 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
653 | DO_Map_LogicIndex_16 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_16 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9911 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
654 | DO_Map_LogicIndex_17 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_17 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9912 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
655 | DO_Map_LogicIndex_18 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_18 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9913 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
656 | DO_Map_LogicIndex_19 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_19 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9914 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
657 | DO_Map_LogicIndex_20 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_20 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9915 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
658 | DO_Map_LogicIndex_21 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_21 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9916 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
659 | DO_Map_LogicIndex_22 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_22 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9917 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
660 | DO_Map_LogicIndex_23 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_23 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9918 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
661 | DO_Map_LogicIndex_24 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_24 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9919 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
662 | DO_Map_LogicIndex_25 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_25 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9920 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
663 | DO_Map_LogicIndex_26 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_26 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9921 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
664 | DO_Map_LogicIndex_27 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_27 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9922 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
665 | DO_Map_LogicIndex_28 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_28 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9923 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
666 | DO_Map_LogicIndex_29 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_29 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9924 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
667 | DO_Map_LogicIndex_30 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_30 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9925 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
668 | DO_Map_LogicIndex_31 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_31 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9926 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
669 | DO_Map_LogicIndex_free1 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9927 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
670 | DO_Map_LogicIndex_free2 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9928 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
671 | DO_Map_LogicIndex_free3 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9929 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
672 | DO_Map_LogicIndex_free4 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9930 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
673 | DO_Map_LogicIndex_free5 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9931 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
674 | DO_Map_LogicIndex_free6 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9932 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
675 | DO_Map_LogicIndex_free7 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9933 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
676 | DO_Map_LogicIndex_free8 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9934 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
677 | DO_Map_LogicIndex_free9 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9935 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
678 | DO_Map_LogicIndex_free10 | Physical mapping of logic index i | CUS40000 | DO_Map_LogicIndex_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9936 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
679 | AO_Map_LogicIndex_0 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_0 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9937 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
680 | AO_Map_LogicIndex_1 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_1 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9938 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
681 | AO_Map_LogicIndex_2 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_2 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9939 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
682 | AO_Map_LogicIndex_3 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_3 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9940 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
683 | AO_Map_LogicIndex_4 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_4 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9941 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
684 | AO_Map_LogicIndex_5 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9942 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
685 | AO_Map_LogicIndex_6 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9943 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
686 | AO_Map_LogicIndex_7 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9944 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
687 | AO_Map_LogicIndex_8 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9945 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
688 | AO_Map_LogicIndex_9 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9946 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
689 | AO_Map_LogicIndex_10 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9947 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
690 | AO_Map_LogicIndex_11 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_11 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9948 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
691 | AO_Map_LogicIndex_12 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_12 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9949 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
692 | AO_Map_LogicIndex_13 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_13 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9950 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
693 | AO_Map_LogicIndex_free5 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free5 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9951 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
694 | AO_Map_LogicIndex_free6 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free6 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9952 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
695 | AO_Map_LogicIndex_free7 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free7 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9953 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
696 | AO_Map_LogicIndex_free8 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free8 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9954 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
697 | AO_Map_LogicIndex_free9 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free9 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9955 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
698 | AO_Map_LogicIndex_free10 | Physical mapping of logic index i | CUS40000 | AO_Map_LogicIndex_free10 |  | 0 | 255 |  |  | FIX(VMU00020) |  |  |  | P | 9956 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
699 | Unit_DD | Unit Working Days | CUS40000 | Unit_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9979 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
700 | Unit_HH | Unit Working Hours | CUS40000 | Unit_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9980 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
701 | FanSupply_DD | Supply Fan Working Days | CUS40000 | FanSupply_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9981 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
702 | FanSupply_HH | Supply Fan Working Hours | CUS40000 | FanSupply_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9982 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
703 | FanReturn_DD | Return Fan Working Days | CUS40000 | FanReturn_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9983 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
704 | FanReturn_HH | Return Fan Working Hours | CUS40000 | FanReturn_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9984 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
705 | FanSupplyBck_DD | Supply Fan 2 Working Days | CUS40000 | FanSupplyBck_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9985 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
706 | FanSupplyBck_HH | Supply Fan 2 Working Hours | CUS40000 | FanSupplyBck_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9986 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
707 | FanReturnBck_DD | Return Fan 2 Working Days | CUS40000 | FanReturnBck_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9987 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
708 | FanReturnBck_HH | Return Fan 2 Working Hours | CUS40000 | FanReturnBck_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 9988 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
709 | Status_PlantMode | Unit Working Mode | CUS40000 | Status_PlantMode |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 9999 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
710 | Status_PID_TSupplyCool | Cooling Regulator Request | CUS40000 | Status_PID_TSupplyCool |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10000 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
711 | Status_PID_TSupplyHeat | Heating Regulator Request | CUS40000 | Status_PID_TSupplyHeat |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10001 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
712 | Status_PID_Humid | Hmidification Regulator Request | CUS40000 | Status_PID_Humid |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10002 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
713 | Status_PID_DeHumid | Dehumidification Regulator Request | CUS40000 | Status_PID_DeHumid |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10003 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
714 | Status_PID_AirQ | Air Quality Regulator Request | CUS40000 | Status_PID_AirQ |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10004 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
715 | Status_PID_PrSupply | Supply Fan Regulator Request | CUS40000 | Status_PID_PrSupply |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10005 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
716 | Status_PID_PrReturn | Return Fan Regulator Request | CUS40000 | Status_PID_PrReturn |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10006 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
717 | Status_PID_PreHeater | Preheater Regulator Request | CUS40000 | Status_PID_PreHeater |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10007 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
718 | Status_OutCool | Cooling Output | CUS40000 | Status_OutCool |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10008 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
719 | Status_OutPre | Preheating Output | CUS40000 | Status_OutPre |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10009 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
720 | Status_OutHeat | Heating Output | CUS40000 | Status_OutHeat |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10010 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
721 | Status_OutPost | Post Heating Output | CUS40000 | Status_OutPost |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10011 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
722 | Status_OutRec | Recovery Output | CUS40000 | Status_OutRec |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10012 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
723 | Status_OutHum | Humidifier Output | CUS40000 | Status_OutHum |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10013 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
724 | Status_FanSupply | Fan Supply Speed | CUS40000 | Status_FanSupply |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10014 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
725 | Status_FanReturn | Fan Return Speed | CUS40000 | Status_FanReturn |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10015 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
726 | Status_ExtDamper | External Damper Status | CUS40000 | Status_ExtDamper |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10016 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
727 | Status_FreeCooling | Free Cooling Status | CUS40000 | Status_FreeCooling |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10017 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
728 | Status_FreeHeating | Free Heating Status | CUS40000 | Status_FreeHeating |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10018 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
729 | Status_ActuatorsOffbyFCH | Actuators off by Free Cooling/Heating | CUS40000 | Status_ActuatorsOffbyFCH |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10019 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
730 | Status_FCHreq | Free Cooling/Heating Request | CUS40000 | Status_FCHreq |  | -32768 | 32767 |  | TRUE | FIX(VMU00026) |  |  |  | P | 10020 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
731 | Status_RecoveryCooling | Cooling Recovery Status | CUS40000 | Status_RecoveryCooling |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10021 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
732 | Status_RecoveryHeating | Heating Recovery Status | CUS40000 | Status_RecoveryHeating |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10022 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
733 | Status_DefrostFan | Defrost with Fan Status | CUS40000 | Status_DefrostFan |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10023 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
734 | Status_DefrostDamper | Defrost with Damper Status | CUS40000 | Status_DefrostDamper |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10024 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
735 | Status_DefrostPreHeat | Defrost with Preheating Status | CUS40000 | Status_DefrostPreHeat |  | 0 | 1 |  | TRUE | FIX(VMU00021) |  |  |  | P | 10025 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
736 | Status_DefrostFanRed | Defrost Supply Fan Speed Reduction | CUS40000 | Status_DefrostFanRed |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 10026 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
737 | Status_LowTempSupplyLimit | Low Supply Limit Regulator Request | CUS40000 | Status_LowTempSupplyLimit |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 10027 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
738 | Status_HighTempSupplyLimit | High Supply Limit Regulator Request | CUS40000 | Status_HighTempSupplyLimit |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 10028 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
739 | Status_HighTempPreHeatLimit | High Preheater Limit Regulator Request | CUS40000 | Status_HighTempPreHeatLimit |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 10029 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
740 | Status_HighHumSupplyLimit | High Humidity Limit Regulator Request | CUS40000 | Status_HighHumSupplyLimit |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00026) |  |  |  | P | 10030 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
741 | Status_ExtSHum | External Specific Humidity | CUS40000 | Status_ExtSHum |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 10031 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
742 | Status_RetSHum | Return Specific Humidity | CUS40000 | Status_RetSHum |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00020) |  |  |  | P | 10032 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
743 | Status_Supply1_FansActualSpeed | Supply Ziehl/EBM Speed | CUS40000 | Status_Supply1_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10033 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
744 | Status_Supply1_FansVoltage | Supply Ziehl/EBM DC Voltage | CUS40000 | Status_Supply1_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10034 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
745 | Status_Supply1_FansCurrent | Supply Ziehl/EBM Current | CUS40000 | Status_Supply1_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10035 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
746 | Status_Supply1_FansActualSpeedHz | Supply ATV212 Speed | CUS40000 | Status_Supply1_FansActualSpeedHz |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00010) |  |  |  | P | 10036 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
747 | Status_Supply1_FansVoltagePerc | Supply ATV212 DC Voltage | CUS40000 | Status_Supply1_FansVoltagePerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10037 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
748 | Status_Supply1_FansCurrentPerc | Supply ATV212 DC Current | CUS40000 | Status_Supply1_FansCurrentPerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10038 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
749 | Status_Supply2_FansActualSpeed | Supply Backup Ziehl/EBM Speed | CUS40000 | Status_Supply2_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10039 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
750 | Status_Supply2_FansVoltage | Supply Backup Ziehl/EBM DC Voltage | CUS40000 | Status_Supply2_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10040 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
751 | Status_Supply2_FansCurrent | Supply Backup Ziehl/EBM Current | CUS40000 | Status_Supply2_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10041 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
752 | Status_Supply2_FansActualSpeedHz | Supply Backup ATV212 Speed | CUS40000 | Status_Supply2_FansActualSpeedHz |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00010) |  |  |  | P | 10042 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
753 | Status_Supply2_FansVoltagePerc | Supply Backup ATV212 DC Voltage | CUS40000 | Status_Supply2_FansVoltagePerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10043 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
754 | Status_Supply2_FansCurrentPerc | Supply Backup ATV212 DC Current | CUS40000 | Status_Supply2_FansCurrentPerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10044 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
755 | Status_Return1_FansActualSpeed | Return Ziehl/EBM Speed | CUS40000 | Status_Return1_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10045 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
756 | Status_Return1_FansVoltage | Return Ziehl/EBM DC Voltage | CUS40000 | Status_Return1_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10046 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
757 | Status_Return1_FansCurrent | Return Ziehl/EBM Current | CUS40000 | Status_Return1_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10047 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
758 | Status_Return1_FansActualSpeedHz | Return ATV212 Speed | CUS40000 | Status_Return1_FansActualSpeedHz |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00010) |  |  |  | P | 10048 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
759 | Status_Return1_FansVoltagePerc | Return ATV212 DC Voltage | CUS40000 | Status_Return1_FansVoltagePerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10049 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
760 | Status_Return1_FansCurrentPerc | Return ATV212 DC Current | CUS40000 | Status_Return1_FansCurrentPerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10050 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
761 | Status_Return2_FansActualSpeed | Return Backup Ziehl/EBM Speed | CUS40000 | Status_Return2_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10051 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
762 | Status_Return2_FansVoltage | Return Backup Ziehl/EBM DC Voltage | CUS40000 | Status_Return2_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10052 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
763 | Status_Return2_FansCurrent | Return Backup Ziehl/EBM Current | CUS40000 | Status_Return2_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10053 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
764 | Status_Return2_FansActualSpeedHz | Return Backup ATV212 Speed | CUS40000 | Status_Return2_FansActualSpeedHz |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00010) |  |  |  | P | 10054 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
765 | Status_Return2_FansVoltagePerc | Return Backup ATV212 DC Voltage | CUS40000 | Status_Return2_FansVoltagePerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10055 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
766 | Status_Return2_FansCurrentPerc | Return Backup ATV212 DC Current | CUS40000 | Status_Return2_FansCurrentPerc |  | -32768 | 32767 | FIX(-2) | TRUE | FIX(VMU00026) |  |  |  | P | 10056 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
767 | Status_Supply1b_FansActualSpeed | Supply 1b Ziehl Speed | CUS40000 | Status_Supply1b_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10149 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
768 | Status_Supply1b_FansVoltage | Supply 1b Ziehl DC Voltage | CUS40000 | Status_Supply1b_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10150 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
769 | Status_Supply1b_FansCurrent | Supply 1b Ziehl Current | CUS40000 | Status_Supply1b_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10151 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
770 | Status_Supply2b_FansActualSpeed | Supply Backup b Ziehl Speed | CUS40000 | Status_Supply2b_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10152 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
771 | Status_Supply2b_FansVoltage | Supply Backup b Ziehl DC Voltage | CUS40000 | Status_Supply2b_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10153 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
772 | Status_Supply2b_FansCurrent | Supply Backup b Ziehl Current | CUS40000 | Status_Supply2b_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10154 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
773 | Status_Return1b_FansActualSpeed | Return 1b Ziehl Speed | CUS40000 | Status_Return1b_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10155 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
774 | Status_Return1b_FansVoltage | Return 1b Ziehl DC Voltage | CUS40000 | Status_Return1b_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10156 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
775 | Status_Return1b_FansCurrent | Return 1b Ziehl Current | CUS40000 | Status_Return1b_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10157 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
776 | Status_Return2b_FansActualSpeed | Return Backup b Ziehl Speed | CUS40000 | Status_Return2b_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10158 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
777 | Status_Return2b_FansVoltage | Return Backup b Ziehl DC Voltage | CUS40000 | Status_Return2b_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10159 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
778 | Status_Return2b_FansCurrent | Return Backup b Ziehl Current | CUS40000 | Status_Return2b_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10160 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
779 | Status_Supply1c_FansActualSpeed | Supply 1c Ziehl Speed | CUS40000 | Status_Supply1c_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10161 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
780 | Status_Supply1c_FansVoltage | Supply 1c Ziehl DC Voltage | CUS40000 | Status_Supply1c_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10162 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
781 | Status_Supply1c_FansCurrent | Supply 1c Ziehl Current | CUS40000 | Status_Supply1c_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10163 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
782 | Status_Supply2c_FansActualSpeed | Supply Backup c Ziehl Speed | CUS40000 | Status_Supply2c_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10164 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
783 | Status_Supply2c_FansVoltage | Supply Backup c Ziehl DC Voltage | CUS40000 | Status_Supply2c_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10165 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
784 | Status_Supply2c_FansCurrent | Supply Backup c Ziehl Current | CUS40000 | Status_Supply2c_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10166 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
785 | Status_Return1c_FansActualSpeed | Return 1c Ziehl Speed | CUS40000 | Status_Return1c_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10167 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
786 | Status_Return1c_FansVoltage | Return 1c Ziehl DC Voltage | CUS40000 | Status_Return1c_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10168 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
787 | Status_Return1c_FansCurrent | Return 1c Ziehl Current | CUS40000 | Status_Return1c_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10169 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
788 | Status_Return2c_FansActualSpeed | Return Backup c Ziehl Speed | CUS40000 | Status_Return2c_FansActualSpeed |  | -32768 | 32767 |  | TRUE | FIX(VMU00020) |  |  |  | P | 10170 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
789 | Status_Return2c_FansVoltage | Return Backup c Ziehl DC Voltage | CUS40000 | Status_Return2c_FansVoltage |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00008) |  |  |  | P | 10171 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
790 | Status_Return2c_FansCurrent | Return Backup c Ziehl Current | CUS40000 | Status_Return2c_FansCurrent |  | -32768 | 32767 | FIX(-1) | TRUE | FIX(VMU00009) |  |  |  | P | 10172 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
791 | StartMonth | Start Month - Log Period Export to USB | CUS40000 | StartMonth |  | 1 | 12 |  |  | FIX(VMU00020) |  |  |  | P | 10099 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
792 | EndMonth | End Month - Log Period Export to USB | CUS40000 | EndMonth |  | 1 | 12 |  |  | FIX(VMU00020) |  |  |  | P | 10100 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
793 | StartYear | Start Year - Log Period Export to USB | CUS40000 | StartYear |  | 0 | 99 |  |  | FIX(VMU00020) |  |  |  | P | 10101 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
794 | EndYear | End Year - Log Period Export to USB | CUS40000 | EndYear |  | 0 | 99 |  |  | FIX(VMU00020) |  |  |  | P | 10102 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
795 | SavingInProgress | Log Export to usb ongoing - Log Export to USB | CUS40000 | SavingInProgress |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10103 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
796 | SaveOk | Number of files correctly exported- Log Export to USB | CUS40000 | SaveOk |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10104 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
797 | SaveFailed | Number of files not exported- Log Export to USB | CUS40000 | SaveFailed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10105 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
798 | SavePercent | Percentage of exported files- Log Export to USB | CUS40000 | SavePercent |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10106 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
799 | SavingAllowed | Export can start - Log Export to USB | CUS40000 | SavingAllowed |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10107 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
800 | LoggingError | Log Error- Log Export to USB | CUS40000 | LoggingError |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10108 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
801 | FileDimension | Size of the current log file- Log Export to USB | CUS40000 | FileDimension |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 10109 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
802 | TotalRecordE2retain | Record saved - Log Export to USB | CUS40000 | TotalRecordE2retain |  | 0 | 4294967295 |  |  | FIX(VMU00020) |  |  |  | P | 10111 | HFFFFFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
803 | microSdMounted | microSD Mounted | CUS40000 | microSdMounted |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10113 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
804 | microSdError | microSD Error | CUS40000 | microSdError |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10114 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
805 | microSdStatus | microSd Status | CUS40000 | microSdStatus |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10115 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
806 | microSdInfo | microSd Info | CUS40000 | microSdInfo |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10116 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
807 | BridgeStatus | Bridge Function Status | CUS40000 | BridgeStatus |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10497 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
808 | SendModbusFanConfiguration | Force Modbus Fan Configuration | CUS40000 | SendModbusFanConfiguration |  | 0 | 1 |  |  | FIX(VMU00021) |  |  |  | P | 10498 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
809 | Ziehl_Basic_CMODE |  | CUS40000 | Ziehl_Basic_CMODE |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10499 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
810 | Ziehl_Basic_D1 |  | CUS40000 | Ziehl_Basic_D1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10500 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
811 | Supply1_Ziehl_Basic_PIN |  | CUS40000 | Supply1_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10501 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
812 | Supply1_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply1_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10502 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
813 | Supply1_Ziehl_Basic_SpeedCmd |  | CUS40000 | Supply1_Ziehl_Basic_SpeedCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10503 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
814 | Supply1_Ziehl_Basic_Status |  | CUS40000 | Supply1_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10504 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
815 | Supply1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply1_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10505 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
816 | Supply1_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply1_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10506 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
817 | Supply1_Ziehl_Basic_Current |  | CUS40000 | Supply1_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 10507 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
818 | Supply1_Ziehl_Basic_Voltage |  | CUS40000 | Supply1_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 10508 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
819 | Supply1_Ziehl_Basic_PINread |  | CUS40000 | Supply1_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10509 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
820 | Supply1_Ziehl_Basic_CMODEread |  | CUS40000 | Supply1_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10510 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
821 | Supply1_Ziehl_Basic_D1read |  | CUS40000 | Supply1_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10511 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
822 | Ziehl_Basic_Seinternal |  | CUS40000 | Ziehl_Basic_Seinternal |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10512 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
823 | Ziehl_Basic_ComWatchDog |  | CUS40000 | Ziehl_Basic_ComWatchDog |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10513 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
824 | Ziehl_Basic_Dummy3 |  | CUS40000 | Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10514 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
825 | Supply1_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply1_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10515 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
826 | Ziehl_Basic_Dummy2 |  | CUS40000 | Ziehl_Basic_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10516 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
827 | Return1_Ziehl_Basic_PIN |  | CUS40000 | Return1_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10517 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
828 | Return1_Ziehl_Basic_ControlCmd |  | CUS40000 | Return1_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10518 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
829 | Return1_Ziehl_Basic_SpeedCmd |  | CUS40000 | Return1_Ziehl_Basic_SpeedCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10519 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
830 | Return1_Ziehl_Basic_Status |  | CUS40000 | Return1_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10520 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
831 | Return1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return1_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10521 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
832 | Return1_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return1_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10522 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
833 | Return1_Ziehl_Basic_Current |  | CUS40000 | Return1_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 10523 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
834 | Return1_Ziehl_Basic_Voltage |  | CUS40000 | Return1_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 10524 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
835 | Return1_Ziehl_Basic_PINread |  | CUS40000 | Return1_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10525 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
836 | Return1_Ziehl_Basic_CMODEread |  | CUS40000 | Return1_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10526 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
837 | Return1_Ziehl_Basic_D1read |  | CUS40000 | Return1_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10527 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
838 | Return1_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return1_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10528 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
839 | Return1_Ziehl_Basic_Dummy2 |  | CUS40000 | Return1_Ziehl_Basic_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10529 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
840 | Return1_Ziehl_Basic_Dummy3 |  | CUS40000 | Return1_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10530 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
841 | Ziehl_Basic_Dummy4 |  | CUS40000 | Ziehl_Basic_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10531 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
842 | Ziehl_Basic_Dummy5 |  | CUS40000 | Ziehl_Basic_Dummy5 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10532 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
843 | Supply2_Ziehl_Basic_PIN |  | CUS40000 | Supply2_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10533 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
844 | Supply2_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply2_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10534 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
845 | Supply2_Ziehl_Basic_SpeedCmd |  | CUS40000 | Supply2_Ziehl_Basic_SpeedCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10535 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
846 | Supply2_Ziehl_Basic_Status |  | CUS40000 | Supply2_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10536 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
847 | Supply2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply2_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10537 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
848 | Supply2_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply2_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10538 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
849 | Supply2_Ziehl_Basic_Current |  | CUS40000 | Supply2_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 10539 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
850 | Supply2_Ziehl_Basic_Voltage |  | CUS40000 | Supply2_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 10540 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
851 | Supply2_Ziehl_Basic_PINread |  | CUS40000 | Supply2_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10541 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
852 | Supply2_Ziehl_Basic_CMODEread |  | CUS40000 | Supply2_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10542 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
853 | Supply2_Ziehl_Basic_D1read |  | CUS40000 | Supply2_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10543 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
854 | Supply2_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply2_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10544 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
855 | Supply2_Ziehl_Basic_Dummy2 |  | CUS40000 | Supply2_Ziehl_Basic_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10545 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
856 | Supply2_Ziehl_Basic_Dummy3 |  | CUS40000 | Supply2_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10546 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
857 | Ziehl_Basic_Dummy6 |  | CUS40000 | Ziehl_Basic_Dummy6 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10547 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
858 | Ziehl_Basic_Dummy7 |  | CUS40000 | Ziehl_Basic_Dummy7 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10548 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
859 | Return2_Ziehl_Basic_PIN |  | CUS40000 | Return2_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10549 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
860 | Return2_Ziehl_Basic_ControlCmd |  | CUS40000 | Return2_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10550 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
861 | Return2_Ziehl_Basic_SpeedCmd |  | CUS40000 | Return2_Ziehl_Basic_SpeedCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10551 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
862 | Return2_Ziehl_Basic_Status |  | CUS40000 | Return2_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10552 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
863 | Return2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return2_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10553 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
864 | Return2_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return2_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10554 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
865 | Return2_Ziehl_Basic_Current |  | CUS40000 | Return2_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 10555 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
866 | Return2_Ziehl_Basic_Voltage |  | CUS40000 | Return2_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 10556 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
867 | Return2_Ziehl_Basic_PINread |  | CUS40000 | Return2_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10557 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
868 | Return2_Ziehl_Basic_CMODEread |  | CUS40000 | Return2_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10558 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
869 | Return2_Ziehl_Basic_D1read |  | CUS40000 | Return2_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10559 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
870 | Return2_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return2_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10560 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
871 | Return2_Ziehl_Basic_Dummy2 |  | CUS40000 | Return2_Ziehl_Basic_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10561 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
872 | Return2_Ziehl_Basic_Dummy3 |  | CUS40000 | Return2_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10562 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
873 | EBM_SourceSetValue | D101+1 | CUS40000 | EBM_SourceSetValue |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10599 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
874 | Supply1_EBM_RunningDir | D102+1 | CUS40000 | Supply1_EBM_RunningDir |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10600 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
875 | EBM_StoreSetValue | D103+1 | CUS40000 | EBM_StoreSetValue |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10601 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
876 | EBM_ControlModeDay | D106+1 | CUS40000 | EBM_ControlModeDay |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10602 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
877 | EBM_ControlModeNight | D107+1 | CUS40000 | EBM_ControlModeNight |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10603 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
878 | EBM_MotorStopEnableDay | D112+1 | CUS40000 | EBM_MotorStopEnableDay |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10604 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
879 | EBM_MotorStopEnableNight | D113+1 | CUS40000 | EBM_MotorStopEnableNight |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10605 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
880 | Supply1_EBM_SourceSetValueRead | D101+1 | CUS40000 | Supply1_EBM_SourceSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10606 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
881 | Supply1_EBM_RunningDirRead | D102+1 | CUS40000 | Supply1_EBM_RunningDirRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10607 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
882 | Supply1_EBM_StoreSetValueRead | D103+1 | CUS40000 | Supply1_EBM_StoreSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10608 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
883 | Supply1_EBM_ControlModeDayRead | D106+1 | CUS40000 | Supply1_EBM_ControlModeDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10609 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
884 | Supply1_EBM_ControlModeNightRead | D107+1 | CUS40000 | Supply1_EBM_ControlModeNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10610 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
885 | Supply1_EBM_MotorStopEnableDayRead | D112+1 | CUS40000 | Supply1_EBM_MotorStopEnableDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10611 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
886 | Supply1_EBM_MotorStopEnableNightRead | D113+1 | CUS40000 | Supply1_EBM_MotorStopEnableNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10612 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
887 | Supply1_EBM_MaxSpeed | D119+1 | CUS40000 | Supply1_EBM_MaxSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10613 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
888 | Supply1_EBM_Reset |  | CUS40000 | Supply1_EBM_Reset |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10614 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
889 | Supply1_EBM_SpecifiedSet |  | CUS40000 | Supply1_EBM_SpecifiedSet |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10615 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
890 | Supply1_EBM_ActualSpeed |  | CUS40000 | Supply1_EBM_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10616 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
891 | Supply1_EBM_MotorStatus | EBM D011+1 : Motor status | CUS40000 | Supply1_EBM_MotorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10617 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
892 | Supply1_EBM_Warning |  | CUS40000 | Supply1_EBM_Warning |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10618 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
893 | Supply1_EBM_DCLinkVoltage |  | CUS40000 | Supply1_EBM_DCLinkVoltage |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10619 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
894 | Supply1_EBM_DCLinkCurrent |  | CUS40000 | Supply1_EBM_DCLinkCurrent |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10620 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
895 | Supply1_EBM_DCLinkVRef |  | CUS40000 | Supply1_EBM_DCLinkVRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10621 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
896 | Supply1_EBM_DCLinkCRef |  | CUS40000 | Supply1_EBM_DCLinkCRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10622 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
897 | Supply1_EBM_Dummy1 |  | CUS40000 | Supply1_EBM_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10623 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
898 | Supply1_EBM_Dummy2 |  | CUS40000 | Supply1_EBM_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10624 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
899 | EBM_Dummy1 | D101+1 | CUS40000 | EBM_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10625 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
900 | Return1_EBM_RunningDir | D102+1 | CUS40000 | Return1_EBM_RunningDir |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10626 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
901 | EBM_Dummy2 | D103+1 | CUS40000 | EBM_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10627 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
902 | EBM_Dummy3 | D106+1 | CUS40000 | EBM_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10628 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
903 | EBM_Dummy4 | D107+1 | CUS40000 | EBM_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10629 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
904 | EBM_Dummy5 | D112+1 | CUS40000 | EBM_Dummy5 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10630 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
905 | EBM_Dummy6 | D113+1 | CUS40000 | EBM_Dummy6 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10631 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
906 | Return1_EBM_SourceSetValueRead | D101+1 | CUS40000 | Return1_EBM_SourceSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10632 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
907 | Return1_EBM_RunningDirRead | D102+1 | CUS40000 | Return1_EBM_RunningDirRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10633 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
908 | Return1_EBM_StoreSetValueRead | D103+1 | CUS40000 | Return1_EBM_StoreSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10634 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
909 | Return1_EBM_ControlModeDayRead | D106+1 | CUS40000 | Return1_EBM_ControlModeDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10635 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
910 | Return1_EBM_ControlModeNightRead | D107+1 | CUS40000 | Return1_EBM_ControlModeNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10636 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
911 | Return1_EBM_MotorStopEnableDayRead | D112+1 | CUS40000 | Return1_EBM_MotorStopEnableDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10637 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
912 | Return1_EBM_MotorStopEnableNightRead | D113+1 | CUS40000 | Return1_EBM_MotorStopEnableNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10638 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
913 | Return1_EBM_MaxSpeed | D119+1 | CUS40000 | Return1_EBM_MaxSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10639 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
914 | Return1_EBM_Reset |  | CUS40000 | Return1_EBM_Reset |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10640 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
915 | Return1_EBM_SpecifiedSet |  | CUS40000 | Return1_EBM_SpecifiedSet |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10641 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
916 | Return1_EBM_ActualSpeed |  | CUS40000 | Return1_EBM_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10642 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
917 | Return1_EBM_MotorStatus | EBM D011+1 : Motor status | CUS40000 | Return1_EBM_MotorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10643 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
918 | Return1_EBM_Warning |  | CUS40000 | Return1_EBM_Warning |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10644 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
919 | Return1_EBM_DCLinkVoltage |  | CUS40000 | Return1_EBM_DCLinkVoltage |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10645 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
920 | Return1_EBM_DCLinkCurrent |  | CUS40000 | Return1_EBM_DCLinkCurrent |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10646 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
921 | Return1_EBM_DCLinkVRef |  | CUS40000 | Return1_EBM_DCLinkVRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10647 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
922 | Return1_EBM_DCLinkCRef |  | CUS40000 | Return1_EBM_DCLinkCRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10648 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
923 | Return1_EBM_Dummy1 |  | CUS40000 | Return1_EBM_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10649 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
924 | Return1_EBM_Dummy2 |  | CUS40000 | Return1_EBM_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10650 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
925 | EBM_Dummy7 | D101+1 | CUS40000 | EBM_Dummy7 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10651 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
926 | Supply2_EBM_RunningDir | D102+1 | CUS40000 | Supply2_EBM_RunningDir |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10652 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
927 | EBM_Dummy8 | D103+1 | CUS40000 | EBM_Dummy8 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10653 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
928 | EBM_Dummy9 | D106+1 | CUS40000 | EBM_Dummy9 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10654 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
929 | EBM_Dummy10 | D107+1 | CUS40000 | EBM_Dummy10 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10655 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
930 | EBM_Dummy11 | D112+1 | CUS40000 | EBM_Dummy11 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10656 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
931 | EBM_Dummy12 | D113+1 | CUS40000 | EBM_Dummy12 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10657 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
932 | Supply2_EBM_SourceSetValueRead | D101+1 | CUS40000 | Supply2_EBM_SourceSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10658 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
933 | Supply2_EBM_RunningDirRead | D102+1 | CUS40000 | Supply2_EBM_RunningDirRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10659 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
934 | Supply2_EBM_StoreSetValueRead | D103+1 | CUS40000 | Supply2_EBM_StoreSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10660 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
935 | Supply2_EBM_ControlModeDayRead | D106+1 | CUS40000 | Supply2_EBM_ControlModeDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10661 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
936 | Supply2_EBM_ControlModeNightRead | D107+1 | CUS40000 | Supply2_EBM_ControlModeNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10662 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
937 | Supply2_EBM_MotorStopEnableDayRead | D112+1 | CUS40000 | Supply2_EBM_MotorStopEnableDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10663 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
938 | Supply2_EBM_MotorStopEnableNightRead | D113+1 | CUS40000 | Supply2_EBM_MotorStopEnableNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10664 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
939 | Supply2_EBM_MaxSpeed | D119+1 | CUS40000 | Supply2_EBM_MaxSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10665 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
940 | Supply2_EBM_Reset |  | CUS40000 | Supply2_EBM_Reset |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10666 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
941 | Supply2_EBM_SpecifiedSet |  | CUS40000 | Supply2_EBM_SpecifiedSet |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10667 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
942 | Supply2_EBM_ActualSpeed |  | CUS40000 | Supply2_EBM_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10668 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
943 | Supply2_EBM_MotorStatus | EBM D011+1 : Motor status | CUS40000 | Supply2_EBM_MotorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10669 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
944 | Supply2_EBM_Warning |  | CUS40000 | Supply2_EBM_Warning |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10670 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
945 | Supply2_EBM_DCLinkVoltage |  | CUS40000 | Supply2_EBM_DCLinkVoltage |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10671 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
946 | Supply2_EBM_DCLinkCurrent |  | CUS40000 | Supply2_EBM_DCLinkCurrent |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10672 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
947 | Supply2_EBM_DCLinkVRef |  | CUS40000 | Supply2_EBM_DCLinkVRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10673 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
948 | Supply2_EBM_DCLinkCRef |  | CUS40000 | Supply2_EBM_DCLinkCRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10674 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
949 | Supply2_EBM_Dummy1 |  | CUS40000 | Supply2_EBM_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10675 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
950 | Supply2_EBM_Dummy2 |  | CUS40000 | Supply2_EBM_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10676 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
951 | EBM_Dummy13 | D101+1 | CUS40000 | EBM_Dummy13 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10677 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
952 | Return2_EBM_RunningDir | D102+1 | CUS40000 | Return2_EBM_RunningDir |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10678 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
953 | EBM_Dummy14 | D103+1 | CUS40000 | EBM_Dummy14 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10679 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
954 | EBM_Dummy15 | D106+1 | CUS40000 | EBM_Dummy15 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10680 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
955 | EBM_Dummy16 | D107+1 | CUS40000 | EBM_Dummy16 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10681 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
956 | EBM_Dummy17 | D112+1 | CUS40000 | EBM_Dummy17 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10682 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
957 | EBM_Dummy18 | D113+1 | CUS40000 | EBM_Dummy18 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10683 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
958 | Return2_EBM_SourceSetValueRead | D101+1 | CUS40000 | Return2_EBM_SourceSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10684 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
959 | Return2_EBM_RunningDirRead | D102+1 | CUS40000 | Return2_EBM_RunningDirRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10685 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
960 | Return2_EBM_StoreSetValueRead | D103+1 | CUS40000 | Return2_EBM_StoreSetValueRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10686 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
961 | Return2_EBM_ControlModeDayRead | D106+1 | CUS40000 | Return2_EBM_ControlModeDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10687 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
962 | Return2_EBM_ControlModeNightRead | D107+1 | CUS40000 | Return2_EBM_ControlModeNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10688 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
963 | Return2_EBM_MotorStopEnableDayRead | D112+1 | CUS40000 | Return2_EBM_MotorStopEnableDayRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10689 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
964 | Return2_EBM_MotorStopEnableNightRead | D113+1 | CUS40000 | Return2_EBM_MotorStopEnableNightRead |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10690 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
965 | Return2_EBM_MaxSpeed | D119+1 | CUS40000 | Return2_EBM_MaxSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10691 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
966 | Return2_EBM_Reset |  | CUS40000 | Return2_EBM_Reset |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10692 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
967 | Return2_EBM_SpecifiedSet |  | CUS40000 | Return2_EBM_SpecifiedSet |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10693 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
968 | Return2_EBM_ActualSpeed |  | CUS40000 | Return2_EBM_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10694 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
969 | Return2_EBM_MotorStatus | EBM D011+1 : Motor status | CUS40000 | Return2_EBM_MotorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10695 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
970 | Return2_EBM_Warning |  | CUS40000 | Return2_EBM_Warning |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10696 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
971 | Return2_EBM_DCLinkVoltage |  | CUS40000 | Return2_EBM_DCLinkVoltage |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10697 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
972 | Return2_EBM_DCLinkCurrent |  | CUS40000 | Return2_EBM_DCLinkCurrent |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10698 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
973 | Return2_EBM_DCLinkVRef |  | CUS40000 | Return2_EBM_DCLinkVRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10699 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
974 | Return2_EBM_DCLinkCRef |  | CUS40000 | Return2_EBM_DCLinkCRef |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10700 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
975 | Return2_EBM_Dummy1 |  | CUS40000 | Return2_EBM_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10701 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
976 | Return2_EBM_Dummy2 |  | CUS40000 | Return2_EBM_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10702 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
977 | Fan_ATV212_CMOD | ATV212: 3+1 | CUS40000 | Fan_ATV212_CMOD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10799 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
978 | Fan_ATV212_FMOD | ATV212: 4+1 | CUS40000 | Fan_ATV212_FMOD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10800 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
979 | Fan_ATV212_Timeout | ATV212: 2051+1 | CUS40000 | Fan_ATV212_Timeout |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10801 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
980 | Fan_ATV212_F732 | ATV212: 1842+1 | CUS40000 | Fan_ATV212_F732 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10802 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
981 | Supply1_ATV212_CMODread | ATV212: 3+1 | CUS40000 | Supply1_ATV212_CMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10803 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
982 | Supply1_ATV212_FMODread | ATV212: 4+1 | CUS40000 | Supply1_ATV212_FMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10804 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
983 | Supply1_ATV212_Timeoutread | ATV212: 2051+1 | CUS40000 | Supply1_ATV212_Timeoutread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10805 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
984 | Supply1_ATV212_F732read | ATV212: 1842+1 | CUS40000 | Supply1_ATV212_F732read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10806 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
985 | Supply1_ATV212_FreqMin | Minimum Frequency ATV212: 19+1 | CUS40000 | Supply1_ATV212_FreqMin |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10807 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
986 | Supply1_ATV212_FreqMax | Maximum Frequency ATV212: 20+1 | CUS40000 | Supply1_ATV212_FreqMax |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10808 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
987 | Supply1_ATV212_Command | ATV212: 64000+1 FA00 | CUS40000 | Supply1_ATV212_Command |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10809 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
988 | Supply1_ATV212_CmdFreq | ATV212: 64001+1 FA01 | CUS40000 | Supply1_ATV212_CmdFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10810 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
989 | Supply1_ATV212_CurrentFreq | ATV212: 64768+1 Fd00 | CUS40000 | Supply1_ATV212_CurrentFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10811 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
990 | Supply1_ATV212_Status | ATV212: 64769+1 Fd01 | CUS40000 | Supply1_ATV212_Status |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10812 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
991 | Supply1_ATV212_Trip | ATV212: 64656+1 FC90 | CUS40000 | Supply1_ATV212_Trip |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10813 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
992 | Supply1_ATV212_Alarm | ATV212: 64657+1 FC91 | CUS40000 | Supply1_ATV212_Alarm |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10814 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
993 | Supply1_ATV212_DCVoltage | ATV212: 65028+1 FE04 | CUS40000 | Supply1_ATV212_DCVoltage |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10815 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
994 | Supply1_ATV212_Current | ATV212: 65027+1 FE03 | CUS40000 | Supply1_ATV212_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10816 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
995 | Supply1_ATV212_Dummy1 |  | CUS40000 | Supply1_ATV212_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10817 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
996 | Supply1_ATV212_Dummy2 |  | CUS40000 | Supply1_ATV212_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10818 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
997 | Supply1_ATV212_Dummy3 |  | CUS40000 | Supply1_ATV212_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10819 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
998 | Supply1_ATV212_Dummy4 |  | CUS40000 | Supply1_ATV212_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10820 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
999 | Fan_ATV212_Dummy1 | ATV212: 3+1 | CUS40000 | Fan_ATV212_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10821 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1000 | Fan_ATV212_Dummy2 | ATV212: 4+1 | CUS40000 | Fan_ATV212_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10822 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1001 | Fan_ATV212_Dummy3 | ATV212: 2051+1 | CUS40000 | Fan_ATV212_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10823 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1002 | Fan_ATV212_Dummy4 | ATV212: 1842+1 | CUS40000 | Fan_ATV212_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10824 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1003 | Return1_ATV212_CMODread | ATV212: 3+1 | CUS40000 | Return1_ATV212_CMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10825 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1004 | Return1_ATV212_FMODread | ATV212: 4+1 | CUS40000 | Return1_ATV212_FMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10826 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1005 | Return1_ATV212_Timeoutread | ATV212: 2051+1 | CUS40000 | Return1_ATV212_Timeoutread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10827 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1006 | Return1_ATV212_F732read | ATV212: 1842+1 | CUS40000 | Return1_ATV212_F732read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10828 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1007 | Return1_ATV212_FreqMin | Minimum Frequency ATV212: 19+1 | CUS40000 | Return1_ATV212_FreqMin |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10829 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1008 | Return1_ATV212_FreqMax | Maximum Frequency ATV212: 20+1 | CUS40000 | Return1_ATV212_FreqMax |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10830 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1009 | Return1_ATV212_Command | ATV212: 64000+1 FA00 | CUS40000 | Return1_ATV212_Command |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10831 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1010 | Return1_ATV212_CmdFreq | ATV212: 64001+1 FA01 | CUS40000 | Return1_ATV212_CmdFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10832 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1011 | Return1_ATV212_CurrentFreq | ATV212: 64768+1 Fd00 | CUS40000 | Return1_ATV212_CurrentFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10833 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1012 | Return1_ATV212_Status | ATV212: 64769+1 Fd01 | CUS40000 | Return1_ATV212_Status |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10834 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1013 | Return1_ATV212_Trip | ATV212: 64656+1 FC90 | CUS40000 | Return1_ATV212_Trip |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10835 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1014 | Return1_ATV212_Alarm | ATV212: 64657+1 FC91 | CUS40000 | Return1_ATV212_Alarm |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10836 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1015 | Return1_ATV212_DCVoltage | ATV212: 65028+1 FE04 | CUS40000 | Return1_ATV212_DCVoltage |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10837 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1016 | Return1_ATV212_Current | ATV212: 65027+1 FE03 | CUS40000 | Return1_ATV212_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10838 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1017 | Return1_ATV212_Dummy1 |  | CUS40000 | Return1_ATV212_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10839 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1018 | Return1_ATV212_Dummy2 |  | CUS40000 | Return1_ATV212_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10840 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1019 | Return1_ATV212_Dummy3 |  | CUS40000 | Return1_ATV212_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10841 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1020 | Return1_ATV212_Dummy4 |  | CUS40000 | Return1_ATV212_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10842 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1021 | Fan_ATV212_Dummy5 | ATV212: 3+1 | CUS40000 | Fan_ATV212_Dummy5 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10843 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1022 | Fan_ATV212_Dummy6 | ATV212: 4+1 | CUS40000 | Fan_ATV212_Dummy6 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10844 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1023 | Fan_ATV212_Dummy7 | ATV212: 2051+1 | CUS40000 | Fan_ATV212_Dummy7 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10845 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1024 | Fan_ATV212_Dummy8 | ATV212: 1842+1 | CUS40000 | Fan_ATV212_Dummy8 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10846 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1025 | Supply2_ATV212_CMODread | ATV212: 3+1 | CUS40000 | Supply2_ATV212_CMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10847 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1026 | Supply2_ATV212_FMODread | ATV212: 4+1 | CUS40000 | Supply2_ATV212_FMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10848 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1027 | Supply2_ATV212_Timeoutread | ATV212: 2051+1 | CUS40000 | Supply2_ATV212_Timeoutread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10849 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1028 | Supply2_ATV212_F732read | ATV212: 1842+1 | CUS40000 | Supply2_ATV212_F732read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10850 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1029 | Supply2_ATV212_FreqMin | Minimum Frequency ATV212: 19+1 | CUS40000 | Supply2_ATV212_FreqMin |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10851 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1030 | Supply2_ATV212_FreqMax | Maximum Frequency ATV212: 20+1 | CUS40000 | Supply2_ATV212_FreqMax |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10852 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1031 | Supply2_ATV212_Command | ATV212: 64000+1 FA00 | CUS40000 | Supply2_ATV212_Command |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10853 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1032 | Supply2_ATV212_CmdFreq | ATV212: 64001+1 FA01 | CUS40000 | Supply2_ATV212_CmdFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10854 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1033 | Supply2_ATV212_CurrentFreq | ATV212: 64768+1 Fd00 | CUS40000 | Supply2_ATV212_CurrentFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10855 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1034 | Supply2_ATV212_Status | ATV212: 64769+1 Fd01 | CUS40000 | Supply2_ATV212_Status |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10856 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1035 | Supply2_ATV212_Trip | ATV212: 64656+1 FC90 | CUS40000 | Supply2_ATV212_Trip |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10857 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1036 | Supply2_ATV212_Alarm | ATV212: 64657+1 FC91 | CUS40000 | Supply2_ATV212_Alarm |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10858 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1037 | Supply2_ATV212_DCVoltage | ATV212: 65028+1 FE04 | CUS40000 | Supply2_ATV212_DCVoltage |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10859 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1038 | Supply2_ATV212_Current | ATV212: 65027+1 FE03 | CUS40000 | Supply2_ATV212_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10860 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1039 | Supply2_ATV212_Dummy1 |  | CUS40000 | Supply2_ATV212_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10861 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1040 | Supply2_ATV212_Dummy2 |  | CUS40000 | Supply2_ATV212_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10862 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1041 | Supply2_ATV212_Dummy3 |  | CUS40000 | Supply2_ATV212_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10863 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1042 | Supply2_ATV212_Dummy4 |  | CUS40000 | Supply2_ATV212_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10864 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1043 | Fan_ATV212_Dummy9 | ATV212: 3+1 | CUS40000 | Fan_ATV212_Dummy9 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10865 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1044 | Fan_ATV212_Dummy10 | ATV212: 4+1 | CUS40000 | Fan_ATV212_Dummy10 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10866 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1045 | Fan_ATV212_Dummy11 | ATV212: 2051+1 | CUS40000 | Fan_ATV212_Dummy11 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10867 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1046 | Fan_ATV212_Dummy12 | ATV212: 1842+1 | CUS40000 | Fan_ATV212_Dummy12 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10868 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1047 | Return2_ATV212_CMODread | ATV212: 3+1 | CUS40000 | Return2_ATV212_CMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10869 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1048 | Return2_ATV212_FMODread | ATV212: 4+1 | CUS40000 | Return2_ATV212_FMODread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10870 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1049 | Return2_ATV212_Timeoutread | ATV212: 2051+1 | CUS40000 | Return2_ATV212_Timeoutread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10871 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1050 | Return2_ATV212_F732read | ATV212: 1842+1 | CUS40000 | Return2_ATV212_F732read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10872 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1051 | Return2_ATV212_FreqMin | Minimum Frequency ATV212: 19+1 | CUS40000 | Return2_ATV212_FreqMin |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10873 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1052 | Return2_ATV212_FreqMax | Maximum Frequency ATV212: 20+1 | CUS40000 | Return2_ATV212_FreqMax |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10874 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1053 | Return2_ATV212_Command | ATV212: 64000+1 FA00 | CUS40000 | Return2_ATV212_Command |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10875 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1054 | Return2_ATV212_CmdFreq | ATV212: 64001+1 FA01 | CUS40000 | Return2_ATV212_CmdFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10876 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1055 | Return2_ATV212_CurrentFreq | ATV212: 64768+1 Fd00 | CUS40000 | Return2_ATV212_CurrentFreq |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00010) |  |  |  | P | 10877 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1056 | Return2_ATV212_Status | ATV212: 64769+1 Fd01 | CUS40000 | Return2_ATV212_Status |  | 0 | 65535 | %04x |  | FIX(VMU00020) |  |  |  | P | 10878 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1057 | Return2_ATV212_Trip | ATV212: 64656+1 FC90 | CUS40000 | Return2_ATV212_Trip |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10879 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1058 | Return2_ATV212_Alarm | ATV212: 64657+1 FC91 | CUS40000 | Return2_ATV212_Alarm |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 10880 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1059 | Return2_ATV212_DCVoltage | ATV212: 65028+1 FE04 | CUS40000 | Return2_ATV212_DCVoltage |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10881 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1060 | Return2_ATV212_Current | ATV212: 65027+1 FE03 | CUS40000 | Return2_ATV212_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00026) |  |  |  | P | 10882 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1061 | Return2_ATV212_Dummy1 |  | CUS40000 | Return2_ATV212_Dummy1 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10883 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1062 | Return2_ATV212_Dummy2 |  | CUS40000 | Return2_ATV212_Dummy2 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10884 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1063 | Return2_ATV212_Dummy3 |  | CUS40000 | Return2_ATV212_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10885 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1064 | Return2_ATV212_Dummy4 |  | CUS40000 | Return2_ATV212_Dummy4 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 10886 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1065 | Supply1b_Ziehl_Basic_Status |  | CUS40000 | Supply1b_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11299 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1066 | Supply1b_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply1b_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11300 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1067 | Supply1b_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply1b_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11301 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1068 | Supply1b_Ziehl_Basic_Current |  | CUS40000 | Supply1b_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11302 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1069 | Supply1b_Ziehl_Basic_Voltage |  | CUS40000 | Supply1b_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11303 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1070 | Supply1b_Ziehl_Basic_PINread |  | CUS40000 | Supply1b_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11304 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1071 | Supply1b_Ziehl_Basic_CMODEread |  | CUS40000 | Supply1b_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11305 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1072 | Supply1b_Ziehl_Basic_D1read |  | CUS40000 | Supply1b_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11306 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1073 | Supply1b_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply1b_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11307 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1074 | Supply1b_Ziehl_Basic_PIN |  | CUS40000 | Supply1b_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11308 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1075 | Supply1b_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply1b_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11309 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1076 | Supply1b_Ziehl_Basic_Dummy3 |  | CUS40000 | Supply1b_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11310 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1077 | Supply1c_Ziehl_Basic_Status |  | CUS40000 | Supply1c_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11311 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1078 | Supply1c_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply1c_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11312 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1079 | Supply1c_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply1c_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11313 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1080 | Supply1c_Ziehl_Basic_Current |  | CUS40000 | Supply1c_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11314 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1081 | Supply1c_Ziehl_Basic_Voltage |  | CUS40000 | Supply1c_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11315 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1082 | Supply1c_Ziehl_Basic_PINread |  | CUS40000 | Supply1c_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11316 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1083 | Supply1c_Ziehl_Basic_CMODEread |  | CUS40000 | Supply1c_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11317 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1084 | Supply1c_Ziehl_Basic_D1read |  | CUS40000 | Supply1c_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11318 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1085 | Supply1c_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply1c_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11319 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1086 | Supply1c_Ziehl_Basic_PIN |  | CUS40000 | Supply1c_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11320 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1087 | Supply1c_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply1c_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11321 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1088 | Supply1c_Ziehl_Basic_Dummy3 |  | CUS40000 | Supply1c_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11322 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1089 | Return1b_Ziehl_Basic_Status |  | CUS40000 | Return1b_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11323 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1090 | Return1b_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return1b_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11324 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1091 | Return1b_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return1b_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11325 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1092 | Return1b_Ziehl_Basic_Current |  | CUS40000 | Return1b_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11326 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1093 | Return1b_Ziehl_Basic_Voltage |  | CUS40000 | Return1b_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11327 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1094 | Return1b_Ziehl_Basic_PINread |  | CUS40000 | Return1b_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11328 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1095 | Return1b_Ziehl_Basic_CMODEread |  | CUS40000 | Return1b_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11329 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1096 | Return1b_Ziehl_Basic_D1read |  | CUS40000 | Return1b_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11330 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1097 | Return1b_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return1b_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11331 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1098 | Return1b_Ziehl_Basic_PIN |  | CUS40000 | Return1b_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11332 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1099 | Return1b_Ziehl_Basic_ControlCmd |  | CUS40000 | Return1b_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11333 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1100 | Return1b_Ziehl_Basic_Dummy3 |  | CUS40000 | Return1b_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11334 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1101 | Return1c_Ziehl_Basic_Status |  | CUS40000 | Return1c_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11335 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1102 | Return1c_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return1c_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11336 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1103 | Return1c_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return1c_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11337 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1104 | Return1c_Ziehl_Basic_Current |  | CUS40000 | Return1c_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11338 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1105 | Return1c_Ziehl_Basic_Voltage |  | CUS40000 | Return1c_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11339 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1106 | Return1c_Ziehl_Basic_PINread |  | CUS40000 | Return1c_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11340 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1107 | Return1c_Ziehl_Basic_CMODEread |  | CUS40000 | Return1c_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11341 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1108 | Return1c_Ziehl_Basic_D1read |  | CUS40000 | Return1c_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11342 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1109 | Return1c_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return1c_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11343 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1110 | Return1c_Ziehl_Basic_PIN |  | CUS40000 | Return1c_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11344 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1111 | Return1c_Ziehl_Basic_ControlCmd |  | CUS40000 | Return1c_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11345 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1112 | Return1c_Ziehl_Basic_Dummy3 |  | CUS40000 | Return1c_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11346 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1113 | Supply2b_Ziehl_Basic_Status |  | CUS40000 | Supply2b_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11347 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1114 | Supply2b_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply2b_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11348 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1115 | Supply2b_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply2b_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11349 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1116 | Supply2b_Ziehl_Basic_Current |  | CUS40000 | Supply2b_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11350 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1117 | Supply2b_Ziehl_Basic_Voltage |  | CUS40000 | Supply2b_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11351 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1118 | Supply2b_Ziehl_Basic_PINread |  | CUS40000 | Supply2b_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11352 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1119 | Supply2b_Ziehl_Basic_CMODEread |  | CUS40000 | Supply2b_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11353 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1120 | Supply2b_Ziehl_Basic_D1read |  | CUS40000 | Supply2b_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11354 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1121 | Supply2b_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply2b_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11355 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1122 | Supply2b_Ziehl_Basic_PIN |  | CUS40000 | Supply2b_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11356 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1123 | Supply2b_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply2b_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11357 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1124 | Supply2b_Ziehl_Basic_Dummy3 |  | CUS40000 | Supply2b_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11358 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1125 | Supply2c_Ziehl_Basic_Status |  | CUS40000 | Supply2c_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11359 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1126 | Supply2c_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Supply2c_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11360 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1127 | Supply2c_Ziehl_Basic_ActualSpeed |  | CUS40000 | Supply2c_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11361 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1128 | Supply2c_Ziehl_Basic_Current |  | CUS40000 | Supply2c_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11362 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1129 | Supply2c_Ziehl_Basic_Voltage |  | CUS40000 | Supply2c_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11363 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1130 | Supply2c_Ziehl_Basic_PINread |  | CUS40000 | Supply2c_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11364 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1131 | Supply2c_Ziehl_Basic_CMODEread |  | CUS40000 | Supply2c_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11365 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1132 | Supply2c_Ziehl_Basic_D1read |  | CUS40000 | Supply2c_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11366 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1133 | Supply2c_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Supply2c_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11367 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1134 | Supply2c_Ziehl_Basic_PIN |  | CUS40000 | Supply2c_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11368 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1135 | Supply2c_Ziehl_Basic_ControlCmd |  | CUS40000 | Supply2c_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11369 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1136 | Supply2c_Ziehl_Basic_Dummy3 |  | CUS40000 | Supply2c_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11370 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1137 | Return2b_Ziehl_Basic_Status |  | CUS40000 | Return2b_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11371 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1138 | Return2b_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return2b_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11372 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1139 | Return2b_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return2b_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11373 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1140 | Return2b_Ziehl_Basic_Current |  | CUS40000 | Return2b_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11374 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1141 | Return2b_Ziehl_Basic_Voltage |  | CUS40000 | Return2b_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11375 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1142 | Return2b_Ziehl_Basic_PINread |  | CUS40000 | Return2b_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11376 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1143 | Return2b_Ziehl_Basic_CMODEread |  | CUS40000 | Return2b_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11377 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1144 | Return2b_Ziehl_Basic_D1read |  | CUS40000 | Return2b_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11378 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1145 | Return2b_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return2b_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11379 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1146 | Return2b_Ziehl_Basic_PIN |  | CUS40000 | Return2b_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11380 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1147 | Return2b_Ziehl_Basic_ControlCmd |  | CUS40000 | Return2b_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11381 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1148 | Return2b_Ziehl_Basic_Dummy3 |  | CUS40000 | Return2b_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11382 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1149 | Return2c_Ziehl_Basic_Status |  | CUS40000 | Return2c_Ziehl_Basic_Status |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11383 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1150 | Return2c_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status | CUS40000 | Return2c_Ziehl_Basic_ErrorStatus |  | 0 | 65535 | %04X |  | FIX(VMU00020) |  |  |  | P | 11384 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1151 | Return2c_Ziehl_Basic_ActualSpeed |  | CUS40000 | Return2c_Ziehl_Basic_ActualSpeed |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11385 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1152 | Return2c_Ziehl_Basic_Current |  | CUS40000 | Return2c_Ziehl_Basic_Current |  | 0 | 65535 | FIX(-2) |  | FIX(VMU00009) |  |  |  | P | 11386 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1153 | Return2c_Ziehl_Basic_Voltage |  | CUS40000 | Return2c_Ziehl_Basic_Voltage |  | 0 | 65535 |  |  | FIX(VMU00008) |  |  |  | P | 11387 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1154 | Return2c_Ziehl_Basic_PINread |  | CUS40000 | Return2c_Ziehl_Basic_PINread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11388 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1155 | Return2c_Ziehl_Basic_CMODEread |  | CUS40000 | Return2c_Ziehl_Basic_CMODEread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11389 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1156 | Return2c_Ziehl_Basic_D1read |  | CUS40000 | Return2c_Ziehl_Basic_D1read |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11390 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1157 | Return2c_Ziehl_Basic_ComWatchDogread |  | CUS40000 | Return2c_Ziehl_Basic_ComWatchDogread |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11391 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1158 | Return2c_Ziehl_Basic_PIN |  | CUS40000 | Return2c_Ziehl_Basic_PIN |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11392 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1159 | Return2c_Ziehl_Basic_ControlCmd |  | CUS40000 | Return2c_Ziehl_Basic_ControlCmd |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11393 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1160 | Return2c_Ziehl_Basic_Dummy3 |  | CUS40000 | Return2c_Ziehl_Basic_Dummy3 |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11394 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1161 | MdbZiehlSupplyMsgError |  | CUS40000 | MdbZiehlSupplyMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11499 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1162 | MdbZiehlReturnMsgError |  | CUS40000 | MdbZiehlReturnMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11500 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1163 | MdbZiehlSupplyBckMsgError |  | CUS40000 | MdbZiehlSupplyBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11501 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1164 | MdbZiehlReturnBckMsgError |  | CUS40000 | MdbZiehlReturnBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11502 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1165 | MdbEBMSupplyMsgError |  | CUS40000 | MdbEBMSupplyMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11503 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1166 | MdbEBMReturnMsgError |  | CUS40000 | MdbEBMReturnMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11504 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1167 | MdbEBMSupplyBckMsgError |  | CUS40000 | MdbEBMSupplyBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11505 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1168 | MdbEBMReturnBckMsgError |  | CUS40000 | MdbEBMReturnBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11506 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1169 | MdbATVSupplyMsgError |  | CUS40000 | MdbATVSupplyMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11507 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1170 | MdbATVReturnMsgError |  | CUS40000 | MdbATVReturnMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11508 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1171 | MdbATVSupplyBckMsgError |  | CUS40000 | MdbATVSupplyBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11509 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1172 | MdbATVReturnBckMsgError |  | CUS40000 | MdbATVReturnBckMsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11510 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1173 | MdbZiehlSupply_1b_MsgError |  | CUS40000 | MdbZiehlSupply_1b_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11511 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1174 | MdbZiehlReturn_1b_MsgError |  | CUS40000 | MdbZiehlReturn_1b_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11512 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1175 | MdbZiehlSupply_2b_MsgError |  | CUS40000 | MdbZiehlSupply_2b_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11513 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1176 | MdbZiehlReturn_2b_MsgError |  | CUS40000 | MdbZiehlReturn_2b_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11514 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1177 | MdbZiehlSupply_1c_MsgError |  | CUS40000 | MdbZiehlSupply_1c_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11515 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1178 | MdbZiehlReturn_1c_MsgError |  | CUS40000 | MdbZiehlReturn_1c_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11516 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1179 | MdbZiehlSupply_2c_MsgError |  | CUS40000 | MdbZiehlSupply_2c_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11517 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1180 | MdbZiehlReturn_2c_MsgError |  | CUS40000 | MdbZiehlReturn_2c_MsgError |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11518 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1181 | CondUnit1_DD | Condensing Unit 1 Working Days | CUS40000 | CondUnit1_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11599 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1182 | CondUnit1_HH | Condensing Unit 1 Working Hours | CUS40000 | CondUnit1_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11600 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1183 | CondUnit2_DD | Condensing Unit 2 Working Days | CUS40000 | CondUnit2_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11601 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1184 | CondUnit2_HH | Condensing Unit 2 Working Hours | CUS40000 | CondUnit2_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11602 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1185 | CondUnit3_DD | Condensing Unit 3 Working Days | CUS40000 | CondUnit3_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11603 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1186 | CondUnit3_HH | Condensing Unit 3 Working Hours | CUS40000 | CondUnit3_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11604 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1187 | CondUnit4_DD | Condensing Unit 4 Working Days | CUS40000 | CondUnit4_DD |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11605 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
1188 | CondUnit4_HH | Condensing Unit 4 Working Hours | CUS40000 | CondUnit4_HH |  | 0 | 65535 |  |  | FIX(VMU00020) |  |  |  | P | 11606 | HFFFF | FIX(0) | Analog Input |  | (UNSIG(THIS())=FIX(H8000))¦(UNSIG(THIS())=FIX(H8001))¦(UNSIG(THIS())=FIX(H8003))
Note on B1: HELP: Try to keep the lenght to no more than 3 chars. Use ENGLISH abbreviations.
Note on D1: HELP: Description code (ex: PCR00050)
Note on E1: HELP: Possible values (input => output): 1) numerical => "string {numerical}" 2) string code => string {actual string from string code} 3) empty NOTE: this apply usually to INP4* / STA4* / ALM4* / FNC4* but other are not excluded
Note on F1: HELP: Group join. The Key_Group describe the group string index. Each item has one or more groups
Note on G1: HELP: lower limit: 1) numerical value: ex. 200; 2) parameter value: ex. Param(LSE)
Note on H1: HELP: lower limit: 1) numerical value: ex. 200; 2) parameter value: ex. Param(LSE)
Note on I1: HELP: 1) any 2) FIX(+/- num): VALUE*10^(+/- num)
Note on J1: HELP: 1) any: absolute value 2) "TRUE": signed value
Note on K1: HELP: Measurement unit string: 1) FIX(VMU00018) -> fix unit measure; 2) INT({0=VMU00018,1=VMU00020},PARAM(dro))
Note on L1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on M1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence. The value format are: a) 122; b) H2002 (Hex value)
Note on N1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on O1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) E: 0x04 and 0x16 Modbus Command
Note on P1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on Q1: HELP: Micronet and Modbus filter: 1) If the resource is a numeric value, then this cell contains the bitmask to be applied to the value (e.g. H01 or HFFFF) and the information about the value endiannes (e.g. REV(HFFFF) for a little endian or HFFFF for a big endian value). 2) If the resource is an array of bytes or a string, then this cell contains the length of the array, in the format A[x] (e.g. use A[10] for a 10 bytes string). If an odd value is provided, the value will be rounded up to the next even value when the modbus protocol is used.
Note on R1: HELP: If the result is 1 THEN the resource is present ELSE the resource is not present
Note on S1: HELP: Resource type: 1) Analog Input 2) Digital Input 3) Alarm 4) Status 5) Command 6) Support 7) RTCCommand
Note on T1: HELP: If defined, the output for the resource will be the output of the statement (instead of the raw value). For example, INT(0,{0=1},THIS()) means 0 default value {0=1} IF raw value=0 THEN return 1 THIS() is the raw value
Note on U1: Antonello Tollot: Colonna speciale per le condizioni di esistenza (il valore di temp. È visualizzabile solo se non è in errore)
Note on V1: HELP: Televis identifier
Note on W1: HELP: Write operation. Name of Write sheet item
Note on X1: HELP: Combine the numerical value with a description string. Examples: 0 -> "NO", 1-> "YES" 0 -> "OFF", 1 -> "ON 0 -> "COMPRESSOR HOURS", 1 -> "DEVICE HOURS", 2 -> "RTC" Field separator is the ";" character
Note on Y1: HELP: 1) TRUE: insert this item into product manual 2) blank: do not insert this item into product manual
Note on Z1: HELP: 1) NO_TELEVIS : resource will not be included in Televis/New Televis Compact 2) NO_WEBADAPTER : resource will not be included in WebAdapter 3) NO_DEVICE_MANAGER : resource will not be included in Device Manager 4) Leave empty (deafult) : resource will be include in every product

## WriteArgs
INDEX | NAME | TYPE | FORMAT | COMPLEMENTED | SIZE | LOW_LIMIT | HIGH_LIMIT | DESCRIPTION_INDEX | PROGRESSIVE |  |  | EXCLUSION
UNSIG(THIS())=FIX(H8000)
WW_
WW_
WW_
WW_
WW_
WW_
WW_
WW_
WW_
WW_
Note on B1: HELP: Argument name, used iito Write sheet
Note on C1: HELP: Argument type: 1) NUMERIC; 2) BOOLEAN.
Note on D1: HELP: 1) any 2) FIX(+/- num): VALUE*10^(+/- num)
Note on E1: HELP: 1) any: absolute value 2) "TRUE": signed value
Note on F1: HELP: Argument data size in bytes
Note on G1: HELP: lower limit: 1) numerical value: ex. 200;
Note on H1: HELP: lower limit: 1) numerical value: ex. 200;
Note on I1: HELP: description string index (ex: PCR00050)
Note on J1: HELP: 1) any : Only String 2) numerical: string {numerical} 3) string index: string {string}

## Write
INDEX | NAME | VALUE | COMPLEMENTED | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER
Note on B1: HELP: Item name, used into Client/RTC sheet
Note on C1: HELP: Value to write
Note on D1: HELP: 1) blank: absolute value 2) TRUE: signed value
Note on E1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on F1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence and writing sequence separated by a semicolon ";". Reading sequence may be "NONE" if not required. The value format are: a) 122; b) H2002 (Hex value)
Note on G1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on H1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) E: 0x04 and 0x16 Modbus Command
Note on I1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on J1: HELP: Micronet and Modbus filter: 1: REV: used for identifier a little-endian format 2) otherwise: big-endian

## RVD
INDEX | LABEL | ELEMENT_TYPE | ON_DOWN_FILENAME | OFF_UP_FILENAME | X_POS | Y_POS | X_DIM | Y_DIM | EXISTENCE | ON_PUSH_ENABLE_CONDITION | BLINK_RELEASE_RESTORE_CONDITION
Note on B1: HELP: Item name. Must be unique.
Note on C1: HELP: Allowed values are: 1) general 2) initialization 3) bufferdisplay 4) background 5) element 6) button
Note on D1: HELP: If ELEMENT_TYPE is background, element or button, fill the cell with path and filename of the image used for the graphic item when its status is ON/DOWN. Paths are relative to the RVD folder. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on E1: HELP: If ELEMENT_TYPE is background, element or button, fill the cell with Path and filename of the image used for the graphic item when its status is OFF/UP. Paths are relative to the RVD folder. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on F1: HELP: If ELEMENT_TYPE is background, element or button fill the cell with the X coordinate of the image. If ELEMENT_TYPE is general, fill the cell with the blink time of the instrument. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on G1: HELP: If ELEMENT_TYPE is background, element or button fill the cell with the Y coordinate of the image. If ELEMENT_TYPE is general, fill the cell with the push button time of the instrument. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on H1: HELP: If ELEMENT_TYPE is background, fill the cell with the X offset value. If ELEMENT_TYPE is button, fill the cell with the X dimension of the button. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on I1: HELP: If ELEMENT_TYPE is background, fill it with the Y offset value. If ELEMENT_TYPE is button, fill it with the Y dimension of the button. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on J1: HELP: Fill the cell with the existence condition.
Note on K1: HELP: If ELEMENT_TYPE is initialization fill the cell with the RVD start up sequence. If ELEMENT_TYPE is bufferdisplay fill the cell with the RVD bufferdisplay reading sequence. If ELEMENT_TYPE is button fill the cell with the button PUSH sequence. If ELEMENT_TYPE is element fill the cell with the ON condition. If ELEMENT_TYPE is none of the above, leave the cell blank.
Note on L1: HELP: If ELEMENT_TYPE is initialization fill the cell with the RVD restore sequence. If ELEMENT_TYPE is button fill the cell with the button RELEASE sequence. If ELEMENT_TYPE is element fill the cell with the BLINK condition. If ELEMENT_TYPE is none of the above, leave the cell blank.

## RTC
INDEX | NAME | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER | WRITE_SEQUENCE
Note on B1: HELP: RTC Resource identifier: 1) InitSequence: sequence for to inizialize the write operation; 2) Seconds: seconds resource; 3) Minutes: minutes resource; 4) Hours: hours resource; 5) Day: day resource; 6) DayOfWeek: day of week resource 7) Month: month resource; 8) Year: Year resource; 9) EndSequence: sequence for conclude thewrite operation.
Note on C1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on D1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence and writing sequence separated by a semicolon ";". The value format are: a) 122; b) H2002 (Hex value)
Note on E1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on F1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) E: 0x04 and 0x16 Modbus Command
Note on G1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on H1: HELP: Micronet and Modbus filter: 1) REV: used for identifier a little-endian format 2) otherwise: big-endian
Note on I1: HELP: Write operation. Name of Write Excel sheet item

## DataBlockDesc
INDEX | LABEL | DESCRIPTION | DESCRIPTION_INDEX | PROGRESSIVE | DESCRIPTION_BLOCK | FORMAT | COMPLEMENTED | MEASUREMENT_UNIT | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER | EXISTENCE | VALUE_CONDITION | OPTIONS
Note on B1: HELP: Strings whit only 3 characters. Where not feasible, to use few characters.
Note on D1: HELP: description string index (ex: PCR00050)
Note on E1: HELP: 1) any : Only String 2) numerical: string {numerical} 3) string index: string {string}
Note on F1: HELP: Data Block Identifier, used by DataBlock Sheet
Note on G1: HELP: 1) any 2) FIX(+/- num): VALUE*10^(+/- num)
Note on H1: HELP: 1) any: absolute value 2) "TRUE": signed value
Note on I1: HELP: Measurement unit string: 1) FIX(VMU00018) -> fix unit measure; 2) INT({0=VMU00018,1=VMU00020},PARAM(dro))
Note on J1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on K1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence and writing sequence separated by a semicolon ";". The value format are: a) 122; b) H2002 (Hex value)
Note on L1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on M1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) E: 0x04 and 0x16 Modbus Command
Note on N1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on O1: HELP: Micronet and Modbus filter: 1: REV: used for identifier a little-endian format 2) otherwise: big-endian
Note on P1: HELP: If the resul is 1 the resource is present, 0 not present
Note on Q1: HELP: If defined, the output for the resource will be the output of the statement (instead of the raw value). For example, INT(0,{0=1},THIS()) means 0 default value {0=1} IF raw value=0 THEN return 1 THIS() is the raw value
Note on R1: HELP: Combine the numerical value with a description string. (ex. 0 -> "NO", 1-> "YES")

## DataBlock
INDEX | LABEL | DESCRIPTION_BLOCK | MICRONET_COMMAND | MICRONET_ADDRESS | MICRONET_SIZE_SUBADDRESS | MODBUS_COMMAND | MODBUS_ADDRESS | FILTER | OFFSET_MICRONET_ADDRESS | OFFSET_MICRONET_SIZE_SUBADDRESS | OFFSET_MODBUS_ADDRESS | EXISTENCE
Note on B1: HELP: Try to keep the lenght to no more than 3 chars. Use ENGLISH abbreviations
Note on C1: HELP: Data Block Identifier, used by DataBlock Sheet
Note on D1: HELP: Possible values: 1) L: Logical Micronet command 2) F: Physical Micronet command 3) E: Extension micronet command 4) D: Record description Micronet command 5) M: DRV_OS Micronet command 6) C: Custom or non standardized command.
Note on E1: HELP: Same order of Micronet command 1) Logical Area number (ex. 1); 2) Physical address (ex. H1001); 3) Extension address 4) DRV_OS address 5) MSB: Area; LSB: MultiArea 6) Raw reading sequence and writing sequence separated by a semicolon ";". The value format are: a) 122; b) H2002 (Hex value)
Note on F1: HELP: Same order of Micronet command: 1) Logic index (ex. 1); 2) Fisic Bytes size (ex. H1001); 3) extension address 4) DRV_OS address 5)Index The value format are: a) 122; b) H2002 (Hex value)
Note on G1: HELP: 1) S: 0x03, 0x06 Modbus Command 2) P: 0x03 and 0x10 Modbus Command 3) E: 0x04 and 0x16 Modbus Command
Note on H1: HELP: Modbus address. The value format are: a) 122; b) H2002 (Hex value)
Note on I1: HELP: Micronet and Modbus filter: 1: REV: used for identifier a little-endian format 2) otherwise: big-endian
Note on J1: HELP: This Data Block start point (address)
Note on K1: HELP: This Data Block start point (address)
Note on L1: HELP: This Data Block start point (address)
Note on M1: HELP: If the resul is 1 the resource is present, 0 not present