Air Handling Unit

FREE Advance

1.	Introduction	5

1.1.	Manufacturer’s Identification Data	5

1.2.	Attached documentation	5

1.3.	Aim and usage of the manual	5

1.4.	Manual update	5

1.5.	Consulting the manual	5

1.6.	Glossary	6

1.7.	Formulation of intellectual property rights	6

2.	Product description	7

2.1.	Controller	8

2.2.	Main functions of the Display Menu	10

2.2.1.	Keypad lock	14

2.3.	Foreseen use	15

2.3.1.	AHU main components	15

2.4.	Reasonably foreseen incorrect use	18

2.5.	I/O Map and components	19

3.	Functions	24

3.1.	ON/OFF	26

3.1.1.	Switch on	26

3.1.2.	Switch off	27

3.2.	Setpoint	28

3.3.	Working modes	29

3.3.1.	Hardware configuration of the AHU to change mode	29

3.3.2.	Procedure for changing mode	29

3.3.3.	Auto mode functioning	30

3.4.	Time periods and events	31

3.4.1.	Time bands	31

3.4.2.	Events	31

3.5.	Temperature regulation	32

3.5.1.	Boost	33

3.5.2.	Preheating regulator	33

3.5.3.	Temperature supply limits	33

3.6.	Humidity regulation	34

3.6.1.	Humidification regulation	34

3.6.2.	Dehumidification regulation	34

3.7.	Free-cooling and free-heating	36

3.8.	Heat recovery	37

3.8.1.	Heat Recovery with return temperature regulation	38

3.8.2.	Heat recovery with supply or cascade temperature regulation	40

3.9.	External dampers and recirculation dampers	41

3.10.	Cooling actuators	42

3.11.	Heating actuators	44

3.11.1.	Activated relays and number of steps	46

3.12.	Pumps	48

3.13.	Fans	49

3.13.1.	ON/OFF fans	50

3.13.2.	Modulating fans (with inverter)	50

3.13.3.	Backup fans	51

3.13.4.	Modbus fans	51

3.14.	Air quality: CO2 probe and VOC probe	53

3.15.	Constant flow regulation	54

3.16.	Constant pressure regulation	54

3.17.	Test output	54

4.	User Settings Menu	55

4.1.	A-Unit	56

4.2.	B-Clock & Events	58

4.3.	C-Languages	66

4.4.	D-Alarms	66

4.5.	E-User Settings	71

4.5.1.	E1-Setpoints	71

4.5.2.	E2-Work Hours	72

4.5.3.	E3-Data Logger	73

4.5.4.	E4-Web Server	74

4.5.5.	E5-Regulator	75

4.6.	F-I/O	76

4.7.	G-Password	79

4.8.	H-System	79

4.8.1.	S-Service	79

4.8.2.	O-I/O	97

4.8.3.	P-Serial ports	110

4.8.4.	Q-USB	111

4.8.5.	U-Unit Configuration	112

4.8.6.	W-Password	114

5.	Datalogger	115

6.	BMS Protocols	117

6.1.	Modbus RTU	117

6.2.	Modbus TCP	117

6.3.	Bacnet	117

7.	Web Server	119

8.	Alarms	125

8.1.	Fire alarm	127

8.2.	Air quality probe alarm	127

8.3.	Pressure probe alarm	127

8.4.	Air flow alarm	128

8.5.	Fan protection alarm	128

8.6.	Fan maintenance alarm	128

8.7.	Antifreeze alarm	129

9.	Disposal	130

10.	Safety Information	131

10.1.	Before You Begin	131

10.2.	Start-Up and Test	132

10.3.	Operations and Adjustments	132

11.	Wiring diagram	133

12.	Modbus Tables	134

12.1.	Modbus EEProm table	134

12.2.	Modbus Status table	165

Introduction

Manufacturer’s Identification Data

Eliwell Controls s.r.l.

Via dell’Industria, 15 • Z.I. Paludi

32010 Pieve d’Alpago (BL) ITALY

Telephone: +39 0437 986 111

Fax: +39 0437 989 066

www.eliwell.com

Attached documentation

The following documents are supplied along with this Manual.

| Document name | Document Code |
| --- | --- |
| User Guide FREE Advance | 9MA10265 (ENG) 9MA00265 (ITA) |

Table 1 - Attached documentation

Aim and usage of the manual

This Manual is an integral part of the product and is aimed at all those working on the product or who interact with those using the product itself. It aims to provide all the information needed to:

rapidly identify all the parts that make up the product

correct carry out all the operations foreseen during the stages of product use and management

guarantee the health safety and protection of staff working on the product in different roles

ensure the product works properly.

This Manual must be read carefully in its entirety before carrying out any operation on the product. If in doubt regarding the correct interpretation of the instruction found in it, contact the Manufacturer for further clarification.

This Manual needs to be carefully stored for the entire life cycle of the product and needs to stay with the product whenever it is transferred to other users, no matter what. It needs to be placed close to the product, in a place protected against atmospheric agents, heat, humidity, corrosive agents and be easily accessible as well as being familiar to all those who use it; it should not be damaged, pages removed or any of its content changed when it is being consulted.

Manual update

If, following constructive changes that lead to the product’s functions changing, the Manual needs to be updated, the Manufacturer will provide the Client with a review copy which will fully replace the previous one.

Consulting the manual

The information in the Manual is arranged as follows:

chapters,

sub-chapters,

paragraphs,

sub-paragraphs

and can easily be traced by consulting the Summary found at the start of this Manual.

In order to attract the user’s attention, in order to use the product properly and safely, the following convention is adopted in the Manual:

NOTE: The symbol is used to supply regulations or updates that are useful to the user.

Glossary

| AI | Acronym of Analogue Input. |
| --- | --- |
| AO | Acronym of Analogue Output. |
| HOT ACTUATOR | Component that heats the air. |
| COLD ACTUATOR | Component that cools the air. |
| BACNET (Building Automation and Control NETwork) | Communication protocol based on standard ASHRAE, ANSI and ISO 16484-5 for the building automation networks. |
| BMS (Building Management System) | Control / monitoring system of mechanical and electrical equipment installed in an area. |
| CO2 | Carbon dioxide. |
| DATALOGGER | Data recording device. |
| DI | Acronym of Digital Input. |
| DO | Acronym of Digital Output. |
| FILESYSTEM | Group of abstract data needed to handle the data. |
| P REGULATOR | Proportional regulator. |
| REGULATOR PI | Proportional-Integral action regulator. |
| PID REGULATOR | Proportional-Integral-Derivative Regulator. |
| SCADA | Acronym of Supervisory Control And Data Acquisition. |
| SUPERVISOR | Control/ monitoring system for mechanical and electrical equipment. |
| VOC | Volatile Organic Compound |

Table 2 - Glossary

Formulation of intellectual property rights

This publication is the exclusive property of the Manufacturer, who completely prohibits any reproduction or distribution if not expressly authorised by the Manufacturer himself.

Every care has been taken in the preparation of this Manual; however the Manufacturer and any person or company involved in its creation and writing cannot accept any liability arising from the use thereof. The Manufacturer reserves the right to make changes or improvements at any time without notice.

Product description

The product is an AVD controller programmed for application on Air Handling Units (AHU).

The programmed AVD controller can be one of the two described in the following table.

| AVD8400 | FREE Advance with display, 28 I/Os |
| --- | --- |
| AVD12600 | FREE Advance with display, 42 I/Os |

Table 3 – programmed AVD controller

The following can be applied to the programmed AVD controller:

up to two EVE4200 expansions

EVK1000 remote graphic terminal.

NOTE: For further information refer to 1.2 Documentation attached to pag. 5.

NOTE: In the continuation of this Manual:

the programmed AVD controller will be shown with the tern “controller”

the Air Handling Unit will be indicated with the term “AHU”.

Controller

The controller (Fig 1 - on pag. 8) has the following components:

keyboard (T);

display (D);

LED Sign (L);

connectors (S).

Fig 1 - Parts of the controller

The keyboard (T) has the following keys:

| Key | Symbol | Name | Description |
| --- | --- | --- | --- |
| 1 |  | UP | - Increase/modify a value - Select the next label |
| 2 |  | DOWN | - Decrease / modify a value - Select the previous label |
| 3 |  | RIGHT | - Move the cursor to the right (in edit mode) - Select the next item - View next page (in the parameter lists) |
| 4 |  | LEFT | - Move the cursor to the left (in edit mode) - Select the previous item - View previous page (in the parameter lists) - (kept pressed) exit the edit mode without saving - (kept pressed) exit the page/return to previous page |
| 5 |  | OK | - Carry out operation linked to a graphic key - Confirm (in edit mode) - Edit mode entry |

Table 4 - Keyboard

The display (D) allows the menus to be viewed and managed for AHU use. For the description of different menus please refer to 2.2 Menu Display on pag. 10. For further information refer to 1.2 Documentation attached to pag. 5.

There are four signal LEDs (L) each one which can assume one or more states to indicate information.

| LED | Colour | Resource | Meaning |
| --- | --- | --- | --- |
| P | Green | On | Powered controller |
|  |  | Off | Controller not-powered |
| A | Red | Off | No alarm |
|  |  | On | Has at least one alarm active; refer to 8 Alarms on pag. 125. |
|  |  | Flashing | Has at least one re-settable alarm and no alarm active (or manual re-armed); please refer to 8 Alarms on pag. 125. |
| B | Yellow | On | Writing on datalogger filesystem or data acquisition from USB port |
| C | Green | Off | AHU in OFF status |
|  |  | On | AHU in ON status |
|  |  | Flashing | AHU in stand-by status |

Table 5 - signal LED

NOTE: The AHU is in stand-by status if the AHU is on and no regulation is activated.

The connectors (S) permit the connection of:

power supply

input/output

communication ports

MicroSD.

For further information on containers please refer to 1.2 Documentation attached to pag. 5.

Main functions of the Display Menu

In order to select one of the icons on the display, press the UP, DOWN, RIGHT, LEFT keys on the keyboard.

The icon selected inverts its colour by going from black on a white background to white on a black background.

On pressing the OK key, access is given to the function relating to the icon selected.

On turning on, the controller sees the “Start splash” menu display.

From the “Start splash” menu to pressure on any key, the “Main” menu is accessed:

the “Main” menu shown below refers to the AHU case in the ON status

the “Main” menu shown below refers to the AHU case in the OFF status.

NOTE: The icons seen in the “Main” menu depend on the hardware configuration of the AHU (refer to 2.2.1.2 Hardware configuration of the AHU on pag. 17).

The “Main” menu parameters are given in the following table.

| Pag | Name | Device Type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | Unit_KbdOnOff | Boolean | 0 | — | — | — | On/Off status from keyboard |
| - - - | Unit_ForceOffAfterReboot | Boolean | 0 | — | — | — | Force Off keyboard after reboot |
| - - - | Unit_KbdMode_E2 | 0=Cool 1=Heat 2=Auto | 0 | 0 | 2 | — | Mode status from keyboard |
| - - - | Unit_KbdEco_E2 | 1=Economy 2=Comfort 3=Night | 2 | 1 | 3 | — | Comfort/Economy/Night status from keyboard |
| - - - | Unit_RegTempType | 0=Supply 1=Return Direct 2=Return Cascade | 1 | 0 | 2 | — | Temperature Regulation Probe |
| - - - | Unit_BMS_OnOff | Boolean | 1 | — | — | — | Unit On/Off via Modbus |
| - - - | Unit_Status | 0=OFF 1=STANDBY 2=RUN | — | 0 | 2 | — | Unit Status |
| - - - | T_RegulationProbe | Signed 16-bit | — | — | — | °C | Temperature Regulation Probe |
| - - - | T_CurrentSetpointByPar | Signed 16-bit | — | — | — | °C | Current Setpoint by parameter based on selected mode |
| - - - | RH_RegulationProbe | Signed 16-bit | — | — | — | %R.H. | Humidity Regulation Probe |
| - - - | AirQ_RegulationProbe | Signed 16-bit | — | — | — | %/ppm | Air Quality Regulation Probe |

Table 6 - Main

The icons foreseen for the “Main” menu are described in the following table.

| Icon | Description |
| --- | --- |
|  | “Action” access key: to modify the AHU status. |
|  | Functioning mode settings key (if activated). |
|  | Alarm presence viewing key. If active, “D1-Alarms” menu access key. |
|  | Profile change settings key: economy, night, comfort. |
|  | Temperature regulation viewing field: temperature taken with a supply probe or return probe, depending on the kind of regulation. |
|  | Weekly and/or annual events viewing field activated. |
|  | Viewing field made operative or boost activated. |
|  | Activation of viewing field (from left to right) of: regenerator, cooling actuators, heating actuators, fans, dehumidification. |
|  | SCADA control viewing field of at least one parameter. |
|  | Datalogger viewing field activated. |
|  | “Setpoint” menu access key to set the set point temperature. The setpoint temperature set can be viewed on the key. |
|  | “Setpoint” menu access key to set the humidity setpoint. The setpoint of the humidity set can be viewed on the key. |
|  | “Setpoint” menu access key to set the air quality setpoint. The set air quality setpoint can be viewed on the key. |

Table 7 - “Main” menu icons

Access to the “Action” page as described below is given  when the key is pressed.

NOTE: If the AHU is in stand-by status, the key allows you to:

turn the AHU to the OFF status using the Off key

turn the AHU to the ON status using the Override key.

The “Setpoint” menu referring to the temperature setpoint as described below, is accessed when the key is pressed.

|  |  | “Setpoint” menu |  |  |
| --- | --- | --- | --- | --- |

The “Setpoint” menu referring to the humidity setpoint as described below is accessed when the key is pressed.

|  |  | “Setpoint” menu |  |  |
| --- | --- | --- | --- | --- |

The “Setpoint” menu referring to the air quality setpoint as described below is accessed when the key is pressed.

|  |  | “Setpoint” menu |  |  |
| --- | --- | --- | --- | --- |

NOTE: Some pages above to the right show the progressive page number of the current page compared to the total number of pages (example: 1/2). In order to change the current page viewed, press the LEFT key or the RIGHT key.

Keep the UP key pressed for at least 2 seconds in order to access the “Events” menu.

|  |  | “Events” menu |  |  |
| --- | --- | --- | --- | --- |

Keep the RIGHT key pressed for at least 2 seconds in order to access the “User Settings Menu”.

NOTE: For further information on the User Settings Menu, see 4 User Settings Menu on pag. 55.

|  |  | “User Settings Menu” |  |  |
| --- | --- | --- | --- | --- |

Keep the LEFT key pressed for at least 2 seconds in order to access the “Start Splash” menu.

|  |  | “Start splash” menu |  |  |
| --- | --- | --- | --- | --- |

Keypad lock

If no key is pressed for more than an hour, the keypad automatically locks.

If the keypad is locked, the displays shows the message .

In order to remove the keypad lock, keep the UP key pressed; in this case, the keypad lock automatically re-activates after 5 minutes of being inactive.

In order to disable the keypad lock, keep the LEFT key pressed; in this case, the keypad lock automatically re-activates after 60 minutes of being inactive.

Foreseen use

The controller is destined to control the AHU for the regulation of environmental conditions.

AHU main components

The AHU (Fig 2 - on pag. 16) consists of the components given in the following table.

NOTE: The number, type and conformation of the components illustrated in Fig 2 - on pag. 16 and shown in the following table, are purely indicative.

| 1 | External suction damper |
| --- | --- |
| 2 | Expulsion damper |
| 3 | Return filter |
| 4 | Supply filter |
| / | Fan dampers |
| 5 | Recirculation dampers |
| 6 | Heat Recovery unit |
| 7 | Recovery unit damper |
| 8 | Pre-heating actuator |
| 9 | Heating actuator |
| 10 | Cooling actuator |
| 11 | Post-heating actuator |
| 12 | Humidifier |
| 13 | Supply fans, powered by the supply engine |
| 14 | Return fans, powered by the return engine |
| 15 | Return probe |
| 16 | Supply probe |
| 17 | External Probe |
| 18 | Expulsion probe |
| / | Antifreeze probe, relating to the heating and cooling actuator |
| / | CO2 probe |
| / | VOC probe |
| / | Pre-heating probe |
| / | Saturation probe |
| / | 0-10 V pressure probe |

Table 8 - Main components of the AHU

NOTE: In Fig 2 - on pag. 16 the recovery unit illustrated has cross flow with the bypass damper.

NOTE: The temperature probes are NTC type.

Fig 2 - Main components of the AHU

AHU Conventions

In the continuation of this Manual, the conventions shown in the following table are adopted.

| Main heating/cooling actuators | - Heating actuator - cooling actuator |
| --- | --- |
| External dampers | - Expulsion damper - external suction damper |
| Air quality probes | - CO2 probe - VOC probe |
| Backup fans | - Backup supply fan - backup return fan |
| Supply fans | - Main supply fan - backup supply fan |
| Main fans | - Main supply fan - main return fan |
| Return fans | - Main return fan - backup return fan |
| Modbus fans | - EBM fan - ATV fan - Ziehl fan |

Table 9 – Conventions

AHU hardware configuration

The hardware configurations of the AHU are described in the following table.

| Component | Feature | Hardware configuration |
| --- | --- | --- |
| Fans | Number of fans | Supply fan; supply fan + return fan. |
|  | Fan type | ON/OFF; modulating; ON/OFF with backup; modulating with backup; ATV; ATV with backup; EBM; EBM with backup; Ziehl; Ziehl with backup. |
|  | Regulation of fans | To constant speed; quality air; constant pressure; constant flow. |
|  | Fan alarm (non Modbus) | Heat; heat + ON/OFF flow switch. |
|  | Fan alarm (Modbus) | None; ON/OFF flow switch. |
| Actuators | Pre-heating type (1) | None; modulating valve; modulating valve + pump; ON/OFF step electric heater; electric heater 0-10 V + step; PWM electric heater + step. |
|  | Heating/Cooling configuration | None; cooling actuator; heating actuator; cooling + heating actuator; multi-purpose actuator. |
|  | Cooling actuator (2) | Modulating valve; modulating valve + pump; condensing unit up to 4 steps or 4 parallel units. |
|  | Heating actuator (2) | Modulating valve; modulating valve + pump; condensing unit up to 4 steps or 4 parallel units; ON/OFF step electric heating element; electric heating element 0-10 V + step; PWM electric heating element + step. |
|  | Multi-purpose actuator (3) | Modulating; modulating + pump; condensing unit up to 4 steps or 4 parallel units. |
|  | Post-heating type (1) – (4) | None; modulating valve; modulating valve + pump; ON/OFF step electric heater; electric heater 0-10 V + step; PWM electric heater + step. |
|  | Antifreeze probe type | None; ON/OFF; NTC. |
| Recovery unit | Recovery unit (5) | None; ON/OFF overlapping flows with by-pass damper; rotary wheel ON/OFF; actuator ON/OFF; overlapping flows proportional with by-pass damper; rotary wheel proportional; actuator proportional. |
|  | Defrost recovery unit type | None; supply far; resistance. |
| Humidifier | Humidifier activation | None; ON/OFF; proportional. |
| Dehumidification | Dehumidification type | None; standard; dew point; standard + winter; dew point + winter. |
| Dampers | External dampers type | None; ON/OFF; ON/OFF + 0-10 V mix |
|  | Fan dampers type | None; supply fan; return ventilators; supply fan + return fan. |
| Air quality probes | Air quality probe type | None; CO2; VOC; CO2 + VOC. |
| Mixing chamber between external dampers and pre-heating actuator | Activation of mixing chamber (6) | None; active. |

Table 10 - Hardware configuration of the AHU

NOTE (1): The pre-heating and post-heating actuator in modulating valve configuration are managed by an analogical output 0-10 V for the request modulation.

NOTE (2): The cooling and heating actuator in modulating valve configuration are managed by an analogical output 0-10 V for the request modulation.

NOTE (3): The multi-purpose actuator is an actuator able to cool or heat based on the current unit mode.

NOTE (4): The post-heating actuator is principally used:

in heating, to dehumidify the air

in cooling, as an integration to the actuator for heating the air if the action of the heating actuator is insufficient.

NOTE (5): The functioning logic of the different types of recovery unit is the same, but in the case of the overlapping flow recovery unit with by-pass damper, the polarity is inverted compared to the polarity of the other two kinds of recovery unit.

NOTE (6): The mixing chamber activation allows you to close the external dampers when the pre-heating actuator is turned on.

Reasonably foreseen incorrect use

Any use of the system that differs from what is indicated in 2.3 Foreseen use on pag. 15 and according to the indications given in this Manual should be considered IMPROPER USE and the Manufacturer declines all responsibility in relation to any damage caused to people or things and will render the product warrant null and void.

For additional Safety Information, see what is reported in 10. Safety Information.

I/O Map and components

The controller software defines the I/O requested in function of the components and the hardware configuration of the AHU. The I/O Map and components is described in the following tables, respectively for:

dampers

actuators

engines

probes and other signals.

NOTE: For the I/O consult the documentation attached.

NOTE: For the hardware configuration see 2.2.1.2 Hardware configuration of the AHU on pag. 17.

In any case, all the I/O can be manually allocated by the controller (see 4.8.2 O-I/O on pag. 96).

NOTE: It is possible not to allocate an input or output even if the hardware configuration foresees its allocation.

The I/O requested depending on the hardware configuration relating to the dampers is shown in the following table.

NOTE: In the column to the far right an “X” indicates that the component is always present.

| Component | Hardware configuration | DI | AI (NTC) | AI (UNIV) | DO | AO | Always present |
| --- | --- | --- | --- | --- | --- | --- | --- |
| External dampers | ON/OFF | — | — | — | 1 | — | — |
|  | Modulating + Recirculation | — | — | — | — | 1 | — |
| By-pass damper | Recovery unit: cross flow with the bypass damper | — | — | — | 1 | 1 | — |
| Fan dampers | Fan supply dampers; Fan return dampers Fan supply and return dampers | — | — | — | 1…4 | — | — |

Table 11 - Map I/O and components - dampers

The I/O requested depending on the hardware configuration relating to the actuators is shown in the following table.

NOTE: In the column to the far right an “X” indicates that the component is always present.

| Component | Hardware configuration | DI | AI (NTC) | AI (UNIV) | DO | AO | Always present |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Recovery unit | Recovery unit type: rotary wheel | 1 | — | — | 1 | 1 | — |
| Pre-heating actuator | Pre-heating actuator type: ON/OFF step electric heater | 1 | — | — | 1 | — | — |
|  | Pre-heating actuator type: ON/OFF step electric heater + modulating | 1 | — | — | 1 | 1 | — |
|  | Pre-heating actuator type: modulating valve | — | — | — | 1 | 1 | — |
|  | Pre-heating actuator type: modulating valve + pump | — | — | — | — | 1 | — |
| Cooling actuator | Cooling actuator type: up to 4 steps condensing unit or 4 parallel units | 1…4 | — | — | 1…4 | 1…4 | — |
|  | Cooling actuator type: modulating valve | — | — | — | — | 1 | — |
|  | Cooling actuator type: modulating valve + pump | — | — | — | 1 | 1 | — |
| Heating actuator | Heating actuator type: up to 4 steps condensing unit or 4 parallel units | 1…4 | — | — | 1…4 | 1…4 | — |
|  | Heating actuator type: ON/OFF step electric heater | 1 | — | — | 1…3 | — | — |
|  | Heating actuator type: ON/OFF step + modulating electric heater | 1 | — | — | 1…3 | 1 | — |
|  | Heating actuator type: modulating valve | — | — | — | — | 1 | — |
|  | Heating actuator type: modulating valve + pump | — | — | — | 1 | 1 | — |
| Multi-purpose actuator | Multi-purpose actuator type: up to 4 steps condensing unit or 4 parallel units | 1…4 | — | — | 1…4 | 1…4 | — |
|  | Heating actuator type: modulating valve | — | — | — | — | 1 | — |
|  | Multi-purpose actuator type: modulating valve + pump | — | — | — | 1 | 1 | — |
| Post-heating actuator | Post-heating actuator type: modulating valve | — | — | — | — | 1 | — |
|  | Post-heating actuator type: modulating valve + pump | — | — | — | 1 | 1 | — |
|  | Post-heating actuator type: ON/OFF step electric heater | 1 | — | — | 1…3 | 1 | — |
| Humidifier | Humidifier activation: ON/OFF | 1 | — | — | 1 | — | — |
|  | Humidifier activation: proportional | 1 | — | — | 1 | 1 | — |

Table 12 - Map I/O and components - actuators

The I/O requested depending on the hardware configuration related to ventilation is shown in the following table.

NOTE: In the column to the far right an “X” indicates that the component is always present.

| Component (if fans are not Modbus) | Hardware configuration | DI | AI (NTC) | AI (UNIV) | DO | AO | Always present |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Supply fan | Fan alarm: Thermal Switch | 1 or 2 (if backup supply fan active) | — | — | — | — | — |
|  | Fan alarm: Thermal Switch + Flowswitch | 2 or 4 (if backup supply fan active) |  |  |  |  |  |
|  | Fan number: supply fan | — | — | — | 1 or 2 (if backup supply fan active) | — | — |
|  | Fan type: modulating | — | — | — | — | 1 | — |
| Return fan | Fan alarm: Thermal Switch | 1 or 2 (if backup return fan active) | — | — | — | — | — |
|  | Fan alarm: Thermal Switch + Flowswitch | 2 or 4 (if backup supply fan active) |  |  |  |  |  |
|  | Number of fans; supply fan + return fan | — | — | — | 1 or 2 (if backup return fan active) | — | — |
|  | Fan type: modulating | — | — | — | — | 1 | — |

Table 13 - Map I/O and components - fans

The I/O requested depending on the hardware configuration relating to probes and other signals is shown in the following table.

NOTE: In the column to the far right an “X” indicates that the component is always present.

| Component | Hardware configuration | DI | AI (NTC) | AI (UNIV) | DO | AO | Always present |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature Return probe |  | — | 1 | — | — | — | X |
| Humidity Return probe | Humidifier or Dehumidification enabled | — | — | 1 | — | — | — |
| Temperature Supply probe |  | — | 1 | — | — | — | X |
| Humidifty Supply probe | Humidifier enabled | — | — | 1 | — | — | — |
| External Probe | — | — | 1 | — | — | — | X |
| Expulsion probe | Recovery unit type: cross flow with bypass damper; rotary wheel | — | 1 | — | — | — | — |
| Pre-heating probe | Pre-heating actuator type: active (if none, it works as primary heating) | — | 1 | — | — | — | — |
| Saturation probe | Dehumidification type: dew point | — | 1 | — | — | — | — |
| Air quality probe: CO2 probe (1) | Fan regulation: air quality or Air quality with CO2 or CO2+VOC | — | — | 1 | — | — | — |
| Air quality probe: VOC probe (1) | Fan regulation: air quality or Air quality with VOC or CO2+VOC | — | — | 1 | — | — | — |
| 0-10 V pressure probe (2) | Fan regulation: constant flow; constant pressure | — | — | 1 | — | — | — |
| Antifreeze probe for modulating valve | Antifreeze probe type: ON/OFF | 1 | — | — | — | — | — |
| Antifreeze probe for modulating valve | Antifreeze probe type: NTC | — | 1 | — | — | — | — |
| Filter pressure switch | — | From 0 to 4 | — | — | — | — | — |
| Fan alarm: flow switch ON/OFF | Flow Switch Alarm Enabled | Number of fans: 1…4 | — | — | — | — | — |
| Remote input ON / OFF | — | 1 | — | — | — | — | X |
| Fire alarm input | — | 1 | — | — | — | — | X |
| Door dip switch input | Door Enabled | 1 | — | — | — | — |  |
| Summer/winter mode change input | Mode Input Enabled | 1 | — | — | — | — |  |
| Output for AHU ON/OFF status | — | — | — | — | 1 | — | X |
| Output for summer/winter mode | Mode Output Enabled | — | — | — | 1 | — |  |
| General alarm output (exchange contact) | — | — | — | — | 1 | — | X |

Table 14 - Map I/O and components - probes and other signals

NOTE: (1) There needs to be at least one of the following - CO2 probe or VOC probe.

NOTE: (2) There can be one or two probes.

Functions

The list of the functions relating to the AHU managed by the controller are given in the following table.

| Functions | Reference in this Manual |
| --- | --- |
| ON/OFF | 3.1 ON/OFF on pag. 25 |
| Mode Change | 3.3 Working modes on on pag. 29 |
| Setpoint | 3.2 Setpoint on pag. 28 |
| Time periods and events | 3.4 Time periods and events on pag. 31 |
| Temperature regulation | 3.5Temperature regulationon on pag. 32 |
| Humidity regulation | 3.6 Humidity regulationon on pag. 34 |
| Free-cooling and free-heating | 3.7 Free-cooling and free-heating on pag. 36 |
| Heat recovery | 3.8 Heat recoveryon on pag. 37 |
| External dampers and recirculation dampers | 3.9 External dampers and recirculation dampers on pag. 41 |
| Cooling actuators | 3.10 Cooling actuatorson on pag. 42 |
| Heating actuators | 3.11 Heating actuatorson on pag. 44 |
| Pumps | 3.12 Pumps on pag. 48 |
| Fans | 3.13 Fanson on pag. 49 |
| Air quality: CO2 probe and VOC probe | 3.14 Air quality: CO2 probe and VOC probe on pag. 53 |
| Constant flow | 3.15 Constant flow regulationon on pag. 54 |
| Constant pressure | 3.16 Constant pressure regulationon on pag. 54 |
| Test output | 3.17 Test outputon on pag. 54 |

Table 15 - Functions relating to the AHU

NOTE: For further information on the parameters given at a later date in the chapter see 2.2 Menu Display on pag. 10 and 4 User Settings Menu on pag. 55.

Conventions for function graphics

At a later date in this Manual, for the illustrative graphs of certain functions, the conventions given in the following table are adopted.

| Actuator Request | Actuator request (regulated) |
| --- | --- |
| Cooler | Cold actuator |
| Cooling | Cooling |
| Heater | Heating actuator |
| Heating | Heating |
| Hysteresis | Hysteresis |
| Main probe | Main probe, relating to the main temperature regulator |
| PI request | PI regulator request (that regulates the actuator) |
| PI Input | PI regulator input |
| PI Output | PI regulator Output |
| Post-Heater | Post-heating actuator |
| Recovery | Recovery unit |
| Return | Return probe |
| Summer mode |  |
| Supply | Supply probe |
| Text | External temperature |
| Tret | Return temperature |
| Winter mode | Winter mode |
| Electric heater | Electrical heater |
| Damper | External damper |

Table 16 - Conventions for function graphics

ON/OFF

Switch on

The AHU can be switched on in one of the following ways:

Standard startup

Startup with boost function, where the dampers are initially kept closed and heat actuators forced to maximum power in order to reduce the time needed to reach the setpoint.

Standard startup is described more in details in chapter 3.1.1.1

Startup with boost function is described more in details in chapter 3.1.1.2

Switch on can be managed via BMS through Modbus or Bacnet protocol (default status is ON).

The AHU is ON if the ON status is ON simultaneously confirmed:

on digital input

on controller display

on BMS

Standard Startup

During the standard startup (Fig 3 - on pag. 26), the controller performs the following operations:

checks the absence of alarms

brings the external dampers to minimum opening

turns on the supply and return fan

activates the actuator regulations.

Fig 3 - Passage to ON status without making operative

Startup with boost function

During the startup with boost function (Fig 4 - on pag. 26), the controller performs the following operations:

- checks the absence of alarms

turns on the supply and return fan

activates the heating actuators at maximum power.

on reaching the setpoint or time-out, the external dampers go to minimum opening.

activates the actuator regulations

Fig 4 - Passage to ON status with making operative process

In the case of:

free-cooling,

free-heating

the boost function is disabled.

During the startup with boost phase the Temperature supply limit regulator is enabled regardless the related enabled parameter.

Switch off

Switching off (Fig 5 - on pag. 27) consists of the passage of the AHU to OFF status with the controller who performs the following operations in order:

- disables the regulations of the actuators

if necessary, starts the post-ventilation (if the electrical heating elements or the condensing units were on)

turns off the supply fan and return fan

closes the external dampers.

Fig 5 - Switching off

NOTE: The digital input OFF status has maximum priority.

The OFF/ON status of the BMS serial port has greater priority compared to the OFF/ON status:

of controller;

via time periods and events (see 3.4 Time periods and events on pag. 31).

The AHU is OFF if the OFF status is confirmed in at least one of the following cases:

on digital input

on controller

on BMS serial port

on time bands.

Setpoint

It is possible to define three setpoints, one for each of the three functioning modes:

summer setpoint

winter setpoint

auto setpoint

NOTE: The three setpoints correspond to three functioning modes described in 3.3 Functioning modes on pag. 29.

Each setpoint can be combined, both in temperature and in humidity, with one of the following profiles:

comfort,

economy,

night.

The night profile is characterised by:

the same setpoint as the economy profile

fan speed reduced to a minimum.

The characteristics of the economy and comfort profiles depending on the setpoints are described in the table below.

| Setpoint | Characteristic of the economy and comfort profiles |
| --- | --- |
| Summer | setpoint with economy profile (SP_T_CoolEco_E2 parameter) > setpoint with comfort profile (SP_T_Cool_E2 profile) |
| Winter | setpoint with economy profile (SP_T_HeatEco_E2 parameter) < setpoint with comfort profile (SP_T_Heat_E2 profile) |
| Auto | setpoint with economy profile = setpoint with comfort profile ± offset (DIFF_T_AutoEco parameter) |

Table 17 - Specifications of the economy and comfort profiles depending on the setpoints

NOTE: The DIFF_T_AutoEco parameter is defined even as a neutral zone.

NOTE: The SP_T_Auto_E2 parameter is the parameter auto setpoint, the T_RegulationProbe parameter is the current setpoint due to economy/comfort, Bacnet, auto/summer/winter.

Working modes

The controller approves three functioning modes for the AHU:

winter

summer

auto.

NOTE: In certain hardware configurations, the AHU (see 3.3.1 Hardware configuration of the AHU to achieve mode change on pag. 29), the summer/winter change mode is approved, that is, the move form summer mode to winter mode or vice versa. To see how to carry out this change of mode, see 3.3.2 Procedure for changing mode pag. 29.

In winter mode, the hot actuators are activated to heat the air and if necessary the recovery unit to limit an excessive rise in temperature.

In summer mode, the cooling actuators are activated to cool the air and if necessary the recovery unit to limit an excessive reduction in temperature.

NOTE: In summer mode, it is not possible to turn on the electrical heating elements.

In auto mode (see 3.3.3 Functioning of the auto mode on pag. 30) there is an automatic move of the AHU from cooling to heating (and vice versa) depending on the temperature of the regulation and temperature setpoint; it is, therefore, possible to activate both the hot and cooling actuators.

Hardware configuration of the AHU to change mode

The summer/winter change mode is not allowed if there is not recovery unit and with AHU configured with components that produce only heat or only cold. If there is just the recovery unit, it is still possible to achieve the cooling and heating.

NOTE: The summer/winter mode change is forced in auto mode in the case of AHU configuration where:

only the fans are on, or

only the recover unit is on.

The move from summer mode to winter mode (heating):

is disabled if there is a request for dehumidification as the dehumidification impedes heating:

it is possible if there is a request for cooling of the temperature regulator has been completed.

The move from winter mode to summer mode (cooling) is possible if the request for heating of the temperature regulator has been completed.

Procedure for changing mode

The summer/winter mode change can take place by:

digital input

keypad, with summer/winter mode change set automatically by default

BMS serial port.

NOTE: If activated, the digital input summer /winter mode change has priority over the keypad selection; in this case, auto mode is not approved.

Auto mode functioning

In auto mode, the change from cooling to heating (and vice versa) depends on:

the heating/cooling request from the main temperature regulator

external temperature:

in the case of an external temperature that is lower than the SP_T_FORCEWINTER parameter, there is heating straining (1 - Fig 6 -on pag. 30);

in the case of an external temperature that is higher than the SP_T_FORCESUMMER parameter, there is cooling straining (2 - Fig 6 -on pag. 30);

in the case of an external temperature between the two previous parameters, depending on the kind of temperature regulation 3.5 Temperature regulation on pag. 32) the move from cooling to heating (and vice versa) is handled via a return probe or a supply probe (3 - Fig 6 -on pag. 30).

Fig 6 - - Auto mode functioning

In Fig 6 -on pag. 30 the reference parameters are shown using tags (capital letters), the reference parameters for the auto mode functioning. See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | SP_T_FORCEWINTER |
| B | SP_T_FORCESUMMER |
| C | DIFF_T_AutoChangeMode |
| D | SP_T_Auto_E2 (parameter setpoint) T_CurrentSetpointByPar (current setpoint) |
| E | T_RegulationProbe |

Table 18 - Auto mode functioning

Time periods and events

The AHU can assume the ON status (active regulators) or OFF status (disabled regulators) depending on the time periods or events. The need for an event takes priority over the time periods.

NOTE: It is possible to force the stand-by status from the keypad.

NOTE: The time period function and events support the clock changing.

Time bands

For each day of the week it is possible to choose between four programmes:

P1

P2

P3

P4

irrespective of the mode set (summer, winter, auto).

In the P1 program and P2 program, it is possible to set four times, where one of the following status-profiles can be associated to each time:

OFF

ON with comfort profile

ON with economy profile

ON with night profile.

If the P3 program is active, the AHU is in the ON status all day in comfort profile.

If the P4 program is active, the AHU is in the OFF status all day.

Events

It is possible to active up to 15 Event. Each event is characterised by:

a start day

an end day

an associated profile-status.

Temperature regulation

NOTE: For the setpoints see 3.2 Setpoint on pag. 28.

When regulating the temperature, the recovery unit and various hot actuators and cooling actuators are turned on in sequence.

There are three kinds of temperature regulation:

supply temperature regulation, with regulation on the supply probe

return temperature regulation, with regulation on the return probe and limit supplied by the supply probe

temperature regulation in cascade, with regulation on the supply probe compared to the return regulator.

In the three kinds of temperature regulation, the supply probe is always present.

NOTE: It is possible to configure the requested allocation to various regulators of the actuators.

The Fig 7 - on pag. 32 describes the supply or in cascade temperature regulation case; in the case of return temperature, the recovery unit regulator is not present because the recovery unit is managed by a separate regulator.

The temperature regulator activates alternatively:

cooling, where the request on the actuators is given in (1 - Fig 7 - on pag. 32);

heating, where the request on the actuators is given in (2 - Fig 7 - on pag. 32).

NOTE: Depending on the hardware configuration of the AHU, in Fig 7 - on pag. 32 the following regulators may not be present:

recovery unit regulator

regulator of the post-heating actuator.

Fig 7 - Temperature regulation

In Fig 7 - on pag. 32 the reference parameters are shown using tags (capital letters), the reference parameters for the temperature regulation. See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | RecoveryPower |
| B | PostPower |

Table 19 - Temperature regulation

Boost

The boost functioning allows you to make it operative from the keypad, similar to what is foreseen for turning on (see 3.1.1.2) at any time following the stand-by status.

Preheating regulator

If activated, the preheating regulator is a PI operating regulator exclusively in heating to keep the temperature at the preheating setpoint.

The preheating regulator is disabled during the making operative process when turning on 3.1.1.2 Move to ON status with the making operative process on pag. 26) or the boost (see 3.5.1 Boost on pag. 33).

Temperature supply limits

If activated, the temperature supply limits are limitations on the regulation of return temperature:

in cooling, it is a limitation lower than the reduction of supply air temperature

in cooling, it is a limitation greater than the increase in supply air temperature.

NOTE: In the case of regulation in cascade, the limitation is not necessary.

With the preheating regulator (see 3.5.2 Preheating regulator on pag. 33), the upper limitation on the increase in temperature of the supply air while heating is done with the preheating probe (if present).

With a dehumidifying request (see 3.6.2 Dehumidifying regulation on pag. 34), there is a limitation lower than the reduction in supply air temperature during cooling.

Humidity regulation

The air humidification is created via the humidifier, the dehumidification of the air is not done by a specific physical actuator but via the combined action of two actuators:

cooling actuator

post-heating actuator.

Humidification regulation

During the regulation of the supply air humidification, the variation in the supply air temperature itself, is negligible. Up until the humidity setpoint is reached, the controller:

activates the production of steam

modulates the amount of steam produced via 0-10 V signal.

The humidifier regulator is proportional or ON/OFF, with:

return humidity probe fitted with hysterisis

supply humidity probe used as limit probe.

Dehumidification regulation

Standard dehumidification

The PI regulation acts on the cooling actuator to obtain the required humidity setpoint. The regulation is carried out on the level of humidity acquired by the return humidity probe.

When a dehumidification request is made, as a result of a return air humidity that is too high, the cooling actuator is activated that equates to a return regulation in cooling.

During dehumidification, the post-heating actuator compulsorily active, compensates the cooling. The post-heating actuator regulates the supply air temperature with the main temperature setpoint.

NOTE: The cooling actuator is driven by the most binding of:

the dehumidification request

the cooling request.

The post-heating regulator is:

activated in the case of a reduction in the regulation temperature (supply/return) to a level lower than the difference between the post-heating setpoint and post-heating offset

disable in the case of reaching the post-heating setpoint.

NOTE: The post-heating actuator can operate:

both as integration of the heating actuator action and as compensation for the reduction in temperature caused by the dehumidification (if present).

Dew point

The activation of the dehumidification regulator to the dew point is the ON/OFF type with differential that can be set via Dehum_Req_Diff parameter and is operated by the return humidity probe.

The regulator uses the saturation temperature probe positioned after the cooling actuator.

The controller calculates the dew point starting from the return temperature setpoint and the return humidity setpoint. The dew point represents the setpoint that the cooling actuator needs to maintain comparing it to the value acquired from the saturation temperature probe.

Dehumidification with external air (or winter)

This is a dehumidification active in cooling.

NOTE: In winter more, the hot actuators are enabled.

In order to start the dehumidification with external air, it is essential to:

activate the Manufacture dehumidification and service

activate the external humidity probe

activate the external temperature probe

activate the external dampers in ON/OFF configuration + 0-10V mix.

NOTE: The dehumidification with external air is only active if enabled by the Manufacturer via cfgDeHumidifier parameter. Once enabled by the Manufacturer, this dehumidification can be managed by the service via the Dehum_WinterEn enabling parameter.

The regulation is ON/OFF with differential that can be set. If the regulator requests dehumidification, if the sum of the external specific humidity and the differential is lower than the internal specific humidity:

the external dampers are fully opened

if necessary, the post-heating actuator is enabled.

Free-cooling and free-heating

The free-cooling is:

disabled in the case of an external temperature that is excessively reduced

active in the case where the following conditions are simultaneously met:

Treg - Text ≥ FreeCHDiff

Treg > T_CurrentSetpointByPar

Text > FreeCHMinExtTemp.

NOTE: Treg indicates the temperature of the regulation probe, Text indicates the external temperature.

NOTE: The default level:

of the FreeCHDiff parameter equates to 5 °C

of the FreeCHMinExtTemp parameter equates to 12 °C.

NOTE: The T_CurrentSetpointByPar parameter is the current setpoint of free-cooling relative to the regulation of temperature or, in the case of temperature regulation in cascade, the setpoint of the supply regulator.

The free-heating is:

disabled in the case of an external temperature that is excessively high

active in the case where the following conditions are simultaneously met:

Text - Treg ≥ FreeCHDiff

Treg < T_CurrentSetpointByPar.

NOTE: The T_CurrentSetpointByPar parameter is the current setpoint of free-heating relative to the regulation of temperature or, in the case of temperature regulation in cascade, the setpoint of the supply regulator.

In the case of the activation of the free-cooling or free-heating, the actuators are stopped for a maximum set time to allow the AHU to meet the setpoint (of free-cooling or free-heating) requested without energy consumption. If this setpoint is not reached within this maximum time, the actuators are reset.

The functioning of the external dampers according to the value of cfgFreeHeating parameter and the cfgFreeCooling parameter is described in the table below.

| Value of the parameter | External damper regulator | External dampers |
| --- | --- | --- |
| cfgFreeHeating = 1 | P regulator | The external dampers are opened in proportion to the difference between the relative setpoint and regulation temperature |
| cfgFreeCooling = 1 | P regulator | The external dampers are opened in proportion to the difference between the regulation temperature and external temperature |
| cfgFreeHeating = 2 | Recovery unit regulator | The external dampers are controlled in parallel with the recovery unit |
| cfgFreeCooling = 2 | Recovery unit regulator | The external dampers are controlled in parallel with the recovery unit |

Table 20 - Functioning of the external dampers according to the cfgFreeHeating and cfgFreeCooling parameters

In the case of overlapping flow recovery units with by-pass dampers, the relative damper allows for external air to be taken and send directly into the atmosphere, if conditions are favourable (free-cooling or free-heating).

Heat recovery

If active, the recover unit can be convenient from an energetic heat recovery point of view. The heat recovery is a heat exchanger, activated by the recovery unit, between the supply air and expulsion air:

in order to pre-heat the supply air, if the external temperature is excessively reduced

in order to pre-cool the supply air, if the external temperature is excessively high.

The sending and stopping conditions of the heat recovery are described in the following table.

| Regulation | Heating/Cooling | Start up condition of the heat recovery | Stop condition of the heat recovery |
| --- | --- | --- | --- |
| Return/Cascade | Heating | Text ≤ Trip | Text > Trip + RecoveryDiff_Band |
| Return/Cascade | Cooling | Text ≥ Trip | Text + RecoveryDiff_Band < Trip |
| Supply | Heating | Text ≤ setpoint and If Trip allocated: Text ≤ Trip | Text > setpoint + RecoveryDiff_Band and If Trip allocated: Text > Trip + RecoveryDiff_Band |
| Supply | Cooling | Text ≥ setpoint and If Trip allocated: Text ≥ Trip | Text + RecoveryDiff_Band < setpoint and If Trip allocated: Text + RecoveryDiff_Band < Trip |

Table 21 - Stop and start conditions of the heat recovery

NOTE: The default level of the RecoveryDiff_Band parameter equates to 1.5 °C.

Defrost (or de-icer) recovery unit

The defrosting (or de-icing) of the recovery unit is a function that foresees the formation of ice on the recovery unit, that can occur following the heat exchange between the air flows.

In order to de-frost the recovery unit, it is possible, alternatively:

to reduce the supply fan with inverter speed

activate the pre-heating actuator and close off the modulating external damper, if the following conditions are simultaneously met:

the pre-heating actuator is active

the cfgMixChamberBeforePreHeat parameter is enabled.

NOTE: The recovery unit defrosting via reduction in speed of the supply fan takes place 240 seconds after turning on the supply fan.

Depending on the kind of recovery unit, when defrosting, the recovery unit functions as described in the table below.

| Recovery unit type | Function of the recovery unit during the recovery unit defrosting |
| --- | --- |
| Cross flow with bypass damper | The recovery unit by-pass damper remains closed |
| Heat Exchanger | The recovery pump continues to function |
| Rotary wheel | The recovery unit wheel continues to function |

Table 22 - Function of the recovery unit during the recovery unit defrosting

Heat Recovery with return temperature regulation

The recovery unit operates separately from the request of the temperature regulator and the supply probe is used as a limit probe.

NOTE: The graphs shown in Fig 8 - on pag. 39 refer to the rotary wheel recovery unit. In the case overlapping flow recovery unit with the by-pass damper, the relative graphs are symmetrical.

NOTE: In Fig 8 - on pag. 39, the following disparities represent the extent of hysterisis relating to the recovery unit with return control in the case of heating:

Text less than or equal to Tret

Text greater than Tret + RecoveryDiff_Band.

NOTE: In Fig 8 - on pag. 39, the following disparities represent the extent of hysterisis relating to the recovery unit with return control in the case of cooling:

Text greater than or equal to Tret

Text + RecoveryDiff_Band less than Tret.

In Fig 8 - on pag. 39 the reference parameters are shown using tags (capital letters), the reference parameters for the recover of heat with return control. See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | RecoveryDiff_Band |
| B | T_CurrentSetpointByPar + RecoveryDeadZone |
| C | T_CurrentSetpointByPar - RecoveryDeadZone |

Table 23 - Recovery of heat with return regulation

With reference to Fig 8 - on pag. 39, for example, the function of the recovery regulation with cooling and Text + RecoveryDiff_Band < Tret is described in the following table.

| Recovery temperature level (Tret) | Cooling mode |
| --- | --- |
| Very high | The recovery unit is disabled and the air in the AHU is cooled by taking air from outside, as it is at a low temperature |
| Lower than the cooling setpoint | The recovery unit is activated and air is not taken from outside because the temperature is too low |

Table 24 - Functioning of the recovery regulation with cooling and Text + RecoveryDiff_Band < Tret

Fig 8 - Recovery of heat with return regulation

Heat recovery with supply or cascade temperature regulation

The heat recovery unit is activated by the temperature regulator as show in Fig 7 - on pag. 32. In this kind of regulation, the recovery unit regulator is always the first regulator to intervene; at a later date, the heating/cooling actuators are also activated.

NOTE: In the event that the start up condition of the heat recovery are unsatisfactory, the request for heating/cooling of the regulator is met only by the heating/cooling actuators. In reference to Fig 9 - on pag. 40, the recovery unit regulator is managed via an analogical output.

Fig 9 - Recovery of heat with supply regulation or in cascade

In supply In Fig 9 - on pag. 40 the reference parameters are shown using tags (capital letters), the reference parameters for the recover of heat with supply regulation or in cascade. See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | RecoveryPower |

Table 25 - Recovery of heat with supply regulation or in cascade

External dampers and recirculation dampers

NOTE: When functioning normally, the external dampers have a minimum opening to guarantee a change of air in the AHU.

The external dampers are piloted by the same output as the controller. They are completely closed if one of the following conditions arises:

AHU in OFF status;

the making operative process in course (to minimise the time it takes to reach the setpoint)

antifreeze alarm active (to heat via anti-freeze activation, if there is a pre-heating actuator)

recovery unit defrost active (see 3.8 Heat recovery on pag. 37).

| Analogical output relating to the dampers | External dampers | Recirculation dampers |
| --- | --- | --- |
| 0% | Closed | Open |
| 100% | Open | Closed |

Table 26 - Functioning logic of the external dampers and recirculation dampers

The relations between the AHU condition and opening of the external dampers is described in the following table.

| AHU conditions | Opening of the external dampers |
| --- | --- |
| Normal | Minimum opening (default equal to 30%) |
| Free-cooling/free-heating procedure | Proportional opening of the external dampers (cfgFreeCooling or cfgFreeHeating parameter equates to 1) |
| CO2/VOC regulation | Modulation between minimum opening (default equal to 30%) and maximum opening (100%) |
| Regulation linked to heat recovery in free-cooling/free-heating procedure | Proportional opening of the external dampers (cfgFreeCooling or cfgFreeHeating parameter equates to 2) |

Table 27 - AHU condition and opening of the external dampers

The CO2 regulation is achieved on the value acquired by the CO2 probe, the VOC regulation is achieved on the value acquired by the VOC probe. From a logical point of view, the CO2 regulation is identical to the VOC regulation; if both are present, the regulator with the greatest request is considered active.

In the case of:

modulating recovery unit, the opening of the external dampers is regulated in parallel to the recovery unit

ON/OFF recovery unit, the opening of the external dampers starts after the recovery unit is in the OFF status.

NOTE: The CO2/VOC regulation is priority to the regulation linked to the recovery of heat.

The damper management in ON/OFF configuration consists of opening/closing the external dampers when the AHU is in the ON/OFF status.

The managing of the dampers in external configuration and 0-10 V mix consists of activating the modulating external dampers and the recirculation dampers, in opposition compared to the modulating external dampers: if the external dampers are completely open, the recirculation damper is completely closed, and vice versa. Generally, in the case of modulating external dampers:

the external dampers open a fixed percentage,

the external dampers open further in the case of:

a request from the probe CO2/VOC (air quality)

free-cooling.

Cooling actuators

The cooling actuators managed are described in the table below.

| Cooling actuators | Management procedure |
| --- | --- |
| Valves (1 - Fig 10 - on pag. 43) | Analogical output 0 -10 V |
| Condensing Unit configuration up to 4 steps (2 - Fig 10 - on pag. 43) | Step command |
| Modulating Condensing Units, up to 4 | Analogical outputs 0 -10 V |

Table 28 - Cold actuators managed and relative management procedure

NOTE: In the case of 0-10 V electrical heating element + step or PWM electrical heating element + step, analogical output and digital output are connected to each other as the modulating interpolates consecutive steps. In the case of condensation unit, the analogical output and digital output intervene in the regulation separately from each other.

In Fig 10 - on pag. 43 the reference parameters are shown using tags (capital letters), the reference parameters for the cooling actuators.

See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | CondUnitS1_Req |
| B | CondUnitS2_Req |
| C | CondUnitS3_Req |
| D | CondUnitS4_Req |

Table 29 - Cold actuators

In Fig 10 - on pag. 43 tags are used to indicate (capital letters):

e, the moving of the hysterisis,

f, the extent of the hysterisis

linked to each other by the following relation:

f = e · [CondUnitSx_Hysteresis]/100

The complete request for cooling is subdivided between the various actuators in cascade, according to the parameters, and is dependent on the supply limits. In the case of a condensing unit configuration up to 4 steps, the parameters for the regulation of the cooling actuators are:

percentage of regulation of condensation unit request for each step

hysterisis, calculated as a percentage of the step.

A minimum ON and OFF time of the condensing unit can be managed, moreover an offset can be applied to the analog output whenever at least a step is on (output is 0V when all steps are OFF).

In case more than one condensing unit is selected, they are switched on using a step logic proportional to the request of the main temperature regulator, the power is balanced over all active units.

Fig 10 - Cold actuators

Heating actuators

The heating actuators managed are described in the table below.

| Heating actuators | Management procedure |
| --- | --- |
| Valves | Analogical output 0 -10 V |
| Condensing unit configuration up to 4 steps | ON/OFF up to 4 steps |
| Modulating Condensing Units, up to 4 | Analogical outputs 0 -10 V |
| Heaters | ON/OFF up to 6 steps + possible modulation with PWM output |

Table 30 - Heating actuators managed and relative management procedure

This is a regulation with two components:

analogical to carry out modulation

digital, to carry out the steps.

The power of the analogical component (modulation) needs to be greater or equal to the power of the digital component (ON/OFF step) to guarantee agreement between the next two steps. The power of the digital component is expressed in %/kW of each step.

The hysterisis of switching off the steps is defined in the percentage of the step.

If the modulating heating element, the maximum hysteresis is limited to 1/4 of the minimum power step.

NOTE: The steps are implemented via a combination of activated relays (see 3.11.1 Activated relays and number of steps on pag. 46).

In Fig 11 - on pag. 45 the graphs of total request for heating of the PI regulator are illustrated, with relative components:

analogical, supplied by an analogue output, indicated with AO

digital, supplied with digital outputs, indicated with DO.

NOTE: Each step of the DO digital component is characterised by a negative hysteresis.

NOTE: The example given in Fig 11 - on pag. 45 refers to two digital steps and an analogical output with equal power to the hysteresis equating to (6/33)·100%.

The condensing unit regulation is described in chapter 3.10.

Fig 11 - Heat actuators

The following table gives the reference parameters for Fig 11 - on pag. 45.

| Parameters relative to Heater | Parameters relative to Pre Heater | Parameters relative to Post Heater | Description |
| --- | --- | --- | --- |
| Heater_Power_Analog | PreHeater_Power_Analog | PostHeater_Power_Analog | Power relative to the analogical status |
| Heater_Power_Step1 | PreHeater_Power_Step1 | PostHeater_Power_Step1 | Power relative to the digital status 1 |
| Heater_Power_Step2 | PreHeater_Power_Step2 | PostHeater_Power_Step2 | Power relative to the digital status 2 |
| Heater_Power_Step3 | PreHeater_Power_Step3 | PostHeater_Power_Step3 | Power relative to the digital status 3 |
| Heater_Power_Step4 | PreHeater_Power_Step4 | PostHeater_Power_Step4 | Power relative to the digital status 4 |
| Heater_Power_Step5 | PreHeater_Power_Step5 | PostHeater_Power_Step5 | Power relative to the digital status 5 |
| Heater_Power_Step6 | PreHeater_Power_Step6 | PostHeater_Power_Step6 | Power relative to the digital status 6 |
| Heater_Hysteresis | PreHeater_Hysteresis | PostHeater_Hysteresis | Hysteresis % of the active status |

Table 31 - Heat actuators

Activated relays and number of steps

The relays activated to obtain a given number of steps are described in the following tables.

| Relay | Step 1 | Step 2 |
| --- | --- | --- |
| 1 | X | X |
| 2 |  | X |
| Diagram |  |  |

Table 32 - Digital output connection: 2 steps, 2 relays

| Relay | Step 1 | Step 2 | Step 3 |
| --- | --- | --- | --- |
| 1 | X |  | X |
| 2 |  | X | X |
| Diagram |  |  |  |

Table 33 - Digital output connection: 3 steps, 2 relays

| Relay | Step 1 | Step 2 | Step 3 | Step 4 |
| --- | --- | --- | --- | --- |
| 1 | X |  | X | X |
| 2 |  | X | X | X |
| 3 |  |  |  | X |
| Diagram |  |  |  |  |

Table 34 - Digital output connection: 4 steps, 3 relays

| Relay | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 |
| --- | --- | --- | --- | --- | --- |
| 1 | X |  | X |  | X |
| 2 |  | X | X | X | X |
| 3 |  |  |  | X | X |
| Diagram |  |  |  |  |  |

Table 35 - Digital output connection: 5 steps, 3 relays

| Relay | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  | X |  | X |
| 2 |  | X |  |  | X | X |
| 3 |  |  | X | X | X | X |
| Diagram |  |  |  |  |  |  |

Table 36 - Digital output connection: 6 steps, 3 relays

Pumps

The management of a pump can be enabled when a valve with 0-10 V analogical output is enabled.

The management of the pump with hot valve is described in the table below.

| Pump status | Condition |
| --- | --- |
| Switch on | Valve opening |
| Switch off | - After 5 minutes of valve closure (post-functioning time), or - if AHU in OFF status |

Table 37 - Pump management

It is possible to activate the anti-sticking function to prevent the pump from blocking if it remains off for a long period of time: in the event of the upper pump not being used for 7 days, the pump is started automatically (see Pump_AntiStickingPeriod parameter and Pump_AntiStickingRun).

Fans

If in the AHU hardware configuration:

there is a single fan, if disabled, the AHU moves to the OFF status

there are several fans and a certain number gets disabled to the point that the AHU does not work properly, an alarm goes off.

Each fan can be disabled via parameter (see 4 User Settings Menu on pag. 55).

The fans have two time delays:

on turning on/turning off of the AHU, to allow for the opening and closure of the dampers

in post-ventilation, after a possible turning off of the heating elements and/or condensing units.

In heating, if the electric heating elements are one, the start-up of the electric heating elements is delayed with respect to the start-up of the fans, as shown in Fig 12 - on pag. 49: the regulation of the heating elements is done after the fans have reached their maximum speed.

Fig 12 - Dynamics of the heating elements and fans

In Fig 12 - on pag. 49 the reference parameters for heating elements and fans are shown using tags (capital letters). See the following table for the correspondence between tags and parameters.

| Tag | Parameters |
| --- | --- |
| A | Status_FanSupply Status_FanReturn |
| B | Fan_NominalSpeed |
| C | Fan_LowSpeed |
| D | Fan_PowerUp1_Time |
| E | Fan_PowerUp2_Time |

Table 38 - Dynamics of the heating elements and fans

The pre-heating function of the fans is activated if the following conditions are simultaneously met:

activation of the heating with modulating valve

external temperature lower than the Fan_PreHeatOnSet parameter

disabling of the making operative process when turning on.

NOTE: If the previous conditions are simultaneously met, the fans are turned on with a further delay of Fan_PreHeating_Time compared to the opening of the external dampers.

When the AHU is turned on, the fans are kept turned off for a time equal to the Fan_PreHeating_Time parameter to reduce the possibility of transmitting air too cold to the valves.

ON/OFF fans

The ON/OFF fans come on / turn off when the AHU is in the ON/OFF status. After turning on, the fan is brought to a stable speed.

The fans are turned on and off with a relay.

Modulating fans (with inverter)

With modulating fans (with inverter), the following are used:

digital output (relay), for the inverter consensus

analogical output, to modulate the speed.

NOTE: It is possible to set a fan regulation at a steady speed even for modulating fan type via an appropriate configuration of the percentage of return and supply.

The management of modulating fans is described in the table below.

| Management of the modulating fans | Management procedure |
| --- | --- |
| Manual (by the controller) | Via the setting of a fixed percentage for each fan |
| Automatic | Via a request from the CO2 probe/VOC probe |
| Automatic | Via pressure sensors (up to two) |

Table 39 - Management of modulating fans

The management of the modulating fans via pressure probes can be done:

by parallel regulating the supply pressure probe and return pressure probe, with an offset of difference between the two sensors to balance the flows

via a specific pressure probe for each fan.

In the case of recovery unit defrosting via the reduction of speed of the supply fan, the speed of the supply fan also depends on the regulator that carries out the recovery unit defrosting.

Backup fans

Each backup fan has the same air flow as the corresponding main fan.

The swap management (or inversion) between fans with backup is done via the Fan_SwapPolicy parameter and on which depends the selection of the supply fans and return fans for start-up, as described in the table below.

| Fan_SwapPolicy parameter | Management of the swap between fans |
| --- | --- |
| 0 | The main fan pair is started-up (if both active) |
| 1 | The pair of fans (main or backup) that has the smallest number of overall hours of functioning |
| 2 | The pair of fans (supply or return) that has the smallest number of overall hours of functioning |
| 3 | The pair of fans (main or backup) with the fan that individually has the smallest number of overall hours of functioning |

Table 40 - Management of the swap between fans

In the case of alarms relating to the pair of:

main fans, at start-up the backup fans are selected

backup fans, at start-up, the main fans are selected.

In the absence of any active alarm relating to the fans, periodically the rotation of the fans is carried out with a regularity equating to the Fan_Swap_Time parameter hours (if different from 0) between main fans and backup fans.

Modbus fans

The Modbus fans are piloted by the controller via the RS485-2 serial port with the following configuration: 19.2 E,8,1.

The kind of Modbus fans supported in the AHU are:

EBM Papst;

ATV212;

Ziehl EC blue.

The relative slave Modbus addresses for each fan in the AHU are given in the following table.

| Fan | ModBUS address |
| --- | --- |
| Main supply | 2 |
| Main return | 3 |
| Backup supply | 4 |
| Backup return | 5 |
| Second Supply (only Ziehl model) | 10 |
| Second Return (only Ziehl model) | 11 |
| Second Supply backup (only Ziehl model) | 12 |
| Second Return backup (only Ziehl model) | 13 |
| Third Supply (only Ziehl model) | 14 |
| Third Return (only Ziehl model) | 15 |
| Third Supply backup (only Ziehl model) | 16 |
| Third Return backup (only Ziehl model) | 17 |

Table 41 - Modbus Fans and relative addresses

For the Modbus EBM Papst type fans, see 3.13.4.1 Modbus EBM Papst type fans on pag. 52.

For the Modbus Ziehl EC blue type fans, see 3.13.4.2 Modbus Ziehl EC blue type fans on pag. 52.

For the Modbus ATV212 type fans, see 3.13.4.3 Modbus ATV212 type fans on pag. 52.

EMB Papst Modbus type fans

The levels of the registers relative to the EBM Papst Modbus type fans are given in the table below.

| Name | Register | Value | Note |
| --- | --- | --- | --- |
| Source set value | D101 | 1 | This parameter specifies the source from which the set value is taken: 1=RS485 (specified set value parameter D001) |
| Store Set Value | D103 | 0 | This parameter specifies whether or not an incoming specified set value (D001) is also stored in the EEPROM under set value (EEPROM) (D114 / D115): 0=Set value is not stored. The fan is stationary after a reset |
| Control Mode Day | D106-D017 | 2 | The external “Day/night” input and the “Day/night internal” parameter are used to select whether the value in “Control mode day” or “Control mode night” is applicable: 2=open loop PWM control. |
| Motor Stop Enable | D112 D113 | 1 | The external “Day/night” input and the “Day/night internal” parameter are used to select whether the value in “Motor stop enable day” or “Motor stop enable night” is applicable: 1=Motor stops if set value = 0 |

Table 42 - Levels of registers relative to the EBM Papst Modbus type fans

NOTE: For additional information consult the EMB Papst manual.

Ziehl EC blue Modbus type fans

The levels of the registers relative to the Ziehl EC blue Modbus type fans are given in the table below.

| Name | Register | Value | Note |
| --- | --- | --- | --- |
| Controlmode | 4 bit 0 | 2 | Speed control register h2 (fractional 0 - 32767 = 0 - 100 %) with possibility for switch over to Set Intern 2,3 |
| D1 Function (digital input) | 14 | 0 | Off |

Table 43 - Levels of registers relative to the Ziehl EC blue type fans

NOTE: For additional information consult the Ziehl EC blue manual.

ATV212 Modbus type fans

The levels of the registers relative to the ATV212 Modbus type fans are given in the table below.

| Name | Register | Value | Note |
| --- | --- | --- | --- |
| CMOD | 3+1 | 2 | The setting of parameter CMOd determines the source of start, stop, forward, and reverse operation commands when the drive is in remote mode. The drive needs to be stopped to make changes to parameter CMOd. |
| FMOD | 4+1 | 4 | The setting of parameter FMOd determines the source of the drive’s speed reference when the drive is in remote mode. The drive needs to be stopped to make changes to parameter FMOd. |
| Timeout | 2051+1 | 10 | WARNING LOSS OF CONTROL - If F803 is set to 0, communication control will be inhibited. - For safety reasons, inhibiting the communication interruption detection should be restricted to the debug phase or to special applications. Failure to follow these instructions can result in death, serious injury, or equipment damage. 0= Communication error detection disabled 1 to 100=1 to 100 seconds |
| F732 | 1842+1 | 1 | Use parameter F732 to enable or disable the LOC/REM key on the drive embedded display terminal. If the LOC/REM key is disabled, switching between local and remote mode can be achieved with parameters [Frequency mode sel] (FMOd) and [Command mode sel] (CMOd). |

Table 44 - Levels of registers relative to the ATV212 Modbus type fans

NOTE: For additional information consults the ATV212 manual.

Air quality: CO2 probe and VOC probe

In the event of a poor air quality reading by a CO2 probe and/or a VOC probe, the regulation increases the speed of the ventilators. In this case, there is an increase in the incoming air flow to increase the concentration of oxygen.

It is possible to enable the air quality control function only if one of the following conditions is verified:

there is a mix damper

the fan is modulating.

The regulation of the air quality control can be:

P, or

PI.

NOTE: In the case of activating the CO2 probe and the VOC probe, the active request is the greater of the two.

After defining the kind of probe, it is essential to define the following parameters relative to the regulation:

setpoint, in the case of P or PI regulator

differential, in the case of P or PI regulator

integral time, in the case of PI regulator.

The quality air regulator is a regulator in cascade; it acts in the following order, depending on the request:

- increasing the output of modulating external dampers (1 – Fig 13 - )

NOTE: It is necessary to set the minimum opening of the dampers.

on the modulating fans (2 - Fig 13 - ), as described below:

if the fans are regulated under pressure, increasing the pressure setpoint

if the fans are at a set speed, increasing t speed (between the minimum value and maximum value approved for the fans).

NOTE: The request for regulating the VOC probe takes priority over the request for regulating the external ON/OFF dampers + 0-10 V mix.

NOTE: In night profile the speed of the fans takes priority.

Fig 13 - Air quality regulator

Constant flow regulation

This regulation foresees a PID regulator to limit unexpected variations in the fan reaction.

The regulation at constant flow is obtained via a differential pressure probe connected to the suction part of the fan.

In the event of flow reduction due to an increase in aeraulic resistance (filter that gradually blocks), the functioning logic is as follows:

- the controller detects a reduction in the pressure via the pressure probe

the controller increases the output value connected to the fan

the controller increases the speed of the fan until it reaches the set setpoint.

NOTE: In order to regulate the constant flow, a calibration of the pressure of flow is requested via the use of two optional inputs.

Constant pressure regulation

This regulation foresees a PID regulator to limit unexpected variations in the fan reaction.

The constant pressure regulation is obtained via a differential pressure probe connected to the supply channel or return channel and detects the difference in pressure compared to the atmospheric pressure.

NOTE: The constant pressure regulation is generally done if the supply flow is channelled on more than one environment characterised by the same need for ventilation but not used simultaneously.

The regulation logic is as follows:

- the controller automatically established the pressure setpoint

the controller compares the pressure setpoint with the value acquired by the differential pressure probe

via this difference, the fan speed is increased or reduced until the pressure setpoint is reached.

Test output

The output test is a function that allows for the digital and analogical outputs to be tested by forcing a given value, with safety measures always in place.

NOTE: The output test can be done either by the controller or from the menu (see EnableTestOutput parameter).

The test function limitations of the output test carried out are given in the following table.

In case of Unit blocking alarms, test mode will be automatically disabled

| Test output | Limitation |
| --- | --- |
| Turning fans on | Not permitted in the case of closed dampers |
| Turning on heat elements | - Not permitted if fans off - No more than 5 minutes |

Table 45 - Limitations

User Settings Menu

The “User Settings Menu” pages are dynamic and some of them are visible only if there are relative functionalities present.

The list of menus which can be accessed from the “User Settings Menu” is shown in the table below.

| Menu | User | Installer | Reference in this Manual |
| --- | --- | --- | --- |
| A-Unit | SI | SI | 4.1 A-Unit on pag. 56 |
| B-Clock & Events | SI | SI | 4.2 B-Clock & Events on pag. 58 |
| C-Languages | SI | SI | 4.3 C-Languages on pag. 66 |
| D-Alarms | SI | SI | 4.4 D-Alarms on pag. 66 |
| E-User Settings | SI | SI | 4.5 E-User Settings on pag. 71 |
| F-I/O | SI | SI | 4.6 F-I/O on pag. 75 |
| G-Password | SI | SI | 4.7 G-Password on pag. 78 |
| H-System | NO | SI | 4.8 H-System on pag. 79 |

Table 46 - Menu that can be accessed from the “User Settings Menu”

NOTE: Below are given the pages that are shown on the display:

in the case of out of range values

as a confirmation message.

| Out of range values |  |  |
| --- | --- | --- |
| Confirmation messages |  |  |

A-Unit

Below is given the “A-Unit”, menu navigation that allows the main parameters to be managed.

The parameters in the “A-Unit” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Unit | Description |
| --- | --- | --- | --- | --- |
| - - - | Status_PlantMode | 0=Cool; 1=Heat; | — | Unit Working Mode |
| - - - | T_CurrentSetpointByPar | Signed 16-bit | °C | Current Setpoint by parameter based on selected mode |
| - - - | T_RegulationProbe | Signed 16-bit | °C | Temperature Regulation Probe |
| - - - | T_CurrentSupplySetpoint | Signed 16-bit | °C | Current Supply Setpoint |
| - - - | AI_LogicIndex_0 | Signed 16-bit | °C | Supply Temperature |
| - - - | Status_OutPost | Signed 16-bit | % | Post Heating Output |
| - - - | Status_OutHeat | Signed 16-bit | % | Heating Output |
| - - - | Status_OutRec | Signed 16-bit | % | Recovery Output |
| - - - | Status_OutCool | Signed 16-bit | % | Cooling Output |
| - - - | Status_PID_TSupplyHeat | Signed 16-bit | % | Heating Regulator Request |
| - - - | Status_PID_TSupplyCool | Signed 16-bit | % | Cooling Regulator Request |
| - - - | Status_LowTempSupplyLimit | Signed 16-bit | % | Low Supply Limit Regulator Request |
| - - - | Status_HighTempSupplyLimit | Signed 16-bit | % | High Supply Limit Regulator Request |
| - - - | Status_HighTempPreHeatLimit | Signed 16-bit | % | High Preheater Limit Regulator Request |
| - - - | Pr_CurrentSupplySetpoint | Signed 32-bit | Pa-m3/h | Current Fan Supply Setpoint - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_CurrentReturnSetpoint | Signed 32-bit | Pa-m3/h | Current Fan Return Setpoint - Units depends on Fan_Return_Pressure_Flow |
| - - - | Pr_Flow_Supply | Signed 32-bit | Pa-m3/h | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_Flow_Return | Signed 32-bit | Pa-m3/h | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| - - - | Pr_Flow_Supply | Signed 32-bit | Pa-m3/h | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_Flow_Return | Signed 32-bit | Pa-m3/h | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| - - - | Status_PID_PrSupply | Signed 16-bit | % | Supply Fan Regulator Request |
| - - - | Status_PID_PrReturn | Signed 16-bit | % | Return Fan Regulator Request |
| - - - | Status_FanSupply | Signed 16-bit | % | Fan Supply Speed |
| - - - | Status_FanReturn | Signed 16-bit | % | Fan Return Speed |
| - - - | Status_DefrostFan | Boolean | — | Defrost with Fan Status |
| - - - | Status_DefrostFanRed | Signed 16-bit | % | Defrost Supply Fan Speed Reduction |
| - - - | RH_CurrentSetpoint | Signed 16-bit | %R.H. | Current Return Setpoint |
| - - - | T_DewPointSetPoint | Signed 16-bit | °C | Current Dewpoint Setpoint |
| - - - | AI_LogicIndex_5 | Signed 16-bit | °C | Saturation Temperature |
| - - - | RH_RegulationProbe | Signed 16-bit | %R.H. | Humdity Regulation Probe |
| - - - | Status_PID_Humid | Signed 16-bit | % | Hmidification Regulator Request |
| - - - | Status_PID_DeHumid | Signed 16-bit | % | Dehumidification Regulator Request |
| - - - | Status_OutHum | Signed 16-bit | % | Humidifier Output |
| - - - | Status_ExtSHum | Signed 16-bit | g/Kg | External Specific Humidity |
| - - - | Status_RetSHum | Signed 16-bit | g/Kg | Return Specific Humidity |
| - - - | Status_HighHumSupplyLimit | Signed 16-bit | % | High Humidity Limit Regulator Request |
| - - - | AirQ_RegulationProbe | Signed 16-bit | %/ppm | Air Quality Regulation Probe |
| - - - | AirQ_CurrentSetpointVOC | Signed 16-bit | % | Current Setpoint VOC |
| - - - | AirQ_CurrentSetpointCO2 | Signed 16-bit | ppm | Current Setpoint CO2 |
| - - - | Status_PID_AirQ | Signed 16-bit | % | Air Quality Regulator Request |
| - - - | AI_LogicIndex_2 | Signed 16-bit | °C | External Temperature |
| - - - | Status_ExtDamper | Signed 16-bit | % | External Damper Status |
| - - - | Status_RecoveryCooling | Boolean | — | Cooling Recovery Status |
| - - - | Status_RecoveryHeating | Boolean | — | Heating Recovery Status |
| - - - | Status_FreeCooling | Boolean | — | Free Cooling Status |
| - - - | Status_FreeHeating | Boolean | — | Free Heating Status |
| - - - | Status_ActuatorsOffbyFCH | Boolean | — | Actuators off by Free Cooling/Heating |
| - - - | Status_FCHreq | Signed 16-bit | % | Free Cooling/Heating Request |
| - - - | Status_DefrostDamper | Boolean | — | Defrost with Damper Status |
| - - - | PreHeaterSetpoint | Signed 16-bit | °C | Setpoint Pre Heating |
| - - - | AI_LogicIndex_4 | Signed 16-bit | °C | Preheating Temp, |
| - - - | Status_OutPre | Signed 16-bit | % | Preheating Output |
| - - - | RecoveryDefrost_SetMaxReq | Signed 16-bit | °C | Recovery Defrost: Setpoint Expulsion Temperature |
| - - - | AI_LogicIndex_3 | Signed 16-bit | °C | Expulsion Temperature |
| - - - | Status_DefrostPreHeat | Boolean | — | Defrost with Preheating Status |

Table 47 - A-Unit

B-Clock & Events

Below is given the “B-Clock & Events” menu navigation that allows for the time periods and events to be managed.

|  |  | Clock |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “B1-Clock” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | sysClock_seconds_WR | Unsigned 8-bit | 0 | 0 | 59 | Second value to update |
| - - - | sysClock_minutes_WR | Unsigned 8-bit | 0 | 0 | 59 | Minute value to update |
| - - - | sysClock_hours_WR | Unsigned 8-bit | 0 | 0 | 23 | Hour value to update |
| - - - | sysClock_dayweek_WR | Unsigned 8-bit | 0 | 0 | 6 | Day of the week value to update |
| - - - | sysClock_daymonth_WR | Unsigned 8-bit | 1 | 1 | 31 | Day of the month value to update |
| - - - | sysClock_month_WR | Unsigned 8-bit | 1 | 1 | 12 | Month value to update |
| - - - | sysClock_year_WR | Unsigned 8-bit | 10 | 10 | 99 | Year value to update |
| - - - | sysClock_update | 0=Current; 1=Update; 2=Modify | 0 | 0 | 2 | Confirm update |
| - - - | DayLight_Region | 0=Europe; 1=USA/Canada | 0 | 0 | 1 | Day Light Region |
| - - - | DayLight_Enable | Boolean | 1 | — | — | Day Light Enable |

Table 48 - B1-Clock

|  |  | Day Event |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Profile P1 |  |  |  |
|  |  |  |  | Profile P2 |  |  |  |
|  |  |  |  | Days |  |  |  |

The parameter in the “B2- Day Event” menu is given in the table below.

| Pag | Name | Device Type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE00_TimeBandEnable | Boolean | 0 | — | — | Time events Enable |

The parameters in the “B21- Profile P1” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE10_TimeProfile1Event1 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #1 of profile #1 |
| - - - | tE11_ModeProfile1Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #1 of profile #1 |
| - - - | tE12_TimeProfile1Event2 | Signed 16-bit | 12:00 | 00:00 | 23:59 | Time of event #2 of profile #1 |
| - - - | tE13_ModeProfile1Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #2 of profile #1 |
| - - - | tE14_TimeProfile1Event3 | Signed 16-bit | 14:00 | 00:00 | 23:59 | Time of event #3 of profile #1 |
| - - - | tE15_ModeProfile1Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #3 of profile #1 |
| - - - | tE16_TimeProfile1Event4 | Signed 16-bit | 18:00 | 00:00 | 23:59 | Time of event #4 of profile #1 |
| - - - | tE17_ModeProfile1Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #4 of profile #1 |

Table 49 - B21-Profile P1

The parameters in the “B22- Profile P2” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE20_TimeProfile2Event1 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #1 of profile #2 |
| - - - | tE21_ModeProfile2Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #1 of profile #2 |
| - - - | tE22_TimeProfile2Event2 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #2 of profile #2 |
| - - - | tE23_ModeProfile2Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #2 of profile #2 |
| - - - | tE24_TimeProfile2Event3 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #3 of profile #2 |
| - - - | tE25_ModeProfile2Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #3 of profile #2 |
| - - - | tE26_TimeProfile2Event4 | Signed 16-bit | 18:00 | 00:00 | 23:59 | Time of event #4 of profile #2 |
| - - - | tE27_ModeProfile2Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #4 of profile #2 |

Table 50 - B22-Profile P2

The parameters in the “B23-Days” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/2 | tE01_TimeProfileMonday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Monday |
| 1/2 | tE02_TimeProfileTuesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Tuesday |
| 1/2 | tE03_TimeProfileWednesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Wednesday |
| 1/2 | tE04_TimeProfileThursday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Thursday |
| 2/2 | tE05_TimeProfileFriday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Friday |
| 2/2 | tE06_TimeProfileSaturday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Saturday |
| 2/2 | tE07_TimeProfileSunday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Sunday |

Table 51 - B23-Days

|  |  | Year Event |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “B3-Year Event” menu are given in the table below, divided up per page.

| Pag | Name | Device Type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | TW00_EnableYearEvents | Boolean | 0 | — | — | — | Enable year events |
| 1/15 | TW01_EventProfile01 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 1 |
| 1/15 | TW16_EnEvent01 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 1 |
| 1/15 | TW31_EventDDStart01 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 1 |
| 1/15 | TW46_EventMMStart01 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 1 |
| 1/15 | TW61_EventDDStop01 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 1 |
| 1/15 | TW76_EventMMStop01 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 1 |
| 2/15 | TW02_EventProfile02 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 2 |
| 2/15 | TW17_EnEvent02 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 2 |
| 2/15 | TW32_EventDDStart02 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 2 |
| 2/15 | TW47_EventMMStart02 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 2 |
| 2/15 | TW62_EventDDStop02 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 2 |
| 2/15 | TW77_EventMMStop02 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 2 |
| 3/15 | TW03_EventProfile03 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 2 |
| 3/15 | TW18_EnEvent03 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 3 |
| 3/15 | TW33_EventDDStart03 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 3 |
| 3/15 | TW48_EventMMStart03 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 3 |
| 3/15 | TW63_EventDDStop03 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 3 |
| 3/15 | TW78_EventMMStop03 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 3 |
| 4/15 | TW04_EventProfile04 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 4 |
| 4/15 | TW19_EnEvent04 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 4 |
| 4/15 | TW34_EventDDStart04 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 4 |
| 4/15 | TW49_EventMMStart04 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 4 |
| 4/15 | TW64_EventDDStop04 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 4 |
| 4/15 | TW79_EventMMStop04 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 4 |
| 5/15 | TW05_EventProfile05 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 5 |
| 5/15 | TW20_EnEvent05 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 5 |
| 5/15 | TW35_EventDDStart05 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 5 |
| 5/15 | TW50_EventMMStart05 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 5 |
| 5/15 | TW65_EventDDStop05 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 5 |
| 5/15 | TW80_EventMMStop05 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 5 |
| 6/15 | TW06_EventProfile06 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 6 |
| 6/15 | TW21_EnEvent06 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 6 |
| 6/15 | TW36_EventDDStart06 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 6 |
| 6/15 | TW51_EventMMStart06 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 6 |
| 6/15 | TW66_EventDDStop06 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 6 |
| 6/15 | TW81_EventMMStop06 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 6 |
| 7/15 | TW07_EventProfile07 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 7 |
| 7/15 | TW22_EnEvent07 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 7 |
| 7/15 | TW37_EventDDStart07 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 7 |
| 7/15 | TW52_EventMMStart07 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 7 |
| 7/15 | TW67_EventDDStop07 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 7 |
| 7/15 | TW82_EventMMStop07 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 7 |
| 8/15 | TW08_EventProfile08 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 8 |
| 8/15 | TW23_EnEvent08 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 8 |
| 8/15 | TW38_EventDDStart08 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 8 |
| 8/15 | TW53_EventMMStart08 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 8 |
| 8/15 | TW68_EventDDStop08 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 8 |
| 8/15 | TW83_EventMMStop08 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 8 |
| 9/15 | TW09_EventProfile09 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 9 |
| 9/15 | TW24_EnEvent09 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 9 |
| 9/15 | TW39_EventDDStart09 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 9 |
| 9/15 | TW54_EventMMStart09 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 9 |
| 9/15 | TW69_EventDDStop09 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 9 |
| 9/15 | TW84_EventMMStop09 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 9 |
| 10/15 | TW10_EventProfile10 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 10 |
| 10/15 | TW25_EnEvent10 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 10 |
| 10/15 | TW40_EventDDStart10 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 10 |
| 10/15 | TW55_EventMMStart10 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 10 |
| 10/15 | TW70_EventDDStop10 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 10 |
| 10/15 | TW85_EventMMStop10 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 10 |
| 11/15 | TW11_EventProfile11 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 11 |
| 11/15 | TW26_EnEvent11 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 11 |
| 11/15 | TW41_EventDDStart11 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 11 |
| 11/15 | TW56_EventMMStart11 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 11 |
| 11/15 | TW71_EventDDStop11 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 11 |
| 11/15 | TW86_EventMMStop11 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 11 |
| 12/15 | TW12_EventProfile12 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 12 |
| 12/15 | TW27_EnEvent12 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 12 |
| 12/15 | TW42_EventDDStart12 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 12 |
| 12/15 | TW57_EventMMStart12 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 12 |
| 12/15 | TW72_EventDDStop12 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 12 |
| 12/15 | TW87_EventMMStop12 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 12 |
| 13/15 | TW13_EventProfile13 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 13 |
| 13/15 | TW28_EnEvent13 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 13 |
| 13/15 | TW43_EventDDStart13 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 13 |
| 13/15 | TW58_EventMMStart13 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 13 |
| 13/15 | TW73_EventDDStop13 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 13 |
| 13/15 | TW88_EventMMStop13 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 13 |
| 14/15 | TW14_EventProfile14 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 14 |
| 14/15 | TW29_EnEvent14 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 14 |
| 14/15 | TW44_EventDDStart14 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 14 |
| 14/15 | TW59_EventMMStart14 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 14 |
| 14/15 | TW74_EventDDStop14 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 14 |
| 14/15 | TW89_EventMMStop14 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 14 |
| 15/15 | TW15_EventProfile15 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 15 |
| 15/15 | TW30_EnEvent15 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 15 |
| 15/15 | TW45_EventDDStart15 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 15 |
| 15/15 | TW60_EventMMStart15 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 15 |
| 15/15 | TW75_EventDDStop15 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 15 |
| 15/15 | TW90_EventMMStop15 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 15 |

Table 52 - B3-Year Event

C-Languages

Below is given the “C-Languages” menu navigation that allows for a language to be selected.

Remote display language is aligned to the one of the PLC at boot and periodically rechecked.

A language change on the remote display is applied also to the local display of the PLC

D-Alarms

Below is given the “D-Alarms” menu navigation that allows for alarms to be managed.

|  |  | Active |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The alarms in the “D1- Alarms” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Description |
| --- | --- | --- | --- |
| - - - | Alxx_Reset | Boolean | Alarm reset request command via Modbus |
| - - - | Al01_SupplyProbe | 0=Not Active; 1=Active; 2=Manual Reset | Al01-Supply Temperature Probe Error |
| - - - | Al02_ReturnProbe | See Al01_SupplyProbe | A02-Return Temperature Probe Error |
| - - - | Al03_ExternalProbe | See Al01_SupplyProbe | A03-External Temperature Probe Error |
| - - - | Al04_ExpulsionProbe | See Al01_SupplyProbe | A04-Expulsion Temperature Probe Error |
| - - - | Al05_PreHeatingProbe | See Al01_SupplyProbe | A05-Preheating Temperature Probe Error |
| - - - | Al06_SaturationProbe | See Al01_SupplyProbe | A06-Saturation Temperature Probe Error |
| - - - | Al07_AntifreezeProbe | See Al01_SupplyProbe | A07-Antifreeze Temperature Probe Error |
| - - - | Al08_AirQualityProbe_CO2 | See Al01_SupplyProbe | A08-CO2 Probe Error |
| - - - | Al09_SupplyPressureProbe | See Al01_SupplyProbe | A09-Supply Pressure Probe Error |
| - - - | Al10_ReturnPressureProbe | See Al01_SupplyProbe | A10-Return Pressure Probe Error |
| - - - | Al11_SupplyHumidityProbe | See Al01_SupplyProbe | A11-Hum. Supply Probe Error |
| - - - | Al12_ReturnHumidityProbe | See Al01_SupplyProbe | A12-Hum. Return Probe Error |
| - - - | Al13_AirQualityProbe_VOC | See Al01_SupplyProbe | A13-VOC Probe Error |
| - - - | Al14_ExternalHumidityProbe | See Al01_SupplyProbe | A14-Hum. External Probe Error |
| - - - | Al26_SensAirFlowSupply | See Al01_SupplyProbe | A26-Supply Airflow by Probe |
| - - - | Al27_SensAirFlowReturn | See Al01_SupplyProbe | A27-Return Airflow by Probe |
| - - - | Al28_SensAirFlowSupplyBck | See Al01_SupplyProbe | A28-Airflow Prb Sup.2 |
| - - - | Al29_SensAirFlowReturnBck | See Al01_SupplyProbe | A29-Airflow Prb Ret.2 |
| - - - | Al30_FanThermalSupply | See Al01_SupplyProbe | A30-Fan Supply |
| - - - | Al31_FanThermalReturn | See Al01_SupplyProbe | A31-Fan Return |
| - - - | Al32_Fire | See Al01_SupplyProbe | A32-Fire |
| - - - | Al33_Door | See Al01_SupplyProbe | A33-Door |
| - - - | Al34_Antifreeze | See Al01_SupplyProbe | A34-Antifreeze |
| - - - | Al35_AirFlowSupply | See Al01_SupplyProbe | A35-Airflow Supply |
| - - - | Al36_AirFlowReturn | See Al01_SupplyProbe | A36-Airflow Return |
| - - - | Al37_Humidifier | See Al01_SupplyProbe | A37-Humidifier |
| - - - | Al38_PreHeater | See Al01_SupplyProbe | A38-Preheater |
| - - - | Al39_Heater | See Al01_SupplyProbe | A39-Heater |
| - - - | Al40_PostHeater | See Al01_SupplyProbe | A40-Postheater |
| - - - | Al41_RotaryWheel | See Al01_SupplyProbe | A41-Recovery |
| - - - | Al42_Filter1 | See Al01_SupplyProbe | A42-Filter 1 |
| - - - | Al43_Filter2 | See Al01_SupplyProbe | A43-Filter 2 |
| - - - | Al44_Filter3 | See Al01_SupplyProbe | A44-Filter 3 |
| - - - | Al45_Filter4 | See Al01_SupplyProbe | A45-Filter 4 |
| - - - | Al46_FanThermalSupplyBck | See Al01_SupplyProbe | A46-Fan Supply 2 |
| - - - | Al47_FanThermalReturnBck | See Al01_SupplyProbe | A47-Fan Return 2 |
| - - - | Al48_AirFlowSupplyBck | See Al01_SupplyProbe | A48-Airflow Supply 2 |
| - - - | Al49_AirFlowReturnBck | See Al01_SupplyProbe | A49-Airflow Return 2 |
| - - - | Al50_CondUnit | See Al01_SupplyProbe | A50-Cond. Unit |
| - - - | Al51_RTC | See Al01_SupplyProbe | A51-Real Time Clock |
| - - - | Al52_FanMaintenance | See Al01_SupplyProbe | A52-Fan Maintenance |
| - - - | Al53_ModbusFanCfg | See Al01_SupplyProbe | A53-Modbus Fan Config. Timeout |
| - - - | Al54_FanSupplyCom | See Al01_SupplyProbe | A54-Modbus Fan Supply Communication |
| - - - | Al55_FanReturnCom | See Al01_SupplyProbe | A55-Modbus Fan Return Communication |
| - - - | Al56_FanSupplyBckCom | See Al01_SupplyProbe | A56-Modbus Fan Supply 2 Communication |
| - - - | Al57_FanReturnBckCom | See Al01_SupplyProbe | A57-Modbus Fan Return 2 Communication |
| - - - | Al58_Filter5 | See Al01_SupplyProbe | A58-Filter 5 |
| - - - | Al60_LogError | See Al01_SupplyProbe | A60-Log Error |
| - - - | Al61_Exp1 | See Al01_SupplyProbe | A61-Can Expansion 1 |
| - - - | Al62_Exp2 | See Al01_SupplyProbe | A62-Can Expansion 2 |
| - - - | Al66_CondUnit2 | See Al01_SupplyProbe | A66-Cond. Unit 2 |
| - - - | Al67_CondUnit3 | See Al01_SupplyProbe | A67-Cond. Unit 3 |
| - - - | Al68_CondUnit4 | See Al01_SupplyProbe | A68-Cond. Unit 4 |
| - - - | Al99_FanSupply_1b_Com | See Al01_SupplyProbe | Al99-Fan Supply 1b Com Alarm |
| - - - | Al100_FanSupply_1c_Com | See Al01_SupplyProbe | Al100-Fan Supply 1c Com Alarm |
| - - - | Al101_FanReturn_1b_Com | See Al01_SupplyProbe | Al101-Fan Return 1b Com Alarm |
| - - - | Al102_FanReturn_1c_Com | See Al01_SupplyProbe | Al102-Fan Return 1c Com Alarm |
| - - - | Al103_FanSupply_2b_Com | See Al01_SupplyProbe | Al103-Fan Supply 2b Com Alarm |
| - - - | Al104_FanSupply_2c_Com | See Al01_SupplyProbe | Al104-Fan Supply 2c Com Alarm |
| - - - | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | Al105-Fan Return 2b Com Alarm |
| - - - | Al106_FanReturn_2c_Com | See Al01_SupplyProbe | Al106-Fan Return 2c Com Alarm |

Table 53 - D1-Alarms

|  |  | Historical |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

Page “D2- Historical” allows to view the list of the last 50 alarms events.

| - - - | Historical_Value_Code | 0 = ---; 1 = A01-Supply Pr.; 2 = A02-Return Pr.; 3 = A03-External Pr.; 4 = A04-Expulsion Pr.; 5 = A05-Preheating Pr.; 6 = A06-Saturation Pr.; 7 = A07-Antifreeze Pr.; 8 = A08-CO2 Pr.; 9 = A09-Supply Press. Pr.; 10 = A10-Return Press. Pr.; 11 = A11-Hum. Supply Pr.; 12 = A12-Hum. Return Pr.; 13 = A13-VOC Pr.; 14 = A14-Hum. External Pr.; 26 = A26-Airflow Prb Sup.; 27 = A27-Airflow Prb Ret.; 28 = A28-Airflow Prb Sup.2; 29 = A29-Airflow Prb Ret.2; 30 = A30-Fan Supply; 31 = A31-Fan Return; 32 = A32-Fire; 33 = A33-Door; 34 = A34-Antifreeze; 35 = A35-Airflow Supply; 36 = A36-Airflow Return; 37 = A37-Humidifier; 38 = A38-Preheater; 39 = A39-Heater; 40 = A40-Postheater; 41 = A41-Recovery; 42 = A42-Filter 1; 43 = A43-Filter 2; 44 = A44-Filter 3; 45 = A45-Filter 4; 46 = A46-Fan Supply 2; 47 = A47-Fan Return 2; 48 = A48-Airflow Supply 2; 49 = A49-Airflow Return 2; 50 = A50-Cond. Unit; 51 = A51-Real Time Clock; 52 = A52-Fan Maintenance; 58 = A58-Filter 5 60 = A60-Log Error; 61 = A61-Can Expansion 1; 62 = A62-Can Expansion 2; 66 = A66-Cond. Unit 2 67 = A67-Cond. Unit 3 68 = A68-Cond. Unit 4 | — | 0 | 106 | Historical: Alarm Code |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | Historical_Value_Code | 99 = A99-Fan Sup.1b Com. 100 = A100-Fan Sup.1c Com. 101 = A101-Fan Ret.1b Com. 102 = A102-Fan Ret.1c Com. 103 = A103-Fan Sup.2b Com. 104 = A104-Fan Sup.2c Com. 105 = A105-Fan Ret.2b Com. 106 = A106-Fan Ret.2c Com. | — | 0 | 106 | Historical: Alarm Code |
| - - - | Historical_Value_Date | Signed 16-bit | — | — | — | Historical: Alarm Date |
| - - - | Historical_Value_Time | Signed 16-bit | — | — | — | Historical: Alarm Time |
| - - - | Historical_Value_SecStatus | Signed 16-bit | — | — | — | Historical: Alarm Seconds and Status: 100x+seconds (x=0 restored, x=1 active, x=2 wait for reset) |
| - - - | Historical_Number_alarms | Signed 16-bit | — | — | — | Historical: Number of stored alarms |
| - - - | Historical_Reset | Boolean | 0 | — | — | Historical: Reset Request |

Table 54 - D2-Historical

E-User Settings

Below is given the “E-User Settings” menu navigation that allows for user parameters to be managed.

E1-Setpoints

Below is given the E1-Setpoints” menu navigation that allows for the setpoints to be managed.

The parameters in the “E1- Setpoints” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6 | SP_T_Cool_E2 | Signed 16-bit | 26.0 | SP_T_MIN | SP_T_MAX | °C | Setpoint Cooling |
| 1/6 | SP_T_CoolEco_E2 | Signed 16-bit | 28.0 | SP_T_Cool_E2 | SP_T_MAX | °C | Setpoint Cooling Economy |
| 2/6 | SP_T_Heat_E2 | Signed 16-bit | 20.0 | SP_T_MIN | SP_T_MAX | °C | Setpoint Heating |
| 2/6 | SP_T_HeatEco_E2 | Signed 16-bit | 18.0 | SP_T_MIN | SP_T_Heat_E2 | °C | Setpoint Heating Economy |
| 3/6 | SP_T_Auto_E2 | Signed 16-bit | 240 | SP_T_MIN | SP_T_MAX | °C | Setpoint Auto |
| 3/6 | DIFF_T_AutoEco | Signed 16-bit | 20 | 0 | — | °C | Differential Economy Mode - Half Band (AUTO) |
| 4/6 | SP_RH_DehumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Dehumidication setpoint (comfort) |
| 4/6 | SP_RH_DehumidificationSetpointEco_E2 | Signed 16-bit | 55 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Dehumidication setpoint (eco) |
| 5/6 | SP_RH_HumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Humidification setpoint (comfort) |
| 5/6 | SP_RH_HumidificationSetpointEco_E2 | Signed 16-bit | 45 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Humidification setpoint (eco) |
| 6/6 | SP_CO2_E2 | Signed 16-bit | 800 | 0 | 2000 | ppm | CO2 Air quality setpoint |
| 6/6 | SP_VOC_E2 | Signed 16-bit | 40 | 0 | 100 | % | VOC Air quality setpoint |

Table 55 - E1-Setpoints

E2-Work Hours

Below is given the E2-Work Hours” menu navigation that allows for the operating periods of the fan to be managed.

The status in the “E2- Work Hours” menu are given in the table below, divided up per page (elements are visible if defined in the current unit configuration).

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| 1/5 | Unit_DD | Unsigned 16-bit | days | Unit Working Days |
| 1/5 | Unit_HH | Unsigned 16-bit | hours | Unit Working Hours |
| 1/5 | FanSupply_DD | Unsigned 16-bit | days | Supply Fan Working Days |
| 1/5 | FanSupply_HH | Unsigned 16-bit | hours | Supply Fan Working Hours |
| 2/5 | FanSupplyBck_DD | Unsigned 16-bit | days | Supply Fan 2 Working Days |
| 2/5 | FanSupplyBck_HH | Unsigned 16-bit | hours | Supply Fan 2 Working Hours |
| 2/5 | FanReturn_DD | Unsigned 16-bit | days | Return Fan Working Days |
| 2/5 | FanReturn_HH | Unsigned 16-bit | hours | Return Fan Working Hours |
| 3/5 | FanReturnBck_DD | Unsigned 16-bit | days | Return Fan 2 Working Days |
| 3/5 | FanReturnBck_HH | Unsigned 16-bit | hours | Return Fan 2 Working Hours |
| 3/5 | CondUnit1_DD | Unsigned 16-bit | days | Condensing Unit 1 Working Days |
| 3/5 | CondUnit1_HH | Unsigned 16-bit | hours | Condensing Unit 1 Working Hours |
| 4/5 | CondUnit2_DD | Unsigned 16-bit | days | Condensing Unit 2 Working Days |
| 4/5 | CondUnit2_HH | Unsigned 16-bit | hours | Condensing Unit 2 Working Hours |
| 4/5 | CondUnit3_DD | Unsigned 16-bit | days | Condensing Unit 3 Working Days |
| 4/5 | CondUnit3_HH | Unsigned 16-bit | hours | Condensing Unit 3 Working Hours |
| 5/5 | CondUnit4_DD | Unsigned 16-bit | days | Condensing Unit 4 Working Days |
| 5/5 | CondUnit4_HH | Unsigned 16-bit | hours | Condensing Unit 4 Working Hours |

Table 56 - E2-Work Hours

E3-Data Logger

Below is given the “E3-Data Logger” menu navigation that allows for the data loggers to be managed.

|  |  | Ok |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters of the “E3-Data Logger” are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | LogEnable | Boolean | 0 | — | — | Logger Enable |
| - - - | StartMonth | Unsigned 8-bit | 1 | 1 | 12 | Start Month - Log Period Export to USB |
| - - - | EndMonth | Unsigned 8-bit | 1 | 1 | 12 | End Month - Log Period Export to USB |
| - - - | StartYear | Unsigned 8-bit | 16 | 0 | 99 | Start Year - Log Period Export to USB |
| - - - | EndYear | Unsigned 8-bit | 16 | 0 | 99 | End Year - Log Period Export to USB |

Table 57 - E3-Data Logger

|  |  | microSD |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “E31- microSD Options” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | microSdStatus | 0=Not present; 1=Unsafe Removed; 2=Not Mounted; 3=Mounted | — | 0 | 3 | microSd Status |
| - - - | microSdError | Boolean | — | — | — | microSD Error |
| - - - | microSdInfo | 0=...; 1=Release SD; 2=Ready to remove/mount; 3=Ready for log; 4=...; 5=insert SD..; 6=Release SD; 7=Retry command..; 8=Yet mounted | — | 0 | 8 | microSd Info |
| - - - | microSDPresCount | Unsigned 16-bit | 0 | — | — | microSD Presence Counter |

Table 58 - E31-microSD Options

E4-Web Server

Below is given the E4-Web Server” menu navigation that allows for the access parameters relating to the web server, to be managed.

The parameters in the “E4- Web Server” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| - - - | WEB_User_E2 | String | administrator | Web User ID |
| - - - | WEB_PSW_E2 | String | password | Web Psw ID |

Table 59 - E4-Web Server

E5-Regulator

Below is given the E5-Regulator” menu navigation that allows for the regulators to be managed.

The parameters in the “E5-Regulators” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6 | cfgFreeCooling | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | FreeCooling Enable |
| 1/7 | cfgFreeHeating | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | FreeHeating Enable |
| 2/7 | FreeCHMinExtTemp | Signed 16-bit | 12.0 | -20.0 | 20.0 | °C | Free Cooling/Heating Minimum External Temperature |
| 2/7 | FreeCHBand | Signed 16-bit | 5.0 | 1.0 | 10.0 | °C | Free Cooling/Heating Proportional Band (direct return reg) |
| 3/7 | FreeCHTimeout | Unsigned 16-bit | 60 | 0 | 180 | min | Free Cooling/Heating Timeout |
| 3/7 | FreeCHDiff | Signed 16-bit | 5.0 | 1.0 | 10.0 | °C | Free Cooling/Heating Outside Regulation Differential |
| 4/7 | FreeCHHyst | Signed 16-bit | 1.0 | 0.2 | 5.0 | °C | Free Cooling/Heating Hysteresis |
| 4/7 | ---------------------- |  |  |  |  |  |  |
| 5/7 | FastHeatCoolEn | Boolean | 0 | — | — | — | Fast Heating/Cooling Enable |
| 5/7 | FastHCTimeout | Signed 16-bit | 10 | 1 | — | Min | Fast Heating/Cooling and StartUp timeout |
| 6/7 | FastCoolSet | Signed 16-bit | 20.0 | -50.0 | 50.0 | °C | Minimum outside temp for Power up Fast Cooling |
| 6/7 | FastCoolExitSet | Signed 16-bit | 26.0 | -50.0 | 50.0 | °C | Fast Cooling Return temperature exit set in case of supply Regulation |
| 7/7 | FastHeatSet | Signed 16-bit | 25.0 | -50.0 | 50.0 | °C | Maximum outside temp for Power up Fast Heating |
| 7/7 | FastHeatExitSet | Signed 16-bit | 18.0 | -50.0 | 50.0 | °C | Fast Heating Return temperature exit set in case of supply Regulation |

Table 60 - E5-Regulator

F-I/O

Below is given the “F-I/O” menu navigation that allows for the inputs and outputs to be managed.

The status in the “F-I/O” menu are given in the table below, divided up per page (elements are visible if defined in the current unit configuration)..

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
|  | AI_LogicIndex_0 | Signed 16-bit | °C | Supply Temperature |
|  | AI_LogicIndex_1 | Signed 16-bit | °C | Return Temperature |
|  | AI_LogicIndex_2 | Signed 16-bit | °C | External Temperature |
|  | AI_LogicIndex_3 | Signed 16-bit | °C | Expulsion Temperature |
|  | AI_LogicIndex_4 | Signed 16-bit | °C | Preheating Temp, |
|  | AI_LogicIndex_5 | Signed 16-bit | °C | Saturation Temperature |
|  | AI_LogicIndex_6 | Signed 16-bit | °C | Antifreeze Temperature |
|  | AI_LogicIndex_7 | Signed 16-bit | % | Air Quality - VOC |
|  | AI_LogicIndex_8 | Signed 16-bit | ppm | Air Quality - CO2 |
|  | AI_LogicIndex_9 | Signed 16-bit | pa | Supply Pressure |
|  | AI_LogicIndex_10 | Signed 16-bit | pa | Return Pressure |
|  | AI_LogicIndex_11 | Signed 16-bit | % | Supply Humidity |
|  | AI_LogicIndex_12 | Signed 16-bit | % | Return Humidity |
|  | AI_LogicIndex_13 | Signed 16-bit | % | External Humidity |
|  | AI_LogicIndex_14 | Signed 32-bit | m3/h | Supply Flow Testing |
|  | AI_LogicIndex_15 | Signed 32-bit | m3/h | Return Flow Testing |
|  | DI_Voltage_LogicIndex_0 | 0 = 0V; 1 = 24V; 2 = Not Used | — | Supply Fan Thermal - Physical Status |
|  | DI_Voltage_LogicIndex_1 | See DI_Voltage_LogicIndex_0 | — | Return Fan Thermal - Physical Status |
|  | DI_Voltage_LogicIndex_2 | See DI_Voltage_LogicIndex_0 | — | On/Off Input - Physical Status |
|  | DI_Voltage_LogicIndex_3 | See DI_Voltage_LogicIndex_0 | — | Fire Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_4 | See DI_Voltage_LogicIndex_0 | — | Mode Input - Physical Status |
|  | DI_Voltage_LogicIndex_5 | See DI_Voltage_LogicIndex_0 | — | Door - Physical Status |
|  | DI_Voltage_LogicIndex_6 | See DI_Voltage_LogicIndex_0 | — | Antifreeze - Physical Status |
|  | DI_Voltage_LogicIndex_7 | See DI_Voltage_LogicIndex_0 | — | Supply Airflow - Physical Status |
|  | DI_Voltage_LogicIndex_8 | See DI_Voltage_LogicIndex_0 | — | Return Airflow - Physical Status |
|  | DI_Voltage_LogicIndex_9 | See DI_Voltage_LogicIndex_0 | — | Humidifier Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_10 | See DI_Voltage_LogicIndex_0 | — | Preheater Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_11 | See DI_Voltage_LogicIndex_0 | — | Postheater Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_12 | See DI_Voltage_LogicIndex_0 | — | Rotary Wheel Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_13 | See DI_Voltage_LogicIndex_0 | — | Filter 1 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_14 | See DI_Voltage_LogicIndex_0 | — | Filter 2 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_15 | See DI_Voltage_LogicIndex_0 | — | Filter 3 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_16 | See DI_Voltage_LogicIndex_0 | — | Filter 4 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_30 | See DI_Voltage_LogicIndex_0 | — | Filter 5 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_17 | See DI_Voltage_LogicIndex_0 | — | Supply Fan 2 Th. - Physical Status |
|  | DI_Voltage_LogicIndex_18 | See DI_Voltage_LogicIndex_0 | — | Return Fan 2 Th. - Physical Status |
|  | DI_Voltage_LogicIndex_19 | See DI_Voltage_LogicIndex_0 | — | Supply Fan 2 Airflow - Physical Status |
|  | DI_Voltage_LogicIndex_20 | See DI_Voltage_LogicIndex_0 | — | Return Fan 2 Airflow - Physical Status |
|  | DI_Voltage_LogicIndex_21 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_22 | See DI_Voltage_LogicIndex_0 | — | El. Heater Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_23 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 2 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_24 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 3 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_25 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 4 Alarm - Physical Status |
|  | DI_Voltage_LogicIndex_26 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 1 Defrost - Physical Status |
|  | DI_Voltage_LogicIndex_27 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 2 Defrost - Physical Status |
|  | DI_Voltage_LogicIndex_28 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 3 Defrost - Physical Status |
|  | DI_Voltage_LogicIndex_29 | See DI_Voltage_LogicIndex_0 | — | Cond. Unit 4 Defrost - Physical Status |
|  | AO_LogicIndex_0 | Signed 16-bit | % | Supply Fan |
|  | AO_LogicIndex_1 | Signed 16-bit | % | Return Fan |
|  | AO_LogicIndex_2 | Signed 16-bit | % | Ext. Dampers |
|  | AO_LogicIndex_3 | Signed 16-bit | % | Bypass Damper |
|  | AO_LogicIndex_4 | Signed 16-bit | % | Modulating Cool - C/H |
|  | AO_LogicIndex_5 | Signed 16-bit | % | Modulating Heat |
|  | AO_LogicIndex_6 | Signed 16-bit | % | Pre Heater |
|  | AO_LogicIndex_7 | Signed 16-bit | % | Post Heater |
|  | AO_LogicIndex_8 | Signed 16-bit | % | Rotary Wheel / Exchanger |
|  | AO_LogicIndex_9 | Signed 16-bit | % | Humidifier |
|  | AO_LogicIndex_10 | Signed 16-bit | % | Condensing Unit 1 |
|  | AO_LogicIndex_11 | Signed 16-bit | % | Condensing Unit 2 |
|  | AO_LogicIndex_12 | Signed 16-bit | % | Condensing Unit 3 |
|  | AO_LogicIndex_13 | Signed 16-bit | % | Condensing Unit 4 |
|  | DO_LogicIndex_0 | 0 = Off; 1 = On; 2 = Not Used | — | Supply Fan - Logic Status |
|  | DO_LogicIndex_1 | See DO_LogicIndex_0 | — | Return Fan - Logic Status |
|  | DO_LogicIndex_2 | See DO_LogicIndex_0 | — | On Off - Logic Status |
|  | DO_LogicIndex_3 | See DO_LogicIndex_0 | — | Alarm - Logic Status |
|  | DO_LogicIndex_4 | See DO_LogicIndex_0 | — | Mode - Logic Status |
|  | DO_LogicIndex_5 | See DO_LogicIndex_0 | — | Ext. Dampers - Logic Status |
|  | DO_LogicIndex_6 | See DO_LogicIndex_0 | — | Bypass Damper - Logic Status |
|  | DO_LogicIndex_7 | See DO_LogicIndex_0 | — | Supply Damper - Logic Status |
|  | DO_LogicIndex_8 | See DO_LogicIndex_0 | — | Return Damper - Logic Status |
|  | DO_LogicIndex_9 | See DO_LogicIndex_0 | — | Pump Preheat - Logic Status |
|  | DO_LogicIndex_10 | See DO_LogicIndex_0 | — | Pump Postheat - Logic Status |
|  | DO_LogicIndex_11 | See DO_LogicIndex_0 | — | Cool/CH Pump - Logic Status |
|  | DO_LogicIndex_12 | See DO_LogicIndex_0 | — | Cool/CH Step 1 - Logic Status |
|  | DO_LogicIndex_13 | See DO_LogicIndex_0 | — | Cool/CH Step 2 - Logic Status |
|  | DO_LogicIndex_14 | See DO_LogicIndex_0 | — | Cool/CH Step 3 - Logic Status |
|  | DO_LogicIndex_15 | See DO_LogicIndex_0 | — | Cool/CH Step 4 - Logic Status |
|  | DO_LogicIndex_16 | See DO_LogicIndex_0 | — | Heat Pump - Logic Status |
|  | DO_LogicIndex_17 | See DO_LogicIndex_0 | — | Heater Step 1 - Logic Status |
|  | DO_LogicIndex_18 | See DO_LogicIndex_0 | — | Heater Step 2 - Logic Status |
|  | DO_LogicIndex_19 | See DO_LogicIndex_0 | — | Heater Step 3 - Logic Status |
|  | DO_LogicIndex_20 | See DO_LogicIndex_0 | — | Pre Heater Step 1 - Logic Status |
|  | DO_LogicIndex_21 | See DO_LogicIndex_0 | — | Pre Heater Step 2 - Logic Status |
|  | DO_LogicIndex_22 | See DO_LogicIndex_0 | — | Pre Heater Step 3 - Logic Status |
|  | DO_LogicIndex_23 | See DO_LogicIndex_0 | — | Post Heater Step 1 - Logic Status |
|  | DO_LogicIndex_24 | See DO_LogicIndex_0 | — | Post Heater Step 2 - Logic Status |
|  | DO_LogicIndex_25 | See DO_LogicIndex_0 | — | Post Heater Step 3 - Logic Status |
|  | DO_LogicIndex_26 | See DO_LogicIndex_0 | — | Humidifier - Logic Status |
|  | DO_LogicIndex_27 | See DO_LogicIndex_0 | — | Rotary Wheel / Exchanger - Logic Status |
|  | DO_LogicIndex_28 | See DO_LogicIndex_0 | — | Supply Fan 2 - Logic Status |
|  | DO_LogicIndex_29 | See DO_LogicIndex_0 | — | Return Fan 2 - Logic Status |
|  | DO_LogicIndex_30 | See DO_LogicIndex_0 | — | Supply Damper 2 - Logic Status |
|  | DO_LogicIndex_31 | See DO_LogicIndex_0 | — | Return Damper 2 - Logic Status |

Table 61 - F-I/O

G-Password

Below is given the “G-Password” menu navigation that allows for the password to be managed.

The parameters in the “G-Password” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| - - - | PSWEntry | Unsigned 16-bit | 0 | Password Entry: |
| - - - | PSWLevel | Unsigned 8-bit | — | Current password level |
| - - - | PSWreset | Boolean | 0 | Password Level Reset Request |
| - - - | Unit_Version | Unsigned 16-bit | 0.00 | Unit Application Version |

Table 62 - G-Password

Two password levels are defined, level 1 for Service and level 2 for OEM.

Access to level 2 is allowed only with unit in OFF status. Access to the submenu without entering a correct password is in read only mode.

H-System

Below is given the “H-System” menu navigation that allows for installer parameters to be managed.

S-Service

NOTE: The key  is only visible on the controller display.

S1-Fans

Below is given the S1-Fans” menu navigation that allows for the fans to be managed.

|  |  | General |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “General” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/12 | Fan_MinimumSpeed | Signed 16-bit | 25.0 | 0.0 | 50.0 | % | Fan Minimum Speed (Pressure Regulation and limit for other speed) |
| 1/12 | Fan_LowSpeed | Signed 16-bit | 30.0 | Fan _MinimumSpeed | 80.0 | % | Fan Low Speed (Start Phase/Night/Min Air Q. and Defrost Speed) |
| 2/12 | Fan_NominalSpeed | Signed 16-bit | 90.0 | Fan_LowSpeed | 100.0 | % | Fan Nominal/Maximum Speed |
| 2/12 | Fan_ReturnSpeedCorrection | Signed 16-bit | 0.0 | -50.0 | 50.0 | % | Fan Return Output correction (not used with 2 pressure probes) |
| 3/12 | Fan_PowerUp1_Time | Unsigned 16-bit | 30 | 0 | 255 | sec | Fan Power Up Time at Min Speed (with Heaters) |
| 3/12 | Fan_PowerUp2_Time | Unsigned 16-bit | 10 | 0 | 255 | sec | Fan Power Up Time at Nom Speed (with Heaters) |
| 4/12 | Fan_SinglePressureReturn | Boolean | 0 | — | — | — | In case of a unique pressure probe mounted on return section and Supply+Return Fans |
| 4/12 | Fan_Post_Time | Unsigned 16-bit | 40 | 0 | 255 | sec | Fan Post Ventilation Time (with Heaters) |
| 5/12 | Fan_PreHeating_Time | Unsigned 16-bit | 180 | 0 | 600 | sec | Fan Preheating Time (with heating valves) |
| 5/12 | Fan_PreHeatOnSet | Signed 16-bit | -5.0 | -20.0 | 10.0 | °C | External Temperature Set forcing preheating time |
| 6/12 | Fan_Swap_Time | Unsigned 16-bit | 240 | 0 | 600 | hours | Fan swap time (0=Disabled) |
| 6/12 | Fan_SwapPolicy | 0 = If available Start always Fans 1; 1 = Start Section with less working hours (Supply + Return); 2 = Start Fans with less working hours; 3 = Start Fans with less working hours keeping parallel sections | 0 | 0 | 3 | — | Fan swap policy |
| 7/12 | Fan_Maintenance_Supply | Boolean | 0 | — | — | — | Fan Main Supply Forced Off for maintenance |
| 7/12 | Fan_Maintenance_Return | Boolean | 0 | — | — | — | Fan Main Return Forced Off for maintenance |
| 8/12 | Fan_Maintenance_SupplyBck | Boolean | 0 | — | — | — | Fan Supply 2 Forced Off for maintenance |
| 8/12 | Fan_Maintenance_ReturnBck | Boolean | 0 | — | — | — | Fan Return 2 Forced Off for maintenance |
| 9/12 | Fan_Maintenance_Supply1b | Boolean | 0 | — | — | — | Fan Main Supply b Forced Off for maintenance |
| 9/12 | Fan_Maintenance_Supply1c | Boolean | 0 | — | — | — | Fan Main Supply c Forced Off for maintenance |
| 10/12 | Fan_Maintenance_Return1b | Boolean | 0 | — | — | — | Fan Main Return b Forced Off for maintenance |
| 10/12 | Fan_Maintenance_Return1c | Boolean | 0 | — | — | — | Fan Main Return c Forced Off for maintenance |
| 11/12 | Fan_Maintenance_Supply2b | Boolean | 0 | — | — | — | Fan Supply 2b Forced Off for maintenance |
| 11/12 | Fan_Maintenance_Supply2c | Boolean | 0 | — | — | — | Fan Supply 2c Forced Off for maintenance |
| 12/12 | Fan_Maintenance_Return2b | Boolean | 0 | — | — | — | Fan Main Return 2b Forced Off for maintenance |
| 12/12 | Fan_Maintenance_Return2c | Boolean | 0 | — | — | — | Fan Main Return 2c Forced Off for maintenance |

Table 63 - General

The parameters in the “Working Hours” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| 1/3 | Unit_DD | Unsigned 16-bit | days | Unit Working Days |
| 1/3 | --------------------- |  |  |  |
| 2/3 | FanSupply_DD | Unsigned 16-bit | days | Supply Fan Working Days |
| 2/3 | FanSupplyBck_DD | Unsigned 16-bit | days | Supply Fan 2 Working Days |
| 3/3 | FanReturn_DD | Unsigned 16-bit | days | Return Fan Working Days |
| 3/3 | FanReturnBck_DD | Unsigned 16-bit | days | Return Fan 2 Working Days |

Table 64 - Working Hours

The parameters in the “Supply” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/7 | Fan_Supply_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | Fan Supply Regulation Unit |
| 1/7 | Fan_K_Supply | Unsigned 16-bit | 100 | 1 | 3000 | — | Fan K Supply |
| 2/7 | Fan_SetFlowSupply | Signed 32-bit | 100 | Fan_Supply_SetMinFlow | Fan_Supply_SetMaxFlow | m3/h | Fan Supply Flow Setpoint |
| 2/7 | Fan_SetPrSupply | Signed 16-bit | 100 | Fan_Supply_SetMinPr | Fan_Supply_SetMaxPr | Pa | Fan Supply Pressure Setpoint |
| 3/7 | AI_LogicIndex_14 | Signed 32-bit | — | — | — | m3/h | Supply Flow Testing |
| 3/7 | AI_LogicIndex_9 | Signed 16-bit | — | — | — | pa | Supply Pressure |
| 4/7 | Fan_Supply_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | Fan Supply Minimum/Night Flow Setpoint |
| 4/7 | Fan_Supply_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | Fan Supply Maximum Flow Setpoint |
| 5/7 | Fan_Supply_SetMinPr | Signed 16-bit | 50 | — | — | Pa | Fan Supply Minimum/Night Pressure Setpoint |
| 5/7 | Fan_Supply_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | Fan Supply Maximum Pressure Setpoint |
| 6/7 | FAN_Supply_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | Fan Supply Prop. Band Pressure |
| 6/7 | FAN_Supply_TiP | Unsigned 16-bit | 75 | — | — | sec | Fan Supply Integral Time Pressure |
| 7/7 | FAN_Supply_TdP | Unsigned 16-bit | 0 | — | — | sec | Fan Supply Derivative Time Pressure |

Table 65 - Supply

The parameters in the “Return” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/7 | Fan_Return_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | Fan Return Regulation Unit |
| 1/7 | Fan_K_Return | Unsigned 16-bit | 100 | 1 | 3000 | — | Fan K Return |
| 2/7 | Fan_SetFlowReturn | Signed 32-bit | 100 | Fan_Return_SetMinFlow | Fan_Return_SetMaxFlow | m3/h | Fan Return Flow Setpoint |
| 2/7 | Fan_SetPrReturn | Signed 16-bit | 100 | Fan_Return_SetMinPr | Fan_Return_SetMaxPr | Pa | Fan Return Pressure Setpoint |
| 3/7 | AI_LogicIndex_15 | Signed 32-bit | — | — | — | m3/h | Return Flow Testing |
| 3/7 | AI_LogicIndex_10 | Signed 16-bit | — | — | — | pa | Return Pressure |
| 4/7 | Fan_Return_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | Fan Return Minimum/Night Flow Setpoint |
| 4/7 | Fan_Return_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | Fan Return Maximum Flow Setpoint |
| 5/7 | Fan_Return_SetMinPr | Signed 16-bit | 50 | — | — | Pa | Fan Return Minimum/Night Pressure Setpoint |
| 5/7 | Fan_Return_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | Fan Return Maximum Pressure Setpoint |
| 6/7 | FAN_Return_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | Fan Return Prop. Band Pressure |
| 6/7 | FAN_Return_TiP | Unsigned 16-bit | 75 | — | — | sec | Fan Return Integral Time Pressure |
| 7/7 | FAN_Return_TdP | Unsigned 16-bit | 0 | — | — | sec | Fan Return Derivative Time Pressure |

Table 66 - Return

In case of Modbus driven fan and based on the number and type of fans, the parameters in the “I Supply” menu are given in the table below, divided up per page.

|  |  | Modbus Fan Info |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| Model | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| Ziehl/EBM | Status_Supply1_FansActualSpeed | Signed 16-bit | Rpm | Supply Ziehl/EBM Speed |
| Ziehl/EBM | Status_Supply1_FansVoltage | Signed 16-bit | V | Supply Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Supply1_FansCurrent | Signed 16-bit | A | Supply Ziehl/EBM Current |
| Ziehl/EBM | Status_Supply2_FansActualSpeed | Signed 16-bit | Rpm | Supply Backup Ziehl/EBM Speed |
| Ziehl/EBM | Status_Supply2_FansVoltage | Signed 16-bit | V | Supply Backup Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Supply2_FansCurrent | Signed 16-bit | A | Supply Backup Ziehl/EBM Current |
| ATV | Status_Supply1_FansActualSpeedHz | Signed 16-bit | Hz | Supply ATV212 Speed |
| ATV | Supply1_ATV212_FreqMin | Unsigned 16-bit | Hz | Supply ATV 212 Minimum Frequency |
| ATV | Supply1_ATV212_FreqMax | Unsigned 16-bit | Hz | Supply ATV 212 Maximum Frequency |
| ATV | Status_Supply1_FansVoltagePerc | Signed 16-bit | % | Supply ATV212 DC Voltage |
| ATV | Status_Supply1_FansCurrentPerc | Signed 16-bit | % | Supply ATV212 DC Current |
| ATV | Status_Supply2_FansActualSpeedHz | Signed 16-bit | Hz | Supply Backup ATV212 Speed |
| ATV | Supply2_ATV212_FreqMin | Unsigned 16-bit | Hz | Supply Backup ATV 212 Minimum Frequency |
| ATV | Supply2_ATV212_FreqMax | Unsigned 16-bit | Hz | Supply Backup ATV 212 Minimum Frequency |
| ATV | Status_Supply2_FansVoltagePerc | Signed 16-bit | % | Supply Backup ATV212 DC Voltage |
| ATV | Status_Supply2_FansCurrentPerc | Signed 16-bit | % | Supply Backup ATV212 DC Current |

Table 67 - I Supply

The parameters in the “I Return” menu are given in the table below, divided up per page.

| Model | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| Ziehl/EBM | Status_Return1_FansActualSpeed | Signed 16-bit | rpm | Return Ziehl/EBM Speed |
| Ziehl/EBM | Status_Return1_FansVoltage | Signed 16-bit | V | Return Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Return1_FansCurrent | Signed 16-bit | A | Return Ziehl/EBM Current |
| Ziehl/EBM | Status_Return2_FansActualSpeed | Signed 16-bit | rpm | Return Backup Ziehl/EBM Speed |
| Ziehl/EBM | Status_Return2_FansVoltage | Signed 16-bit | V | Return Backup Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Return2_FansCurrent | Signed 16-bit | A | Return Backup Ziehl/EBM Current |
| ATV | Status_Return1_FansActualSpeedHz | Signed 16-bit | Hz | Return ATV212 Speed |
| ATV | Return1_ATV212_FreqMin | Unsigned 16-bit | Hz | Return ATV 212 Minimum Frequency |
| ATV | Return1_ATV212_FreqMax | Unsigned 16-bit | Hz | Return ATV 212 Maximum Frequency |
| ATV | Status_Return1_FansVoltagePerc | Signed 16-bit | % | Return ATV212 DC Voltage |
| ATV | Status_Return1_FansCurrentPerc | Signed 16-bit | % | Return ATV212 DC Current |
| ATV | Status_Return2_FansActualSpeedHz | Signed 16-bit | Hz | Return Backup ATV212 Speed |
| ATV | Return2_ATV212_FreqMin | Unsigned 16-bit | Hz | Return Backup ATV 212 Minimum Frequency |
| ATV | Return2_ATV212_FreqMax | Unsigned 16-bit | Hz | Return Backup ATV 212 Maximum Frequency |
| ATV | Status_Return2_FansVoltagePerc | Signed 16-bit | % | Return Backup ATV212 DC Voltage |
| ATV | Status_Return2_FansCurrentPerc | Signed 16-bit | % | Return Backup ATV212 DC Current |

Table 68 - I Return

|  |  | Modbus Fan Alarm Info Supply |  |  | ATV212 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | EBM |  |  |
|  |  |  |  |  | ZIEHL |  |  |

The parameters in the “Sup.Alarms” menu, S17, are given in the table below, divided up per page.

| Name | Description |
| --- | --- |
| Supply1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply1_EBM_MotorStatus | EBM D011+1 : Motor status |
| Supply2_EBM_MotorStatus | EBM D011+1 : Motor status |
| Supply1_ATV212_Status | ATV212: 64769+1 Fd01 |
| Supply1_ATV212_Trip | ATV212: 64656+1 FC90 |
| Supply2_ATV212_Status | ATV212: 64769+1 Fd01 |
| Supply2_ATV212_Trip | ATV212: 64656+1 FC90 |
| Supply1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |

Table 69 - Sup.Alarms

The parameters in the “Ret.Alarms” menu are given in the table below, divided up per page.

| Name | Description |
| --- | --- |
| Return1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return1_EBM_MotorStatus | EBM D011+1 : Motor status |
| Return2_EBM_MotorStatus | EBM D011+1 : Motor status |
| Return1_ATV212_Status | ATV212: 64769+1 Fd01 |
| Return1_ATV212_Trip | ATV212: 64656+1 FC90 |
| Return2_ATV212_Status | ATV212: 64769+1 Fd01 |
| Return2_ATV212_Trip | ATV212: 64656+1 FC90 |
| Return1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |

Table 70 - Ret.Alarms

NOTE: For the Modbus fans, the reset is only possible with password.

NOTE: The “I Supply” can only be viewed if a Modbus fan is active.

NOTE: The “Alarm Info Supply” can only be viewed if an alarm relative to a Modbus fan is active.

S2-Actuators

Below is given the S2-Actuators” menu navigation that allows for the actuators to be managed.

|  |  | Dampers |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “Dampers” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | ExtDamperOpenDelay | Unsigned 16-bit | 60 | — | — | sec | External/Fan Damper Open Time |
| 1/2 | ExtDamperCloseDelay | Unsigned 16-bit | 60 | — | — | sec | External/Fan Damper Close Time |
| 2/2 | ExtDamperMinOpen | Signed 16-bit | 50 | 0 | 100 | % | External Damper Minimum Open |
| 2/2 | ExtDamperMaxOpen | Signed 16-bit | 100 | ExtDamperMinOpen | 100 | % | External Damper Maximum Open |

Table 71 - Dampers

The parameters in the “El.Heat.” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/15 | Heater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Analog Power |
| 1/15 | Heater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 1 Power |
| 2/15 | Heater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 2 Additional Power |
| 2/15 | Heater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 3 Additional Power |
| 3/15 | Heater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 4 Additional Power |
| 3/15 | Heater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 5 Additional Power |
| 4/15 | Heater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 6 Additional Power |
| 4/15 | Heater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | El. Heater Hysteresis [% of current step] |
| 5/15 | Heater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | El. Heater PWM Period |
| 5/15 | ----------------------------- |  |  |  |  |  |  |
| 6/15 | PreHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Analog Power |
| 6/15 | PreHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 1 Power |
| 7/15 | PreHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 2 Power |
| 7/15 | PreHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 3 Power |
| 8/15 | PreHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 4 Power |
| 8/15 | PreHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 5 Power |
| 9/15 | PreHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 6 Power |
| 9/15 | PreHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | PreHeater Hysteresis [% of current step] |
| 10/15 | PreHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | PreHeater PWM Period |
| 10/15 | ----------------------------- |  |  |  |  |  |  |
| 11/15 | PostHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Analog Power |
| 11/15 | PostHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 1 Power |
| 12/15 | PostHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 2 Power |
| 12/15 | PostHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 3 Power |
| 13/15 | PostHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 4 Power |
| 13/15 | PostHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 5 Power |
| 14/15 | PostHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 6 Power |
| 14/15 | PostHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | PostHeater Hysteresis [% of current step] |
| 15/15 | PostHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | PreHeater PWM Period |

Table 72 - El.Heat.

The parameters in the “Pumps” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | Pump_AntiStickingRun | Unsigned 16-bit | 20 | 0 | 255 | sec | Antisticking run time |
| 1/2 | Pump_AntiStickingPeriod | Unsigned 16-bit | 7 | 0 | 30 | days | Antisticking period (0=Disabled) |
| 2/2 | Pump_Post_Time | Unsigned 16-bit | 5 | 0 | 255 | min | Pump Post Running Time |

Table 73 - Pumps

The parameters in the “Cond.Unit” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/11 | CondUnitS1_Req | Signed 16-bit | 20.0 | 0.0 | 100.0 | % | % CondUnit Step 1 |
| 1/11 | CondUnitS2_Req | Signed 16-bit | 40.0 | 0.0 | 100.0 | % | % CondUnit Step 2 |
| 2/11 | CondUnitS3_Req | Signed 16-bit | 60.0 | 0.0 | 100.0 | % | % CondUnit Step 3 |
| 2/11 | CondUnitS4_Req | Signed 16-bit | 80.0 | 0.0 | 100.0 | % | % CondUnit Step 4 |
| 3/11 | CondUnitSx_Hysteresis | Signed 16-bit | 50 | 10 | 100 | % | Cond. Unit Hysteresis % of current Step size |
| 3/11 | CondUnit_Offset | Signed 16-bit | 0.0 | 0.0 | 100.0 | % | Cond Unit AO Offset |
| 4/11 | CondUnit_Ton | Unsigned 16-bit | 0 | 0 | 600 | sec | Cond Unit Step Minimum On Time |
| 4/11 | CondUnit_Toff | Unsigned 16-bit | 0 | 0 | 600 | sec | Cond Unit Step Minimum Off Time |
| 5/11 | CondUnit_FanSpeedDefrost | 0=No Action 1=Low Speed 2=Fan Off |  |  |  |  | Condensing Unit: Fan Speed During Defrost |
| 6/11 | MultiCondUnit_CtrlMode | 0=Delay 1=Hysteresis |  |  |  |  | Multi Condensing Unit: Control |
| 6/11 | MultiCondUnit_RegHyst | Signed 16-bit | 5 | 2 | 30 | % | Multi Condensing Unit regulator hysteresis |
| 7/11 | MultiCondUnit_DelayOn | Unsigned 16-bit | 0 | 0 | 600 | Sec | Multi Cond Unit Delay On |
| 7/11 | MultiCondUnit_DelayOff | Unsigned 16-bit | 0 | 0 | 600 | Sec | Multi Cond Unit Delay Off |
| 8/11 | CU1_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 1 Forced Off for maintenance |
| 8/11 | CU2_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 2 Forced Off for maintenance |
| 9/11 | CU3_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 3 Forced Off for maintenance |
| 9/11 | CU4_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 4 Forced Off for maintenance |
| 10/11 | CondUnit1_DD | Unsigned 16-bit |  |  |  | days | Condensing Unit 1 Working Days |
| 10/11 | CondUnit2_DD | Unsigned 16-bit |  |  |  | Days | Condensing Unit 2 Working Days |
| 11/11 | CondUnit3_DD | Unsigned 16-bit |  |  |  | Days | Condensing Unit 3 Working Days |
| 11/11 | CondUnit4_DD | Unsigned 16-bit |  |  |  | days | Condensing Unit 4 Working Days |

Table 74 - Cond.Unit

S3-Regulators

Below is given the S3-Regulators” menu navigation that allows for the regulators to be managed.

|  |  | Temperature |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “Temperat.” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/17 | Unit_RegTempType | 0=Supply; 1=Return Direct; 2=Return Cascade | 1 | 0 | 2 | — | Temperature Regulation Probe |
| 1/17 | ---------------------- |  |  |  |  |  |  |
| 2/17 | SP_T_MIN | Signed 16-bit | 14.0 | — | SP_T_MAX | °C | Minimum Temperature Setpoint |
| 2/17 | SP_T_MAX | Signed 16-bit | 30.0 | SP_T_MIN | — | °C | Maximum Temperature Setpoint |
| 3/17 | SP_T_FORCESUMMER | Signed 16-bit | 24.0 | — | — | °C | Force Summer Mode (AUTO) |
| 3/17 | SP_T_FORCEWINTER | Signed 16-bit | 16.0 | — | — | °C | Force Winter Mode (AUTO) |
| 4/17 | DIFF_T_AutoChangeMode | Signed 16-bit | 2.0 | 0.5 | — | °C | Differential Change season (AUTO) |
| 4/17 | ---------------------- |  |  |  |  |  |  |
| 5/17 | Pb_Cooling | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Cooling Proportional Band |
| 5/17 | Ti_Cooling | Unsigned 16-bit | 0 | 0 | — | sec | Cooling Integral Time |
| 6/17 | Temp_LowSupplyEn | Boolean | 0 | — | — | — | Temperature Low Supply Limit Enable (Summer) |
| 6/17 | Temp_LowSupplySet | Signed 16-bit | 15.0 | 0.0 | 100.0 | °C | Temperature Low Supply Limit Setpoint (Summer) |
| 7/17 | Temp_LowSupplyBand | Signed 16-bit | 10.0 | 1.0 | 99.9 | °C | Temperature Low Supply Band (Summer) |
| 7/17 | ---------------------- |  |  |  |  |  |  |
| 8/17 | Pb_ReturnCooling | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Return Temp. Reg: Cooling Proportional Band (only Cascade) |
| 8/17 | Ti_ReturnCooling | Unsigned 16-bit | 0 | 0 | — | sec | Return Temp. Reg: Cooling Integral Time (only Cascade) |
| 9/17 | SupplyDeltaUpCooling | Signed 16-bit | 1.0 | 0.5 | 5.0 | °C | Cooling Max Supply =RegSet+SupplyDeltaUpCooling |
| 9/17 | SupplyDeltaDwCooling | Signed 16-bit | 12.0 | 0.5 | 15.0 | °C | Cooling Min Supply =RegSet-SupplyDeltaDwCooling |
| 10/17 | Pb_Heating | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Heating Proportional Band |
| 10/17 | Ti_Heating | Unsigned 16-bit | 0 | 0 | — | sec | Heating Integral Time |
| 11/17 | Temp_HighSupplyEn | Boolean | 0 | — | — | — | Temperature High Supply Limit Enable (Winter) |
| 11/17 | Temp_HighSupplySet | Signed 16-bit | 35.0 | 0.0 | 100.0 | °C | Temperature High Supply Limit Setpoint (Winter) |
| 12/17 | Temp_HighSupplyBand | Signed 16-bit | 10.0 | 1.0 | 99.9 | °C | Temperature High Supply Band (Winter) |
| 12/17 | ---------------------- |  |  |  |  |  |  |
| 13/17 | Pb_ReturnHeating | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Return Temp. Reg: Heating Proportional Band (only Cascade) |
| 13/17 | Ti_ReturnHeating | Unsigned 16-bit | 0 | 0 | — | sec | Return Temp. Reg: Heating Integral Time (only Cascade) |
| 14/17 | SupplyDeltaUpHeating | Signed 16-bit | 16.0 | 0.5 | 40.0 | °C | Heating Max Supply =RegSet+SupplyDeltaUpHeating |
| 14/17 | SupplyDeltaDwHeating | Signed 16-bit | 2.0 | 0.0 | 5.0 | °C | Heating Min Supply =RegSet-SupplyDeltaDwHeating |
| 15/17 | PostHeating4Integration | Boolean | 1 | — | — | — | Use the post heating also in the heating phase |
| 15/17 | PostPower | Signed 16-bit | 30.0 | 0.1 | 100.0 | % | % of PI out sent to post (if enabled as heat integration) |
| 16/17 | PreHeaterSetpoint | Signed 16-bit | 5.0 | -10.0 | 20.0 | °C | Setpoint Pre Heating |
| 16/17 | Pb_PreHeating | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | PreHeating Proportional Band |
| 17/17 | Ti_PreHeating | Unsigned 16-bit | 300 | 0 | — | sec | PreHeating Integral Time |

Table 75 - Temperat.

The parameters in the “Humidity” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/10 | SP_RH_MinSetpoint | Signed 16-bit | 30 | 20 | SP_RH _MaxSetpoint | %R.H. | Minimum relative humidity setpoint |
| 1/10 | SP_RH_MaxSetpoint | Signed 16-bit | 90 | SP_RH _MinSetpoint | 100 | %R.H. | Maximum relative humidity setpoint |
| 2/10 | Hum_Band | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | Humidification Band |
| 2/10 | Hum_HighSupplyEn | Boolean | 0 | — | — | — | Humidification High Supply Limit Enable |
| 3/10 | Hum_HighSupplySet | Signed 16-bit | 70.0 | 0.0 | 100.0 | %R.H. | Humidification High Supply Limit Setpoint |
| 3/10 | Hum_HighSupplyBand | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | Humidification High Supply Band |
| 4/10 | Pb_Dehum | Signed 16-bit | 10.0 | 0.2 | 20.0 | %R.H. | Dehum. Proportional Band |
| 4/10 | Ti_Dehum | Unsigned 16-bit | 0 | 0 | — | sec | Dehum. Integral Time |
| 5/10 | Pb_Dewpoint | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | Dewpoint Dehum. Proportional Band |
| 5/10 | Ti_Dewpoint | Unsigned 16-bit | 300 | 0 | — | sec | Dewpoint Dehum. Integral Time |
| 6/10 | Dehum_WinterEn | Boolean | 0 | — | — | — | Enable Winter Dehumidification |
| 6/10 | Dehum_WinterHumHyst | Signed 16-bit | 1.0 | 0.4 | 5.0 | g/Kg | Winter Dehumidification Hysteresis |
| 7/10 | Dehum_Req_Diff | Signed 16-bit | 5.0 | 0.1 | 15.0 | %R.H. | Dehumidification Request Differential on Return Humidity for Winter and Dewpoint mode |
| 7/10 | DeHum_LowSupplyEn | Boolean | 0 | — | — | %R.H. | DeHumidification Low Supply Limit Enable |
| 8/10 | DeHum_LowSupplySet | Signed 16-bit | 30.0 | 0.0 | 100.0 | %R.H. | DeHumidification Low Supply Limit Setpoint |
| 8/10 | DeHum_LowSupplyBand | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | DeHumidification Low Supply Band |
| 9/10 | Pb_Post | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | PostHeating Dehum. Proportional Band |
| 9/10 | Ti_Post | Unsigned 16-bit | 300 | 0 | — | sec | PostHeating Dehum. Integral Time |
| 10/10 | Offset_Post | Signed 16-bit | 1.0 | 0.4 | 5.0 | °C | PostHeating Setpoint offset with respect to current set |

Table 76 - Humidity

The parameters in the “Air Qual.” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/2 | VOC_Bp | Unsigned 16-bit | 30.0 | 0.1 | % | VOC Regulator: Prop. Band |
| 1/2 | VOC_Ti | Unsigned 16-bit | 0 | — | sec | VOC Regulator: Integral Time |
| 2/2 | CO2_Bp | Unsigned 16-bit | 400 | 1 | ppm | CO2 Regulator: Prop. Band |
| 2/2 | CO2_Ti | Unsigned 16-bit | 0 | — | sec | CO2 Regulator: Integral Time |

Table 77 - Air Qual.

The parameters in the “Recovery” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | RecoveryDiff_Band | Signed 16-bit | 1.5 | 0.1 | 10.0 | °C | Recovery Diff (On/Off Case) Recovery Band (Mod Case with Direct Return control); |
| 1/2 | RecoveryDeadZone | Signed 16-bit | 1.0 | 0.0 | 10.0 | °C | Recovery Dead Zone |
| 2/2 | RecoveryPower | Signed 16-bit | 25.0 | 0.0 | 100.0 | % | % of PI out sent to recovery (Only for Cascade or Supply control) |
| 2/2 | RecoveryReqDuringFastHC | Signed 16-bit | 0 | 0 | 100.0 | % | Recovery request during Fast Heating/Cooling |

Table 78 - Recovery

The parameters in the “Defrost” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | RecoveryDefrost_SetMaxReq | Signed 16-bit | -4.0 | -15.0 | 10.0 | °C | Recovery Defrost: Setpoint Expulsion Temperature |
| 1/2 | RecoveryDefrost_Band | Signed 16-bit | 4.0 | 0.1 | 10.0 | °C | Recovery Defrost: Band Mix Chamber/PreHeater/Supply Fan |
| 2/2 | RecoveryDefrost_Cutoff | Signed 16-bit | 0.0 | 0.0 | 10.0 | °C | Recovery Defrost: CutOff Modulating Fan |

Table 79 - Defrost

The parameters in the “Other” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| 1/1 | Unit_ForceOffAfterReboot | Boolean | 0 | Force Off keyboard after reboot |

Table 80 – Other

S4-Conf.Alarms

Below is given the “S4-Conf.Alarms” menu navigation that allows for the alarms to be managed.

The parameters in the “Conf.Alarms” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/8 | AFset | Signed 16-bit | 5.0 | -5.0 | 15.0 | °C | Antifreeze Setpoint |
| 1/8 | AFdiff | Signed 16-bit | 2.0 | 0.1 | 5.0 | °C | Antifreeze Differential |
| 2/8 | AFphtime | Unsigned 16-bit | 5 | 0 | 255 | min | Antifreeze Preheater time |
| 2/8 | ---------------------- |  |  |  |  |  |  |
| 3/8 | cfgFireAlarm | 0=Off All; 1=All Fans-Damper On; 2=ReturnFan-Damper On | 0 | 0 | 2 | — | Fire Alarm Configuration |
| 3/8 | FireTempSet | Signed 16-bit | 95.0 | 90.0 | — | °C | Setpoint Temperature for Fire Alarm |
| 4/8 | Fan_SupplyAirflowAlrmByAi | Boolean | 0 | — | — | — | Enable supply flow alarm by probe (pressure probe must be already enabled) |
| 4/8 | Fan_ReturnAirflowAlrmByAi | Boolean | 0 | — | — | — | Enable return flow alarm by probe (pressure probe must be already enabled) |
| 5/8 | Fan_SetMinAirflow | Signed 16-bit | 50 | — | — | Pa | Fan Airflow Alarm setpoint |
| 5/8 | Fan_AlrmPressBypass | Unsigned 16-bit | 30 | 1 | 600 | Sec | Flow Bypass |
| 6/8 | Alm_MinHumiditySens | Signed 16-bit | 2.0 | 0.0 | 100.0 | %R.H. | Minimum Valid Humidity Value |
| 6/8 | Alm_MinCO2Sens | Signed 16-bit | 40 | 0 | — | ppm | Minimum Valid CO2 Value |
| 7/8 | Alm_MinVOCSens | Signed 16-bit | 2.0 | 0.0 | 100.0 | % | Minimum Valid VOC Value |
| 7/8 | Alm_MinPrSens | Signed 16-bit | 40 | 0 | — | pa | Minimum Valid Pr Value (Fans on) |
| 8/8 | Alm_ActiveProbeBypass | Unsigned 16-bit | 30 | 0 | 600 | sec | Active Probe alarm bypass |

Table 81 - Conf.Alarms

S5-Data Logger

Below is given the “S5-Data Logger” menu navigation that allows for the data loggers to be managed.

The parameters in the “Data Logger” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | LogEnable | Boolean | 0 | — | — | — | Logger Enable |
| 1/2 | LogCycle | Unsigned 16-bit | 00:01 | MinLogCycle | 23:59 | Min | Logger Period |
| 2/2 | FileDimension | Unsigned 32-bit | — | — | — | — | Size of the current log file- Log Export to USB |
| 2/2 | MinLogCycle | Signed 16-bit | 00:01 | 0 | 23:59 | Min | Minimum Log Cycle |

Table 82 - Data Logger

S6-Restore Factory

Below is given the S6-Restore Factory” menu navigation that allows for the parameter resetting to be managed.

The parameters in the “Restore Factory” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | RestoreFactoryStatus | 0=Completed; 1=Running; 248=Open in write failed; 249=Write failed; 250=Some parameters failed; 251=File not compatible; 252=Usb not connected; 253=File too long; 254=File not present; 255=Command Failed | — | 0 | 255 | Restore Factory Settings Status |
| - - - | RestoreFactoryCommand | Boolean | 0 | — | — | Restore Factory Settings Request |

Table 83 - Restore Factory

S7-Modbus Scan

Below is given the S7-Modbus Scan” menu navigation that allows for the configuration of the holding register per slave with address (1…10 or 247) 19.2 E,8,1 connected to RS485-2 port.

NOTE: The Preset key refers to the Modbus fans.

|  |  | Preset |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O-I/O

NOTE: The sub-menu can be edited only after the password has been typed in.

O1-Polarity

Below is given “O1-Polarity” menu navigation that allows for the management of the input polarities and digital outputs.

|  |  | Polarity |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters of the “O1-Polarity” page are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/29 | DI_Polarity_LogicIndex_0 | 0V = Off, 24V = On/Alarm; 0V = On/Alarm, 24V = Off | 1 | 0 | 1 | Polarity - Supply Fan Thermal |
| 1/29 | DI_Polarity_LogicIndex_1 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return Fan Thermal |
| 2/29 | DI_Polarity_LogicIndex_2 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - On/Off Input |
| 2/29 | DI_Polarity_LogicIndex_3 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Fire Alarm |
| 3/29 | DI_Polarity_LogicIndex_4 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Mode Input |
| 3/29 | DI_Polarity_LogicIndex_5 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Door |
| 4/29 | DI_Polarity_LogicIndex_6 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Antifreeze |
| 4/29 | DI_Polarity_LogicIndex_7 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply Airflow |
| 5/29 | DI_Polarity_LogicIndex_8 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return Airflow |
| 5/29 | DI_Polarity_LogicIndex_9 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Humidifier Alarm |
| 6/29 | DI_Polarity_LogicIndex_10 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Preheater Alarm |
| 6/29 | DI_Polarity_LogicIndex_11 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Postheater Alarm |
| 7/29 | DI_Polarity_LogicIndex_12 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Rotary Wheel Alarm |
| 7/29 | DI_Polarity_LogicIndex_13 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 1 Alarm |
| 8/29 | DI_Polarity_LogicIndex_14 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 2 Alarm |
| 8/29 | DI_Polarity_LogicIndex_15 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 3 Alarm |
| 9/29 | DI_Polarity_LogicIndex_16 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 4 Alarm |
| 9/29 | DI_Polarity_LogicIndex_30 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 5 Alarm |
| 10/29 | DI_Polarity_LogicIndex_17 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply 2 Fan Th. |
| 10/29 | DI_Polarity_LogicIndex_18 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return 2 Fan Th. |
| 11/29 | DI_Polarity_LogicIndex_19 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply 2 Airflow |
| 11/29 | DI_Polarity_LogicIndex_20 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return 2 Airflow |
| 12/29 | DI_Polarity_LogicIndex_21 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Cond. Unit Alarm |
| 12/29 | DI_Polarity_LogicIndex_22 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - El. Heater Alarm |
| 13/29 | DI_Polarity_LogicIndex_26_29 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Cond. Unit Defrost |
| 13/29 | DO_Polarity_LogicIndex_0 | 0=NO; 1=NC | 0 | 0 | 1 | Supply Fan - DO Polarity |
| 14/29 | DO_Polarity_LogicIndex_1 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Fan - DO Polarity |
| 14/29 | DO_Polarity_LogicIndex_2 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | On Off - DO Polarity |
| 15/29 | DO_Polarity_LogicIndex_3 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Alarm - DO Polarity |
| 15/29 | DO_Polarity_LogicIndex_4 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Mode - DO Polarity |
| 16/29 | DO_Polarity_LogicIndex_5 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Ext. Dampers - DO Polarity |
| 16/29 | DO_Polarity_LogicIndex_6 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Bypass Damper - DO Polarity |
| 17/29 | DO_Polarity_LogicIndex_7 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Damper - DO Polarity |
| 17/29 | DO_Polarity_LogicIndex_8 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Damper - DO Polarity |
| 18/29 | DO_Polarity_LogicIndex_9 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump Preheat - DO Polarity |
| 18/29 | DO_Polarity_LogicIndex_10 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump Postheat - DO Polarity |
| 19/29 | DO_Polarity_LogicIndex_11 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Pump - DO Polarity |
| 19/29 | DO_Polarity_LogicIndex_12 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 1 - DO Polarity |
| 20/29 | DO_Polarity_LogicIndex_13 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 2 - DO Polarity |
| 20/29 | DO_Polarity_LogicIndex_14 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 3 - DO Polarity |
| 21/29 | DO_Polarity_LogicIndex_15 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 4 - DO Polarity |
| 21/29 | DO_Polarity_LogicIndex_16 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump heat - DO Polarity |
| 22/29 | DO_Polarity_LogicIndex_17 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 1 - DO Polarity |
| 22/29 | DO_Polarity_LogicIndex_18 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 2 - DO Polarity |
| 23/29 | DO_Polarity_LogicIndex_19 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 3 - DO Polarity |
| 23/29 | DO_Polarity_LogicIndex_20 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 1 - DO Polarity |
| 24/29 | DO_Polarity_LogicIndex_21 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 2 - DO Polarity |
| 24/29 | DO_Polarity_LogicIndex_22 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 3 - DO Polarity |
| 25/29 | DO_Polarity_LogicIndex_23 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 1 - DO Polarity |
| 25/29 | DO_Polarity_LogicIndex_24 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 2 - DO Polarity |
| 26/29 | DO_Polarity_LogicIndex_25 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 3 - DO Polarity |
| 26/29 | DO_Polarity_LogicIndex_27 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Humidifier - DO Polarity |
| 27/29 | DO_Polarity_LogicIndex_26 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Recovery - DO Polarity |
| 27/29 | DO_Polarity_LogicIndex_28 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Fan 2 - DO Polarity |
| 28/29 | DO_Polarity_LogicIndex_29 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Fan 2 - DO Polarity |
| 28/29 | DO_Polarity_LogicIndex_30 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Damper 2 - DO Polarity |
| 29/29 | DO_Polarity_LogicIndex_31 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Damper 2 - DO Polarity |

Table 84 - O1-Polarity

O2-Test Out

Below is given “O2-Test Out” menu navigation that allows for the management of the tests on analogue and digital outputs.

|  |  | Test Out |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

The parameters in the “O2- Test Out” menu depends on the current configuration of the unit.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | doTst_LogicIndex_0 | Boolean | 0 | — | — | — | Test DO - Supply Fan |
| - - - | aoTst_LogicIndex_0 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Supply Fan |
| - - - | doTst_LogicIndex_28 | Boolean | 0 | — | — | — | Test DO - Supply Fan 2 |
| - - - | doTst_LogicIndex_1 | Boolean | 0 | — | — | — | Test DO - Return Fan |
| - - - | aoTst_LogicIndex_1 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Return Fan |
| - - - | doTst_LogicIndex_29 | Boolean | 0 | — | — | — | Test DO - Return Fan 2 |
| - - - | doTst_LogicIndex_2 | Boolean | 0 | — | — | — | Test DO - On Off |
| - - - | doTst_LogicIndex_3 | Boolean | 0 | — | — | — | Test DO - Alarm |
| - - - | doTst_LogicIndex_4 | Boolean | 0 | — | — | — | Test DO - Mode |
| - - - | doTst_LogicIndex_5 | Boolean | 0 | — | — | — | Test DO - Ext. Dampers |
| - - - | aoTst_LogicIndex_2 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Ext. Dampers |
| - - - | doTst_LogicIndex_6 | Boolean | 0 | — | — | — | Test DO - Bypass Damper |
| - - - | aoTst_LogicIndex_3 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Bypass Damper |
| - - - | doTst_LogicIndex_7 | Boolean | 0 | — | — | — | Test DO - Supply Damper |
| - - - | doTst_LogicIndex_30 | Boolean | 0 | — | — | — | Test DO - Supply Damper 2 |
| - - - | doTst_LogicIndex_8 | Boolean | 0 | — | — | — | Test DO - Return Damper |
| - - - | doTst_LogicIndex_31 | Boolean | 0 | — | — | — | Test DO - Return Damper 2 |
| - - - | doTst_LogicIndex_9 | Boolean | 0 | — | — | — | Test DO - Pump Preheat |
| - - - | doTst_LogicIndex_10 | Boolean | 0 | — | — | — | Test DO - Pump Postheat |
| - - - | doTst_LogicIndex_11 | Boolean | 0 | — | — | — | Test DO - Cool/CH Pump |
| - - - | doTst_LogicIndex_12 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 1 |
| - - - | doTst_LogicIndex_13 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 2 |
| - - - | doTst_LogicIndex_14 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 3 |
| - - - | doTst_LogicIndex_15 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 4 |
| - - - | doTst_LogicIndex_16 | Boolean | 0 | — | — | — | Test DO - Heat Pump |
| - - - | doTst_LogicIndex_17 | Boolean | 0 | — | — | — | Test DO - Heater Step 1 |
| - - - | doTst_LogicIndex_18 | Boolean | 0 | — | — | — | Test DO - Heater Step 2 |
| - - - | doTst_LogicIndex_19 | Boolean | 0 | — | — | — | Test DO - Heater Step 3 |
| - - - | doTst_LogicIndex_20 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 1 |
| - - - | doTst_LogicIndex_21 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 2 |
| - - - | doTst_LogicIndex_22 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 3 |
| - - - | doTst_LogicIndex_23 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 1 |
| - - - | doTst_LogicIndex_24 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 2 |
| - - - | doTst_LogicIndex_25 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 3 |
| - - - | doTst_LogicIndex_26 | Boolean | 0 | — | — | — | Test DO - Humidifier |
| - - - | doTst_LogicIndex_27 | Boolean | 0 | — | — | — | Test DO - Rotary Wheel / Exchanger |
| - - - | aoTst_LogicIndex_9 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Humidifier |
| - - - | aoTst_LogicIndex_8 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Rotary Wheel / Exchanger |
| - - - | aoTst_LogicIndex_4 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Cool - C/H Valve |
| - - - | aoTst_LogicIndex_5 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Heat Valve |
| - - - | aoTst_LogicIndex_6 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Pre Heater |
| - - - | aoTst_LogicIndex_7 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Post Heater |
| - - - | aoTst_LogicIndex_10 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 1 |
| - - - | aoTst_LogicIndex_11 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 2 |
| - - - | aoTst_LogicIndex_12 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 3 |
| - - - | aoTst_LogicIndex_13 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 4 |

Table 85 - O2-Test Out

O3-I/O Allocation

Below is given “O3-I/O Allocation” menu navigation that allows for the management of the input and output allocations.

|  |  | Allocate |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

NOTE (1): The AllocationCmdSet parameter corresponds with the “O3-IO Allocation” menu page given above and allows for the management of the analogical and digital input and output allocations, as described in the following table.

| Key | Description |
| --- | --- |
| AI | “Al” access key to sub-menu |
| DI | “DI” access key to sub-menu |
| AO | “AO” access key to sub-menu |
| DO | “DO” access key to sub-menu |
| Auto | Automatic allocation command |
| Save | Save command on EEProm of the set allocation |
| Clear | Cancellation command of the set allocation |
| Reload | Reload command of allocation |

Table 86 - “O3-IO Allocation” menu description

The parameters in the “O3-I/O Allocation” menu relating to the analogical inputs are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | — | Allocation command |
| 1/35 | ioSV_base_AI_01 | -1 = Not Used; 0=Supply Temp.; 1=Return Temp.; 2=External Temp.; 3=Expulsion Temp.; 4=Preheat Temp.; 5=Saturation Temp.; 6=Antifreeze; 7=Air Quality CO2; 8=Air Quality VOC; 9=Pressure 1; 10=Pressure 2; 11=Supply Hum.; 12=Return Hum.; 13=External Hum.; 14=Flow Tuning 1; 15=Flow Tuning 2 | -1 | -1 | 15 | — | Temporary: Logic Allocation of the physical input |
| 1/35 | ioSV_base_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | Save command required to be effective |
| 2/35 | ioSV_base_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 2/35 | ioSV_base_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 3/35 | ioSV_base_AI_05 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 3/35 | ioSV_base_AI_06 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 4/35 | ioSV_base_AI_07 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 4/35 | ioSV_base_AI_08 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 5/35 | ioSV_base_AI_09 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 5/35 | ioSV_base_AI_10 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 6/35 | ioSV_base_AI_11 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 6/35 | ioSV_base_AI_12 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 7/35 | ioSV_exp1_AI_01 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 7/35 | ioSV_exp1_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 8/35 | ioSV_exp1_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 8/35 | ioSV_exp1_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 9/35 | ioSV_exp2_AI_01 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 9/35 | ioSV_exp2_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 10/35 | ioSV_exp2_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 10/35 | ioSV_exp2_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 11/35 | ioSV_base_AI_0102 | 0=NTC(NK103); 2=NTC(103AT); 3=4...20mA; 4=0-10V; 5=Ratiometric; 6=PT1000; 9=PTC; 10=0-5V; 11=0...20mA | 2 | 0 | 11 | — | Temporary: AI probe configuration |
| 11/35 | ioSV_base_AI_0304 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | Save command required to be effective |
| 12/35 | ioSV_base_AI_0506 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | — |
| 12/35 | ioSV_base_AI_0708 | See ioSV_base_AI_0102 | 4 | 0 | 11 | — | — |
| 13/35 | ioSV_base_AI_0910 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | — |
| 13/35 | ioSV_base_AI_1112 | See ioSV_base_AI_0102 | 4 | 0 | 11 | — | — |
| 14/35 | ioSV_exp1_AI_0102 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 14/35 | ioSV_exp1_AI_0304 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 15/35 | ioSV_exp2_AI_0102 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 15/35 | ioSV_exp2_AI_0304 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 16/35 | ioSV_base_AI01_min | Signed 16-bit | 0 | — | — | digit | Temporary: AI ranges |
| 16/35 | ioSV_base_AI01_max | Unsigned 16-bit | 1000 | — | — | digit | Save command required to be effective |
| 17/35 | ioSV_base_AI02_min | Signed 16-bit | 0 | — | — | digit | — |
| 17/35 | ioSV_base_AI02_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 18/35 | ioSV_base_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 18/35 | ioSV_base_AI03_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 19/35 | ioSV_base_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 19/35 | ioSV_base_AI04_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 20/35 | ioSV_base_AI05_min | Signed 16-bit | 0 | — | — | digit | — |
| 20/35 | ioSV_base_AI05_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 21/35 | ioSV_base_AI06_min | Signed 16-bit | 0 | — | — | digit | — |
| 21/35 | ioSV_base_AI06_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 22/35 | ioSV_exp1_AI01_min | Signed 16-bit | -500 | — | — | digit | — |
| 22/35 | ioSV_exp1_AI01_max | Signed 16-bit | 1100 | — | — | digit | — |
| 23/35 | ioSV_exp1_AI02_max | Signed 16-bit | 1100 | — | — | digit | — |
| 23/35 | ioSV_exp1_AI02_min | Signed 16-bit | -500 | — | — | digit | — |
| 24/35 | ioSV_exp1_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 24/35 | ioSV_exp1_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 25/35 | ioSV_exp1_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 25/35 | ioSV_exp1_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |
| 26/35 | ioSV_base_AI07_min | Signed 16-bit | 0 | — | — | digit | — |
| 26/35 | ioSV_base_AI07_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 27/35 | ioSV_base_AI08_min | Signed 16-bit | 0 | — | — | digit | — |
| 27/35 | ioSV_base_AI08_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 28/35 | ioSV_base_AI09_min | Signed 16-bit | 0 | — | — | digit | — |
| 28/35 | ioSV_base_AI09_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 29/35 | ioSV_base_AI10_min | Signed 16-bit | 0 | — | — | digit | — |
| 29/35 | ioSV_base_AI10_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 30/35 | ioSV_base_AI11_min | Signed 16-bit | 0 | — | — | digit | — |
| 30/35 | ioSV_base_AI11_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 31/35 | ioSV_base_AI12_min | Signed 16-bit | 0 | — | — | digit | — |
| 31/35 | ioSV_base_AI12_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 32/35 | ioSV_exp1_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 32/35 | ioSV_exp1_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 33/35 | ioSV_exp1_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 33/35 | ioSV_exp1_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |
| 34/35 | ioSV_exp2_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 34/35 | ioSV_exp2_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 35/35 | ioSV_exp2_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 35/35 | ioSV_exp2_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |

Table 87 - O3-I/O Allocation for analogical inputs

The parameters in the “O3-I/O Allocation” menu relating to the digital inputs are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/10 | ioSV_base_DI_01 | -1 = Not Used; 0=Supply Fan Th.Prot.; 1=Return Fan Th.Prot.; 2=On Off; 3=Fire Alarm; 4=Mode; 5=Door; 6=Antifreeze Alarm; 7=Airflow Alarm Supply; 8=Airflow Alarm Return; 9=Humidifier Alarm; 10=Pre Heater Alarm 11=Post Heater Alarm 12=Rotary Heat Exch. Alarm 13=Filter 1 Alarm 14=Filter 2 Alarm 15=Filter 3 Alarm 16=Filter 4 Alarm 17=Supply Fan 2 Th.Prot. 18=Return Fan 2 Th.Prot. 19=Supply Fan 2 Airflow Alarm 20=Return Fan 2 Airflow Alarm 21=Cond. Unit Alarm 22=Heater Alarm 23=Cond. Unit 2 Alarm 24=Cond. Unit 3 Alarm 25=Cond. Unit 4 Alarm 26=Cond. Unit 1 Defrost 27=Cond. Unit 2 Defrost 28=Cond. Unit 3 Defrost 29=Cond. Unit 4 Defrost 30=Filter 5 Alarm | -1 | -1 | 10 | — |
| 1/10 | ioSV_base_DI_02 | See ioSV_base_DI_01 | -1 | -1 | 10 | — |
| 2/10 | ioSV_base_DI_03 |  | -1 | -1 | 10 | — |
| 2/10 | ioSV_base_DI_04 |  | -1 | -1 | 10 | — |
| 3/10 | ioSV_base_DI_05 |  | -1 | -1 | 10 | — |
| 3/10 | ioSV_base_DI_06 |  | -1 | -1 | 10 | — |
| 4/10 | ioSV_base_DI_07 |  | -1 | -1 | 10 | — |
| 4/10 | ioSV_base_DI_08 |  | -1 | -1 | 10 | — |
| 5/10 | ioSV_base_DI_09 |  | -1 | -1 | 10 | — |
| 5/10 | ioSV_base_DI_10 |  | -1 | -1 | 10 | — |
| 6/10 | ioSV_base_DI_11 |  | -1 | -1 | 10 | — |
| 6/10 | ioSV_base_DI_12 |  | -1 | -1 | 10 | — |
| 7/10 | ioSV_exp1_DI_01 |  | -1 | -1 | 10 | — |
| 7/10 | ioSV_exp1_DI_02 |  | -1 | -1 | 10 | — |
| 8/10 | ioSV_exp1_DI_03 |  | -1 | -1 | 10 | — |
| 8/10 | ioSV_exp1_DI_04 |  | -1 | -1 | 10 | — |
| 9/10 | ioSV_exp2_DI_01 |  | -1 | -1 | 10 | — |
| 9/10 | ioSV_exp2_DI_02 |  | -1 | -1 | 10 | — |
| 10/10 | ioSV_exp2_DI_03 |  | -1 | -1 | 10 | — |
| 10/10 | ioSV_exp2_DI_04 |  | -1 | -1 | 10 | — |

Table 88 - O3-I/O Allocation for digital inputs

The parameters in the “O3-I/O Allocation” menu relating to the digital outputs are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/10 | ioSV_base_DO_01 | -1 = Not Used; 0=Supply Fan; 1=Return Fan; 2=On Off; 3=Alarm; 4=Mode; 5=Ext. Dampers; 6=Bypass Damper; 7=Supply Damper; 8=Return Damper; 9=Pump Preheat; 10=Pump Postheat; 11=Cool / Cool-Heat Pump; 12=Cool / Cool-Heat Step 1 or Cond.Unit 1; 13=Cool / Cool-Heat Step 2 or Cond.Unit 2; 14=Cool / Cool-Heat Step 3 or Cond.Unit 3; 15=Cool / Cool-Heat Step 4 or Cond.Unit 4; 16=Heat Pump; 17=Heater Step 1; 18=Heater Step 2; 19=Heater Step 3; 20=Pre Heater Step 1; 21=Pre Heater Step 2; 22=Pre Heater Step 3; 23=Post Heater Step 1; 24=Post Heater Step 2; 25=Post Heater Step 3; 26=Humidifier; 27=Recovery; 28=Supply Fan 2; 29=Return Fan 2; 30=Supply Damper 2; 31=Return Damper 2 | -1 | -1 | 31 | Temporary: Logic Allocation of the physical output |
| 1/10 | ioSV_base_DO_02 | See ioSV_base_DO_01 | -1 | -1 | 31 | Save command required to be effective |
| 2/10 | ioSV_base_DO_03 |  | -1 | -1 | 31 | — |
| 2/10 | ioSV_base_DO_04 |  | -1 | -1 | 31 | — |
| 3/10 | ioSV_base_DO_05 |  | -1 | -1 | 31 | — |
| 3/10 | ioSV_base_DO_06 |  | -1 | -1 | 31 | — |
| 4/10 | ioSV_base_DO_07 |  | -1 | -1 | 31 | — |
| 4/10 | ioSV_base_DO_08 |  | -1 | -1 | 31 | — |
| 5/10 | ioSV_base_DO_09 |  | -1 | -1 | 31 | — |
| 5/10 | ioSV_base_DO_10 |  | -1 | -1 | 31 | — |
| 6/10 | ioSV_base_DO_11 |  | -1 | -1 | 31 | — |
| 6/10 | ioSV_base_DO_12 |  | -1 | -1 | 31 | — |
| 7/10 | ioSV_exp1_DO_02 |  | -1 | -1 | 31 | — |
| 7/10 | ioSV_exp1_DO_01 |  | -1 | -1 | 31 | — |
| 8/10 | ioSV_exp1_DO_03 |  | -1 | -1 | 31 | — |
| 8/10 | ioSV_exp1_DO_04 |  | -1 | -1 | 31 | — |
| 9/10 | ioSV_exp2_DO_01 |  | -1 | -1 | 31 | — |
| 9/10 | ioSV_exp2_DO_02 |  | -1 | -1 | 31 | — |
| 10/10 | ioSV_exp2_DO_03 |  | -1 | -1 | 31 | — |
| 10/10 | ioSV_exp2_DO_04 |  | -1 | -1 | 31 | — |

Table 89 - “O3-I/O Allocation” relative to digital outputs

The parameters in the “O3-I/O Allocation” menu relating to the analogical outputs are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/5 | ioSV_base_AO_01 | -1 = Not Used; 0=Supply Fan; 1=Return Fan; 2=Ext. Dampers; 3=Byp. Damper; 4=Cool / Cool-Heat; 5=Heat; 6=Pre Heater; 7=Post Heater; 8=Recovery; 9=Humidifier 10=Cond.Unit 1 11=Cond.Unit 2 12=Cond.Unit 3 13=Cond.Unit 4 | -1 | -1 | 9 | — |
| 1/5 | ioSV_base_AO_02 | See ioSV_base_AO_01 | -1 | -1 | 9 | — |
| 2/5 | ioSV_base_AO_03 |  | -1 | -1 | 9 | — |
| 2/5 | ioSV_base_AO_04 |  | -1 | -1 | 9 | — |
| 3/5 | ioSV_base_AO_05 |  | -1 | -1 | 9 | — |
| 3/5 | ioSV_base_AO_06 |  | -1 | -1 | 9 | — |
| 4/5 | ioSV_exp1_AO_01 |  | -1 | -1 | 9 | — |
| 4/5 | ioSV_exp1_AO_02 |  | -1 | -1 | 9 | — |
| 5/5 | ioSV_exp2_AO_01 |  | -1 | -1 | 9 | — |
| 5/5 | ioSV_exp2_AO_02 |  | -1 | -1 | 9 | — |

Table 90 - “O3-I/O Allocation” relative to analogical outputs

O4-Base AI Cfg.

|  |  | Bios AI |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O5-AO Config.

|  |  | Bios AI |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O6-Not Allocate

|  |  | I/O Not Fully Cfg |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

P-Serial ports

The “P-Serial ports” menu allows for the management of communication ports via the relative keys, as shown in the following table.

| Communication port | “P-Serial ports” menu key | Meaning |
| --- | --- | --- |
| P1 | 485-1 | RS485 - 1 communication port of the controller |
| P2 | 485-2 | RS485 - 2 communication port of the controller |
| P3 | ETH | Ethernet communication port of the controller |
| P5 | BACnet | BACnet communication port of the controller |
| P6 | RS485 | RS485 communication port of the plug-in |
| P7 | RS232 | RS232 communication port of the plug-in |
| P8 | CAN | CAN communication port of the plug-in |

Table 91 - Management of the communication ports

|  |  | 485-1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 485-2 |  |  |  |  |  |
|  |  | ETH |  |  |  |  |  |
|  |  | BACnet |  |  |  |  |  |

The parameters in the “P5-Bacnet” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | BACNET_ENABLE | Boolean | 1 | — | — | Bacnet Protocol Enable |
| - - - | BACNET_ID | Unsigned 16-bit | 1 | 1 | — | Bacnet Device ID |
| - - - | BACNET_SUBNET | Unsigned 16-bit | 0 | 0 | 63 | Bacnet Device SUBNET |
| - - - | BACNET_BBMD_Ip1 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip2 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip3 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip4 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_TMO | Unsigned 16-bit | 60 | — | sec | BBMD Timeout - Foreing Devices Handling |

Table 92 - P5-Bacnet

|  |  | RS485 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | RS232 |  |  |  |  |  |
|  |  | CAN |  |  |  |  |  |

NOTE: The parameter relative to the communication ports P1, P2, P3, P6, P7, P8 are BIOS parameters of the controller. For additional information consult the User Guide FREE Advance manual.

Q-USB

U-Unit Configuration

Below is given the “Unit Configuration” menu navigation that allows for the AHU hardware configuration to be managed.

The parameters in the “Unit Configuration” menu are given in the table below, divided up per page.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/14 | cfgFans | 0=Supply; 1=Supply+Return | 0 | 0 | 1 | OEM: Fan Sections |
| 1/14 | cfgFanType | 0=On Off; 1=Modulating; 2=On Off Backup; 3=Modulating Backup; 4=ATV; 5=ATV Backup; 6=EBM; 7=EBM Backup; 8=Ziehl; 9=Ziehl Backup | 0 | 0 | 9 | OEM: Fan Type |
| 2/14 | cfgFanRegulation | 0=Fixed Speed; 1=Air Quality; 2=Pressure 1 Probe; 3=Pressure 2 Probes | 0 | 0 | 3 | OEM: Fan Regulator |
| 2/14 | cfgFanAlarm | 0=Thermal/Digital Protection; 1=Digital+Flowswitch | 0 | 0 | 1 | OEM: Fan Alarm Selection |
| 3/14 | cfgCoolHeatModules | 0=None; 1=Cool; 2=Heat; 3=Cool+Heat; 4=Cool/Heat Single out | 0 | 0 | 4 | OEM: Heating Cooling Enable |
| 5/14 | cfgPreHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Preheater Selection |
| 3/14 | cfgCooling | 0=Modulating Valve; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | OEM: Cooling Actuator Selection |
| 4/14 | cfgHeating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Heating Actuator Selection |
| 4/14 | cfgCooling_Heating | 0=Modulating Valve; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | OEM: Cooling+Heating Actuator Selection |
| 5/14 | cfgPostHeating | 0=None; 1=Modulating Valve; 2=Mod.Valve+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Postheater Selection |
| 6/14 | cfgAntifreeze | 0=None; 1=On Off; 2=NTC | 0 | 0 | 2 | OEM: Antifreeze Selection |
| 6/14 | cfgHeatRecovery | 0=None/Not Regulated; 1=Bypass On Off; 2=Bypass Mod; 3=Rotary On Off; 4=Rotary Mod; 5=Exchanger On Off; 6=Exchanger Mod | 0 | 0 | 6 | OEM: Heat Recovery Selection |
| 7/14 | cfgDefrostHeatRec | 0=None; 1=Supply Fans; 2=Preheating | 0 | 0 | 2 | OEM: Defrost Regulation Selection |
| 7/14 | cfgDampers | 0=None; 1=External On Off; 2=External + Mix Mod | 1 | 0 | 2 | OEM: External Dampers Selection |
| 8/14 | cfgHumidifier | 0=None; 1=On Off; 2=Modulating | 0 | 0 | 2 | OEM: Humidifier Selection |
| 8/14 | cfgDeHumidifier | 0=None; 1=Standard; 2=Dew Point; 3=Standard+Winter; 4=Dew Point+Winter | 0 | 0 | 4 | OEM: Dehumification Regulator |
| 9/14 | cfgDampersForFans | 0=None; 1=Supply; 2=Return; 3=Supply+Return | 0 | 0 | 3 | OEM: Dampers for fam Selection |
| 9/14 | cfgAirQuality | 0=None; 1=CO2; 2=VOC; 3=CO2+VOC | 0 | 0 | 3 | OEM: Air Quality Probe Selection |
| 10/14 | cfgFilterPressostat | Unsigned 8-bit | 0 | 0 | 5 | OEM: Number of filter pressostat |
| 10/14 | cfgDoorDI | Boolean | 0 | — | — | OEM: Door Input Enable |
| 11/14 | cfgModeDI | Boolean | 0 | — | — | OEM: Unit Mode Input Enable |
| 11/14 | cfgModeDO | Boolean | 0 | — | — | OEM: Unit Mode Output Enable |
| 12/14 | cfgCoolHeat_NumSteps | 0=1 Cond Unit – AO 1=1 Cond Unit - 1 Step+AO 2=1 Cond Unit - 2 Steps 3=1 Cond Unit - 3 Steps 4=1 Cond Unit - 4 Steps 16=2 Cond Units 32=3 Cond Units 64=4 Cond Units | 0 | 0 | 48 | OEM: Condensing Unit Steps |
| 12/14 | cfgHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Heater Steps |
| 13/14 | cfgPreHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Pre Heater Steps |
| 13/14 | cfgPostHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Post Heater Steps |
| 14/14 | cfgMixChamberBeforePreHeat | Boolean | 0 | — | — | OEM: If enabled dampers closed with PreAntifreeze and Defrost with PreHeating |
|  | CfgParallelFans | Unsigned 8-bit | 1 | 1 | 3 | OEM: Number of parallel fans (Ziehl only) |

Table 93 - Unit Configuration

W-Password

Datalogger

The controller allows for data to be saved on MicroSD.

Below are given some indications on how to use the MicroSD on the controller properly.

Removal of the MicroSD is forbidden without having previously dismantled it (see 4 User Settings Menu on pag. 55) and before previously disabling the data-logging to avoid an error signal.

It is essential to dismantle the MicroSD in the event it gets inserted into the controller already on (see 4 User Settings Menu on pag. 55).

Use of the MicroSD is forbidden with more than 500 stored files.

The MicroSD needs to be formatted FAT32.

If enabled, the data saving on MicroSD starts 1 minute after booting. The data saved on MicroSD are:

alarm status

the data shown in the following table:

| Data saved on MicroSD | Description |
| --- | --- |
| 'On/Off' | AHU status |
| 'Set T.' | Temperature set-point |
| 'Set RH' | Humidity setpoint |
| 'Set CO2' | Setpoint of air quality for CO2 probe |
| 'Set VOC' | Setpoint of air quality for VOC probe |
| 'Supply T.' | Temperature of supply probe |
| 'Return T.' | Temperature of return probe |
| 'Ext.T.' | Temperature of outdoor probe |
| 'Exp.T.' | Temperature of expulsion probe |
| 'Preheat T.' | Temperature of preheat probe |
| 'Sat. T.' | Temperature of saturation probe |
| 'Af T.' | Temperature of antifreeze probe |
| 'CO2' | CO2 probe |
| 'VOC' | VOC probe |
| 'Supply Pr.' | Supply probe |
| 'Return Pr.' | Return probe |
| 'Supply Hum.' | Humidity of supply probe |
| 'Return Hum.' | Humidity of return probe |
| 'Ext.Hum.' | Humidity of external probe |
| Mode | Corrent Mode: 0=Cooling 1=Heating |
| Supply Fan | Supply Fan Speed |
| Return Fan | Return Fan Speed |
| Ext.Damper | External Damper Out |
| Recovery | Recovery Out |
| Free C. | Free Cooling Status |
| Free H. | Free Heating Status |
| Off by FC | Actuators Off due to Active Free Cooling/Heating |
| Heat | Heating Output |
| Cool | Cooling Output |
| Pre Heat | Pre-Heating Output |
| Post Heat | Post-Heating Output |
| Humidifier | Humidifier Output |
| PID Cool | Cooling PID Request |
| PID Heat | Heating PID Request |
| PID Air Q. | Air Quality PID Request |
| Dehum. Req. | Dehumidification Request |
| Defrost Fan | Defrost Fan Status |

Table 94 - Data saved on MicroSD

BMS Protocols

The BMS protocols available are:

Modbus RTU

Modbus TCP.

Bacnet

In the Modbus protocol, the bridge procedure is activated towards all the enabled slaves if the display is not in the S7-Modbus Scan menu for the management of the Modbus master (see 4.8.1.7 S7-Modbus Scan on pag. 95).

Modbus RTU

NOTE: The parameters relative to the Modbus RTU protocol are BIOS parameters of the controller. For further information, see User Guide FREE Advance manual and in 11 Tables Modbus on pag. 133, 8 Alarms on pag. 125 for the Modbus register addresses that can be read and written.

Modbus TCP

NOTE: The parameters relative to the TCP Modbus protocol are BIOS parameters of the controller. For further information, see User Guide FREE Advance manual and in 11 Tables Modbus on pag. 133, 8 Alarms on pag. 125 for the Modbus register addresses that can be read and written.

Bacnet

The specifications relating to the Bacnet protocol are given in the table below.

| Profile | ACC Controller |
| --- | --- |
| Door | On Ethernet door or in alternative exclusive Bacnet MS/TP on door RS485-1 (see 4.8.3 P-Serial Ports on pag. 109). |

Table 95 - Specifications relative to the Bacnet protocol

The objects relative to the Bacnet protocol are given in the table below.

| Object name | Object type | Object instance | Description | Supports COV |
| --- | --- | --- | --- | --- |
| Supply Temperature | AI | 0 | Supply Temperature | Y |
| Return Temperature | AI | 1 | Return Temperature | Y |
| External Temperature | AI | 2 | External Temperature | Y |
| Expulsion Temperature | AI | 3 | Expulsion Temperature | Y |
| Preheating Temperature | AI | 4 | Preheating Temperature | Y |
| Saturation Temperature | AI | 5 | Saturation Temperature | Y |
| Antifreeze Temperature | AI | 6 | Antifreeze Temperature | Y |
| Air Quality CO2 | AI | 7 | Air Quality CO2 | Y |
| Air Quality VOC | AI | 8 | Air Quality VOC | Y |
| Supply Ventilation | AI | 9 | Supply Pressure or Flow | Y |
| Return Ventilation | AI | 10 | Return Pressure or Flow | Y |
| Supply Humidity | AI | 11 | Supply Humidity | Y |
| Return Humidity | AI | 12 | Return Humidity | Y |
| External Humidity | AI | 13 | External Humidity | Y |
| Supply Flow Tuning | AI | 14 | Supply Flow Tuning | Y |
| Return Flow Tuning | AI | 15 | Return Flow Tuning | Y |
| BAI16 | AI | 16 | Future Use | Y |
| Set Comfort Cool | AV | 17 | Set Comfort Cool | Y |
| Set Comfort Heat | AV | 18 | Set Comfort Heat | Y |
| Set Eco Cool | AV | 19 | Set Eco Cool | Y |
| Set Eco Heat | AV | 20 | Set Eco Heat | Y |
| Set Auto | AV | 21 | Set Auto | Y |
| Set Comfort Humidification | AV | 22 | Set Comfort Humidification | Y |
| Set Comfort DeHumidification | AV | 23 | Set Comfort DeHumidification | Y |
| Set Eco Humidification | AV | 24 | Set Eco Humidification | Y |
| Set Ecot DeHumidification | AV | 25 | Set Ecot DeHumidification | Y |
| Set CO2 | AV | 26 | Set CO2 | Y |
| Set VOC | AV | 27 | Set VOC | Y |
| Damper Position | AI | 28 | Damper Position | Y |
| Fan Supply Speed | AI | 29 | Fan Supply Speed | Y |
| Fan Return Speed | AI | 30 | Fan Return Speed | Y |
| Cooling Actuator | AI | 31 | Cooling Actuator | Y |
| Heating Actuator | AI | 32 | Heating Actuator | Y |
| PreHeating Actuator | AI | 33 | PreHeating Actuator | Y |
| PostHeating Actuator | AI | 34 | POstHeating Actuator | Y |
| Heat-Cool Recovery Request | AI | 35 | Heat-Cool Recovery Request | Y |
| Humidifier Actuator | AI | 36 | Humidifier Actuator | Y |
| On/Off Unit | BV | 0 | On Off Unit | N |
| Unit Alarm | BV | 1 | Unit Alarm | N |
| Unit Blocking Alarm | BV | 2 | Unit Blocking Alarm | N |
| Fire Alarm | BV | 3 | Unit Fire Alarm | N |
| Alarms Reset Request | BV | 4 | Alarms Reset Request |  |
| Unit Mode | MSV | 0 | Season Mode | N |
| Unit Set Mode | MSV | 2 | Setpoint Mode | N |
| Unit Current Mode | MSI | 1 | Season Mode | N |
| Unit Status | MSV | 3 | On Off Standby Unit | N |
| NC0 | NC | 0 | NC0 | N |
| NC1 | NC | 1 | NC1 | N |
| NC2 | NC | 2 | NC2 | N |
| NC3 | NC | 3 | NC3 | N |
| AHU_<subnet>_<id> | Device | 0 | — | N |

Table 96 - Items relative to the Bacnet protocol

If an object is not enabled, the applicative forces the status to “out of service”.

The unit of AI Supply, Return Ventilation, Supply Flow Tuning e Return Flow Tuning can be configured as Pascal (53) o m3/h (135).

Web Server

The Web Server is a software application that allows for the AHU to be managed. It is sub-divided into the following screens:

Home

  - Settings

  - Weekly Scheduler

  - Event Scheduler

State

  - IOs

  - Alarms and Historical

Log

  - Logged File

  - Trend.

The Home screen allows for the synoptic of the AHU to be dynamically configured, managed the main functions, including the ON/OFF status of the AHU and the summer/winter mode change, and view the status of the probes and alarms.

Fig 14 - Home Screen

Fig 15 - Visualizzazione Mobile

The Settings screen allows for the setpoints to be configured.

Fig 16 - Settings Screen

The Weekly Scheduler screen allows for the configuration of the weekly events.

Fig 17 – Weekly Scheduler

The Event Scheduler screen allows for the yearly event settings.

Fig 18 – Event Scheduler

The Alarms screen allows monitoring the current active alarms and the historical alarm.

Fig 19 - Alarms Screen

The Log screens allow to show the graphs of the logged data and download the logged files.

Fig 20 - Logged Files Screen

Fig 21 – Trends Screen

Alarms

The following table describes the alarms that may be activated.

| Modbus Register | Descrizione | Effetto | Riarmo | Ritardo |
| --- | --- | --- | --- | --- |
| 9520 | Alarm reset request command via Modbus | — | — | — |
| 9521 | Al01-Supply Temperature Probe Error | Force Stop Unit | Auto | — |
| 9522 | A02-Return Temperature Probe Error | Force supply temperature regulation Disable Winter Dehumidification | Auto | — |
| 9523 | A03-External Temperature Probe Error | Disable FreeCooling FreeHeating Disable Recovery | Auto | — |
| 9524 | A04-Expulsion Temperature Probe Error | Disable Defrost Recovery | Auto | — |
| 9525 | A05-Preheating Temperature Probe Error | Disable Preheating Actuators | Auto | — |
| 9526 | A06-Saturation Temperature Probe Error | Disable Dewpoint Dehumidification | Auto | — |
| 9527 | A07-Antifreeze Temperature Probe Error | Disable Antifreeze alarm When unit is on, open all the valves | Auto | — |
| 9528 | A08-CO2 Probe Error | Disable Air quality regulator | Auto | Delayed |
| 9529 | A09-Supply Pressure Probe Error | If 2 pressure probes enabled, uses single pressure probe regulation Otherwise uses fixed speed regulation | Auto | Delayed |
| 9530 | A10-Return Pressure Probe Error | If 2 pressure probes enabled, uses single pressure probe regulation Otherwise uses fixed speed regulation | Auto | Delayed |
| 9531 | A11-Hum. Supply Probe Error | Disable Humidification | Auto | Delayed |
| 9532 | A12-Hum. Return Probe Error | Disable Humidification and Dehumidification | Auto | Delayed |
| 9533 | A13-VOC Probe Error | Disable Air quality regulator | Auto | Delayed |
| 9534 | A14-Hum. External Probe Error | Disable Winter Dehumidification | Auto | Delayed |
| 9546 | A26-Supply Airflow by Probe | Force stop unit if backup fans are not available | Manual | Delay at fan start |
| 9547 | A27-Return Airflow by Probe | Force stop unit if backup fans are not available | Manual | Delay at fan start |
| 9548 | A28-Airflow Prb Sup.2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9549 | A29-Airflow Prb Ret.2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9550 | A30-Fan Supply | Force stop unit if backup fans are not available | Manual | — |
| 9551 | A31-Fan Return | Force stop unit if backup fans are not available | Manual | — |
| 9552 | A32-Fire | Refer to 8.1 Allarme incendio a pag. 127 | Manual | — |
| 9553 | A33-Door | Force Stop Unit | Manual | — |
| 9554 | A34-Antifreeze | Force Off Unit Enabled only in heating mode | Auto | Delayed if preheating enabled |
| 9555 | A35-Airflow Supply | Force stop unit if backup fans are not available | Manual | — |
| 9556 | A36-Airflow Return | Force stop unit if backup fans are not available | Manual | — |
| 9557 | A37-Humidifier | Disable Humidification | Manual | — |
| 9558 | A38-Preheater | Disable Preheating Electric Heaters | Manual | — |
| 9559 | A39-Heater | Disable Electric Heaters | Manual | — |
| 9560 | A40-Postheater | Disable Post Electric Heaters | Manual | — |
| 9561 | A41-Recovery | Disable Heat Recovery | Manual | — |
| 9562 | A42-Filter 1 | --- | Manual | — |
| 9563 | A43-Filter 2 | --- | Manual | — |
| 9564 | A44-Filter 3 | --- | Manual | — |
| 9565 | A45-Filter 4 | --- | Manual | — |
| 9566 | A46-Fan Supply 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9567 | A47-Fan Return 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9568 | A48-Airflow Supply 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9569 | A49-Airflow Return 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9570 | A50-Cond. Unit | Disable Condensing Unit | Manual | — |
| 9571 | A51-Real Time Clock | Disable Time and Events | Manual | — |
| 9572 | A52-Fan Maintenance | Force stop unit | Auto | — |
| 9573 | A53-Modbus Fan Config. Timeout | Force stop unit | Manual | — |
| 9574 | A54-Modbus Fan Supply Communication | Force stop unit if backup fans are not available | Manual | — |
| 9575 | A55-Modbus Fan Return Communication | Force stop unit if backup fans are not available | Manual | — |
| 9576 | A56-Modbus Fan Supply 2 Communication | Force stop unit if backup fans are not available | Manual | — |
| 9577 | A57-Modbus Fan Return 2 Communication | Force stop unit if backup fans are not available | Manual | — |
| 9578 | Al58_Filter5 | --- | Manual | — |
| 9580 | A60-Log Error | Disable Datalogging | Manual | — |
| 9581 | A61-Can Expansion 1 | Force Stop Unit | Manual | — |
| 9582 | A62-Can Expansion 2 | Force Stop Unit | Manual | — |
| 9586 | Al66_CondUnit2 | Disable Condensing Unit 2 | Manual | — |
| 9587 | Al67_CondUnit3 | Disable Condensing Unit 3 | Manual | — |
| 9588 | Al68_CondUnit4 | Disable Condensing Unit 4 | Manual | — |
| 9619 | Al99-Fan Supply 1b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9620 | Al100-Fan Supply 1c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9621 | Al101-Fan Return 1b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9622 | Al102-Fan Return 1c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9623 | Al103-Fan Supply 2b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9624 | Al104-Fan Supply 2c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9625 | Al105-Fan Return 2b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9626 | Al106-Fan Return 2c Com Alarm | Force stop unit if backup fans are not available | Manual |  |

Table 97 - Alarms

NOTE: The following alarms have no effect on the AHU but are exclusively pointed out:

A42-Filter 1

A43-Filter 2

A44-Filter 3

A45-Filter 4.

A58-Filter 5.

NOTE: In delay type alarms, the alarm is activated after a time delay between it and the event that generated it.

NOTE: In “Delay at fan start” alarms, the alarm can only be activated after the fans have been turned on.

Fire alarm

The fire alarm is managed via a digital input.

In the event of a fire, one of the following actions for the AHU can be configured:

stop

opening of the dampers and forcing of the fans at maximum speed

opening of the dampers and forcing of the single fan at maximum speed.

Air quality probe alarm

The air quality probe is managed via 0-10 V analogical input.

The air quality probe alarm activates when the analogical input acquires a lower signal:

than the Alm_MinCO2Sens parameter, in the case of the CO2 probe,

than the Alm_MinVOCSens parameter, in the case of the VOC probe,

for a period of time greater than the time-out, given by the Alm_ActiveProbeBypass parameter.

In the case of air quality probe alarm, the fans are put at maximum speed.

Pressure probe alarm

The pressure probe is managed via 0-10 V analogical input.

The pressure probe alarm is activated if the following conditions are simultaneously met:

the analogical input acquires a signal lower than the Fan_SupplyAirflowAlrmByAi parameter for a time greater than the time-out given by the Alm_ActiveProbeBypass parameter

the fans are on.

In the case of pressure probe alarm, the fans are put at maximum speed.

Air flow alarm

The air flow alarm can be enabled if there is a differential pressure probe, it is disabled during the switch off procedure.

In the event of an air flow alarm, the AHU is stopped.

Fan protection alarm

The fan protection alarm is relative both to the supply fan as well as the return fan.

In the event of fans with physical inputs, the fan protection alarm is managed via a digital input. The fan protection alarm is generated even in the case of Modbus fans.

Re-setting after the fan protection alarm is manual.

If there are no backup fans, when the fan protection alarm goes off, the AHU stops.

If there are backup fans, when the fan protection alarm goes off:

both the main fans are stopped

- the main fan damper is closed

the backup fan damper is opened, if present

both backup fans are started up.

If the fan protection alarm is generated by the return fan, the post-ventilation for cooling the heating elements is also carried out.

When the fan protection alarm is turned off, the main fans are started up again if, simultaneously, the following conditions are met:

Fan_SwapPolicy parameter different from 2

a main fan is active

a backup fan is active.

The pair of main fans or the pair of backup fans is then activated, depending on the value of the Fan_SwapPolicy parameter and the hours of functioning of the fans themselves.

Fan maintenance alarm

As controller, it is possible to disable a single fan in order to carry out maintenance work. If both supply fans or both return fans are disabled, the fan maintenance alarm appears as it is not possible to start-up the AHU.

The fan maintenance alarm is automatically reset.

Antifreeze alarm

The antifreeze alarm can be activated:

by the thermostat, via digital input

by antifreeze probe, via analogical input.

In the event of the antifreeze alarm being activated by the thermostat, the preheating actuator is activated at 100% of its power.

The antifreeze alarm management by the antifreeze probe is described in the following table.

| Temperature measured by the antifreeze probe | Time (in minutes) | Antifreeze signal | Effects |
| --- | --- | --- | --- |
| Lower than setpoint + differential | Lower than AFphtime parameter | The control within the “antifreeze prevention” procedure | - The power is increased gradually via P regulator with proportional band equal to the differential between antifreeze probe temperature and antifreeze setpoint - Closure of external dampers, if the cfgMixChamberBeforePreHeat parameter is enabled |
| Greater than setpoint + differential | / | The control exits the “antifreeze prevention” procedure | None |
| Lower than setpoint + differential | Greater than AFphtime parameter | Antifreeze alarm | - AHU in OFF status - Valve opening - External damper closure |

Table 98

Management of the antifreeze probe antifreeze alarm

If the controller enters the “antifreeze prevention” procedure:

it stops the fans

closes the external gates

activates the valves at 100%

activates all the pumps.

The controller exits “antifreeze prevention” procedure if the antifreeze probe returns to a temperature greater than setpoint + differential.

The antifreeze is active with AHU in heating mode or OFF/Standby status.

The antifreeze alarm resets automatically.

Disposal

|  | The product needs to be disposed of separately in compliance with current regulations regarding the disposal of electric and electronic equipment, in the country where it is installed. |
| --- | --- |

|  | It is forbidden to dispose of the product or part of it in the environment. Improper disposal of the product could damage the environment and/or persons. |
| --- | --- |

Safety Information

Before You Begin

General

The products specified in this document have been tested under actual service conditions. Of course, your specific application requirements may be different from those assumed for this and any related examples described herein. In that case, you will have to adapt the information provided in this and other related documents to your particular needs. To do so, you will need to consult the specific product documentation of the hardware and/or software components that you may add or substitute for any examples specified in this documentation. Pay particular attention and conform to any safety information, different electrical requirements and normative standards that would apply to your adaptation.

© 2019 Schneider Electric. All rights reserved.

|  | WARNING: REGULATORY INCOMPATIBILITY Be sure that all equipment applied and systems designed comply with all applicable local, regional and national regulations and standards. Failure to follow these instructions can result in death, serious injury, or equipment damage. |
| --- | --- |

Note

Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material. A qualified person is one who has skills and knowledge related to the construction and operation of electrical equipment and its installation, and has received safety training to recognize and avoid the hazards involved. Failure to observe this information can result in injury or equipment damage.

The use and application of the information contained herein require expertise in the design and programming of automated control systems. Only the user or integrator can be aware of all the conditions and factors present during installation and setup, operation, and maintenance of the machine or process, and can therefore determine the automation and associated equipment and the related safeties and interlocks which can be effectively and properly used. When selecting automation and control equipment, and any other related equipment or software, for a particular application, the user or integrator must also consider any applicable local, regional or national standards and/or regulations.

Some of the major software functions and/or hardware components used in the proposed architectures and examples described in this document cannot be substituted without significantly compromising the performance of your application. Further, any such substitutions or alterations may completely invalidate any proposed architectures, descriptions, examples, instructions, wiring diagrams and/or compatibilities between the various hardware components and software functions specified herein and in related documentation. You must be aware of the consequences of any modifications, additions or substitutions.

A residual risk, as defined by EN/ISO 12100-1, Article 5, will remain if:

- it is necessary to modify the recommended logic and if the added or modified components are not properly integrated in the control circuit;

- you do not follow the required standards applicable to the operation of the machine, or if the adjustments to and the maintenance of the machine are not properly made (it is essential to strictly follow the prescribed machine maintenance schedule);

- the devices connected to any safety outputs do not have mechanically-linked contacts.

|  | CAUTION: EQUIPMENT INCOMPATIBILITY Read and thoroughly understand all device and software documentation before attempting any component substitutions or other changes related to the application examples provided in the document. Failure to follow these instructions can result in injury, or equipment damage. |
| --- | --- |

Start-Up and Test

Before using electrical control and automation equipment after design and installation, the application and associated functional safety system must be subjected to a start-up test by qualified personnel to verify correct operation of the equipment. It is important that arrangements for such testing be made and that enough time is allowed to perform complete and satisfactory testing.

|  | CAUTION: EQUIPMENT OPERATION HAZARD - Verify that all installation and set up procedures have been completed. - Before operational tests are performed, remove all blocks or other temporary holding means used for shipment from all component devices. - Remove tools, meters, and debris from equipment. Failure to follow these instructions can result in injury, or equipment damage. |
| --- | --- |

Verify that the completed system, including the functional safety system, is free from all short circuits and grounds, except those grounds installed according to local regulations. If high-potential voltage testing is necessary, follow the recommendations in equipment documentation to help prevent injury or equipment damage.

Operations and Adjustments

Regardless of the care exercised in the design and manufacture of equipment or in the selection and ratings of components, there are hazards that can be encountered if such equipment is improperly installed and operated.

In some applications, such as packaging machinery, additional operator protection such as point-of-operation guarding must be provided. This is necessary if the hands and other parts of the body are free to enter the pinch points or other hazardous areas where serious injury can occur. Software products alone cannot protect an operator from injury. For this reason, the software cannot be substituted for or take the place of point-of-operation protection.

|  | WARNING: UNGUARDED MACHINERY CAN CAUSE SERIOUS INJURY - Do not use this software and related automation equipment on equipment which does not have point-of -operation protection. - Do not reach into machinery during operation. Failure to follow these instructions can result in death, serious injury, or equipment damage. |
| --- | --- |

Ensure that appropriate safeties and mechanical/electrical interlocks related to point-of-operation protection have been installed and are operational before placing the equipment into service. All interlocks and safeties related to point-of-operation protection must be coordinated with the related automation equipment and software programming.

Note

Coordination of safeties and mechanical/electrical interlocks for point-of-operation protection is outside the scope of the examples and implementations suggested herein. It is sometimes possible to adjust the equipment incorrectly and this produce unsatisfactory or unsafe operation. Always use the manufacturer instructions as a guide to functional adjustments. Personnel who have access to these adjustments must be familiar with the equipment manufacturer instructions and the machinery used with the electrical equipment.

Only those operational adjustments actually required by the machine operator should be accessible to the operator. Access to other controls should be restricted to help prevent unauthorized changes in operating characteristics.

Wiring diagram

Fig 22 - Wiring diagram

Modbus Tables

NOTE: In the following tables:

in the case of XXX.Y format, divide by 10 the value found in the relative register

in the case of XXX.YY format, divide by 100 the value found in the relative register.

Modbus EEProm table

The following table describes the EEProm parameters.

| Modbus Register | Name | Device type | Def | Min | Max | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 16384 | PSW1 | Unsigned 16-bit | 10 | — | — | — | — | Level 1 Password |
| 16385 | PSW2 | Unsigned 16-bit | 65315 | — | — | — | %x | Level 2 Password |
| 16386 | cfgFans | 0=Supply; 1=Supply+Return | 0 | 0 | 1 | — | — | OEM: Fan Sections |
| 16387 | cfgFanType | 0=On Off; 1=Modulating; 2=On Off Backup; 3=Modulating Backup; 4=ATV; 5=ATV Backup; 6=EBM; 7=EBM Backup; 8=Ziehl; 9=Ziehl Backup | 0 | 0 | 9 | — | — | OEM: Fan Type |
| 16388 | cfgFanRegulation | 0=Fixed Speed; 1=Air Quality; 2=Pressure 1 Probe; 3=Pressure 2 Probes | 0 | 0 | 3 | — | — | OEM: Fan Regulator |
| 16389 | cfgFanAlarm | 0=Thermal/Digital Protection; 1=Digital+Flowswitch | 0 | 0 | 1 | — | — | OEM: Fan Alarm Selection |
| 16390 | cfgCoolHeatModules | 0=None; 1=Cool; 2=Heat; 3=Cool+Heat; 4=Cool/Heat Single out | 0 | 0 | 4 | — | — | OEM: Heating Cooling Enable |
| 16391 | cfgCooling | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | — | — | OEM: Cooling Actuator Selection |
| 16392 | cfgHeating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Heating Actuator Selection |
| 16393 | cfgCooling_Heating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | — | — | OEM: Cooling+Heating Actuator Selection |
| 16394 | cfgPreHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Preheater Selection |
| 16395 | cfgPostHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Postheater Selection |
| 16396 | cfgAntifreeze | 0=None; 1=On Off; 2=NTC | 0 | 0 | 2 | — | — | OEM: Antifreeze Selection |
| 16397 | cfgHeatRecovery | 0=None/Not Regulated; 1=Bypass On Off; 2=Bypass Mod; 3=Rotary On Off; 4=Rotary Mod; 5=Exchanger On Off; 6=Exchanger Mod | 0 | 0 | 6 | — | — | OEM: Heat Recovery Selection |
| 16398 | cfgDefrostHeatRec | 0=None; 1=Supply Fans; 2=Preheating | 0 | 0 | 2 | — | — | OEM: Defrost Regulation Selection |
| 16399 | cfgDampers | 0=None; 1=External On Off; 2=External + Mix Mod | 1 | 0 | 2 | — | — | OEM: External Dampers Selection |
| 16400 | cfgHumidifier | 0=None; 1=On Off; 2=Modulating | 0 | 0 | 2 | — | — | OEM: Humidifier Selection |
| 16401 | cfgDeHumidifier | 0=None; 1=Standard; 2=Dew Point; 3=Standard+Winter; 4=Dew Point+Winter | 0 | 0 | 4 | — | — | OEM: Dehumification Regulator |
| 16402 | cfgDampersForFans | 0=None; 1=Supply; 2=Return; 3=Supply+Return | 0 | 0 | 3 | — | — | OEM: Dampers for fam Selection |
| 16403 | cfgAirQuality | 0=None; 1=CO2; 2=VOC; 3=CO2+VOC | 0 | 0 | 3 | — | — | OEM: Air Quality Probe Selection |
| 16404 | cfgFilterPressostat | Unsigned 8-bit | 0 | 0 | 4 | — | — | OEM: Number of filter pressostat |
| 16405 | cfgDoorDI | Boolean | 0 | — | — | — | — | OEM: Door Input Enable |
| 16406 | cfgModeDI | Boolean | 0 | — | — | — | — | OEM: Unit Mode Input Enable |
| 16407 | cfgModeDO | Boolean | 0 | — | — | — | — | OEM: Unit Mode Output Enable |
| 16408 | cfgCoolHeat_NumSteps | 0=1 Cond Unit – AO 1=1 Cond Unit - 1 Step+AO 2=1 Cond Unit - 2 Steps 3=1 Cond Unit - 3 Steps 4=1 Cond Unit - 4 Steps 16=2 Cond Units 32=3 Cond Units 64=4 Cond Units | 0 | 0 | 48 | — | — | OEM: Condensing Unit Steps |
| 16409 | cfgHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Heater Steps |
| 16410 | cfgPreHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Pre Heater Steps |
| 16411 | cfgPostHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Post Heater Steps |
| 16412 | cfgMixChamberBeforePreHeat | Boolean | 0 | — | — | — | — | OEM: If enabled dampers closed with PreAntifreeze and Defrost with PreHeating |
| 16413 | cfgEE_free2 | Signed 16-bit | 0 | — | — | — | — | — |
| 16414 | cfgEE_free3 | Signed 16-bit | 0 | — | — | — | — | — |
| 16415 | cfgEE_free4 | Signed 16-bit | 0 | — | — | — | — | — |
| 16416 | cfgEE_free5 | Signed 16-bit | 0 | — | — | — | — | — |
| 16417 | cfgEE_free6 | Signed 16-bit | 0 | — | — | — | — | — |
| 16418 | cfgEE_free7 | Signed 16-bit | 0 | — | — | — | — | — |
| 16419 | cfgEE_free8 | Signed 16-bit | 0 | — | — | — | — | — |
| 16420 | ioEE_base_AI_01 | -1 = -1=Not Used; 0=Supply Temp.; 1=Return Temp.; 2=External Temp.; 3=Expulsion Temp.; 4=Preheat Temp.; 5=Saturation Temp.; 6=Antifreeze; 7=Air Quality CO2; 8=Air Quality VOC; 9=Pressure 1; 10=Pressure 2; 11=Supply Hum.; 12=Return Hum.; 13=External Hum.; 14=Flow Tuning 1; 15=Flow Tuning 2 | 0 | -1 | 15 | — | — | Saved Logic Allocation of the physical input |
| 16421 | ioEE_base_AI_02 | See ioEE_base_AI_01 | 1 | -1 | 15 | — | — | — |
| 16422 | ioEE_base_AI_03 | See ioEE_base_AI_01 | 2 | -1 | 15 | — | — | — |
| 16423 | ioEE_base_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16424 | ioEE_base_AI_05 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16425 | ioEE_base_AI_06 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16426 | ioEE_base_AI_07 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16427 | ioEE_base_AI_08 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16428 | ioEE_base_AI_09 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16429 | ioEE_base_AI_10 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16430 | ioEE_base_AI_11 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16431 | ioEE_base_AI_12 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16432 | ioEE_exp1_AI_01 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16433 | ioEE_exp1_AI_02 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16434 | ioEE_exp1_AI_03 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16435 | ioEE_exp1_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16436 | ioEE_exp2_AI_01 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16437 | ioEE_exp2_AI_02 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16438 | ioEE_exp2_AI_03 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16439 | ioEE_exp2_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16440 | ioEE_free1 | Signed 16-bit | 0 | — | — | — | — | — |
| 16441 | ioEE_free2 | Signed 16-bit | 0 | — | — | — | — | — |
| 16442 | ioEE_free3 | Signed 16-bit | 0 | — | — | — | — | — |
| 16443 | ioEE_free4 | Signed 16-bit | 0 | — | — | — | — | — |
| 16444 | ioEE_free5 | Signed 16-bit | 0 | — | — | — | — | — |
| 16445 | ioEE_free6 | Signed 16-bit | 0 | — | — | — | — | — |
| 16446 | ioEE_free7 | Signed 16-bit | 0 | — | — | — | — | — |
| 16447 | ioEE_free8 | Signed 16-bit | 0 | — | — | — | — | — |
| 16448 | ioEE_base_DI_01 | -1 = Not Used; 0=Supply Fan Th.Prot.; 1=Return Fan Th.Prot.; 2=On Off; 3=Fire Alarm; 4=Mode; 5=Door; 6=Antifreeze Alarm; 7=Airflow Alarm Supply; 8=Airflow Alarm Return; 9=Humidifier Alarm; 10=Pre Heater A 11=Post Heater Alarm 12=Rotary Heat Exch. Alarm 13=Filter 1 Alarm 14=Filter 2 Alarm 15=Filter 3 Alarm 16=Filter 4 Alarm 17=Supply Fan 2 Th.Prot. 18=Return Fan 2 Th.Prot. 19=Supply Fan 2 Airflow Alarm 20=Return Fan 2 Airflow Alarm 21=Cond. Unit Alarm 22=Heater Alarm 23=Cond. Unit 2 Alarm 24=Cond. Unit 3 Alarm 25=Cond. Unit 4 Alarm 26=Cond. Unit 1 Defrost 27=Cond. Unit 2 Defrost 28=Cond. Unit 3 Defrost 29=Cond. Unit 4 Defrost 30=Filter 5 Alarm | 2 | -1 | 30 | — | — | — |
| 16449 | ioEE_base_DI_02 | See ioEE_base_DI_01 | 3 | -1 | 10 | — | — | — |
| 16450 | ioEE_base_DI_03 | See ioEE_base_DI_01 | 0 | -1 | 10 | — | — | — |
| 16451 | ioEE_base_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16452 | ioEE_base_DI_05 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16453 | ioEE_base_DI_06 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16454 | ioEE_base_DI_07 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16455 | ioEE_base_DI_08 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16456 | ioEE_base_DI_09 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16457 | ioEE_base_DI_10 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16458 | ioEE_base_DI_11 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16459 | ioEE_base_DI_12 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16460 | ioEE_exp1_DI_01 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16461 | ioEE_exp1_DI_02 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16462 | ioEE_exp1_DI_03 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16463 | ioEE_exp1_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16464 | ioEE_exp2_DI_01 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16465 | ioEE_exp2_DI_02 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16466 | ioEE_exp2_DI_03 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16467 | ioEE_exp2_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16468 | ioEE_free9 | Signed 16-bit | 0 | — | — | — | — | — |
| 16469 | ioEE_free10 | Signed 16-bit | 0 | — | — | — | — | — |
| 16470 | ioEE_free11 | Signed 16-bit | 0 | — | — | — | — | — |
| 16471 | ioEE_free12 | Signed 16-bit | 0 | — | — | — | — | — |
| 16472 | ioEE_free13 | Signed 16-bit | 0 | — | — | — | — | — |
| 16473 | ioEE_free14 | Signed 16-bit | 0 | — | — | — | — | — |
| 16474 | ioEE_free15 | Signed 16-bit | 0 | — | — | — | — | — |
| 16475 | ioEE_free16 | Signed 16-bit | 0 | — | — | — | — | — |
| 16476 | ioEE_base_DO_01 | -1 = -1=Not Used; 0=Supply Fan; 1=Return Fan; 2=On Off; 3=Alarm; 4=Mode; 5=Ext. Dampers; 6=Bypass Damper; 7=Supply Damper; 8=Return Damper; 9=Pump Preheat; 10=Pump Postheat; 11=Cool / Cool-Heat Pump; 12=Cool / Cool-Heat Step 1 or Cond.Unit 1; 13=Cool / Cool-Heat Step 2 or Cond.Unit 2; 14=Cool / Cool-Heat Step 3 or Cond.Unit 3; 15=Cool / Cool-Heat Step 4 or Cond.Unit 4; 16=Heat Pump; 17=Heater Step 1; 18=Heater Step 2; 19=Heater Step 3; 20=Pre Heater Step 1; 21=Pre Heater Step 2; 22=Pre Heater Step 3; 23=Post Heater Step 1; 24=Post Heater Step 2; 25=Post Heater Step 3; 26=Humidifier; 27=Recovery; 28=Supply Fan 2; 29=Return Fan 2; 30=Supply Damper 2; 31=Return Damper 2 | 2 | -1 | 31 | — | — | Saved Logic Allocation of the physical output |
| 16477 | ioEE_base_DO_02 | See ioEE_base_DO_01 | 3 | -1 | 31 | — | — | — |
| 16478 | ioEE_base_DO_03 | See ioEE_base_DO_01 | 0 | -1 | 31 | — | — | — |
| 16479 | ioEE_base_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16480 | ioEE_base_DO_05 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16481 | ioEE_base_DO_06 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16482 | ioEE_base_DO_07 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16483 | ioEE_base_DO_08 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16484 | ioEE_base_DO_09 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16485 | ioEE_base_DO_10 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16486 | ioEE_base_DO_11 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16487 | ioEE_base_DO_12 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16488 | ioEE_exp1_DO_01 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16489 | ioEE_exp1_DO_02 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16490 | ioEE_exp1_DO_03 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16491 | ioEE_exp1_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16492 | ioEE_exp2_DO_01 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16493 | ioEE_exp2_DO_02 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16494 | ioEE_exp2_DO_03 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16495 | ioEE_exp2_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16496 | ioEE_free17 | Signed 16-bit | 0 | — | — | — | — | — |
| 16497 | ioEE_free18 | Signed 16-bit | 0 | — | — | — | — | — |
| 16498 | ioEE_free19 | Signed 16-bit | 0 | — | — | — | — | — |
| 16499 | ioEE_free20 | Signed 16-bit | 0 | — | — | — | — | — |
| 16500 | ioEE_free21 | Signed 16-bit | 0 | — | — | — | — | — |
| 16501 | ioEE_free22 | Signed 16-bit | 0 | — | — | — | — | — |
| 16502 | ioEE_free23 | Signed 16-bit | 0 | — | — | — | — | — |
| 16503 | ioEE_free24 | Signed 16-bit | 0 | — | — | — | — | — |
| 16504 | ioEE_base_AO_01 | -1 = -1=Not Used; 0=Supply Fan; 1=Return Fan; 2=Ext. Dampers; 3=Byp. Damper; 4=Cool / Cool-Heat; 5=Heat; 6=Pre Heater; 7=Post Heater; 8=Recovery; 9=Humidifier | -1 | -1 | 9 | — | — | — |
| 16505 | ioEE_base_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16506 | ioEE_base_AO_03 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16507 | ioEE_base_AO_04 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16508 | ioEE_base_AO_05 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16509 | ioEE_base_AO_06 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16510 | ioEE_exp1_AO_01 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16511 | ioEE_exp1_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16512 | ioEE_exp2_AO_01 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16513 | ioEE_exp2_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16514 | ioEE_free25 | Signed 16-bit | 0 | — | — | — | — | — |
| 16515 | ioEE_free26 | Signed 16-bit | 0 | — | — | — | — | — |
| 16516 | ioEE_free27 | Signed 16-bit | 0 | — | — | — | — | — |
| 16517 | ioEE_free28 | Signed 16-bit | 0 | — | — | — | — | — |
| 16518 | ioEE_free29 | Signed 16-bit | 0 | — | — | — | — | — |
| 16519 | ioEE_free30 | Signed 16-bit | 0 | — | — | — | — | — |
| 16520 | ioEE_free31 | Signed 16-bit | 0 | — | — | — | — | — |
| 16521 | ioEE_free32 | Signed 16-bit | 0 | — | — | — | — | — |
| 16522 | Cfg_exp1_AI1 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16523 | Cfg_exp1_AI2 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16524 | Cfg_exp1_AI3 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16525 | Cfg_exp1_AI4 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16526 | Cfg_exp2_AI1 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16527 | Cfg_exp2_AI2 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16528 | Cfg_exp2_AI3 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16529 | Cfg_exp2_AI4 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16530 | ioEE_free33 | Signed 16-bit | 0 | — | — | — | — | — |
| 16531 | ioEE_free34 | Signed 16-bit | 0 | — | — | — | — | — |
| 16532 | ioEE_free35 | Signed 16-bit | 0 | — | — | — | — | — |
| 16533 | ioEE_free36 | Signed 16-bit | 0 | — | — | — | — | — |
| 16534 | ioEE_free37 | Signed 16-bit | 0 | — | — | — | — | — |
| 16535 | ioEE_free38 | Signed 16-bit | 0 | — | — | — | — | — |
| 16536 | ioEE_free39 | Signed 16-bit | 0 | — | — | — | — | — |
| 16537 | ioEE_free40 | Signed 16-bit | 0 | — | — | — | — | — |
| 16538 | FullScaleMin_exp1_AI1 | Signed 16-bit | -500 | -500 | -500 | — | — | Saved: AI probe configuration |
| 16539 | FullScaleMax_exp1_AI1 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16540 | FullScaleMin_exp1_AI2 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16541 | FullScaleMax_exp1_AI2 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16542 | FullScaleMin_exp1_AI3 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16543 | FullScaleMax_exp1_AI3 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16544 | FullScaleMin_exp1_AI4 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16545 | FullScaleMax_exp1_AI4 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16546 | FullScaleMin_exp2_AI1 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16547 | FullScaleMax_exp2_AI1 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16548 | FullScaleMin_exp2_AI2 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16549 | FullScaleMax_exp2_AI2 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16550 | FullScaleMin_exp2_AI3 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16551 | FullScaleMax_exp2_AI3 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16552 | FullScaleMin_exp2_AI4 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16553 | FullScaleMax_exp2_AI4 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16554 | ioEE_free41 | Signed 16-bit | 0 | — | — | — | — | — |
| 16555 | ioEE_free42 | Signed 16-bit | 0 | — | — | — | — | — |
| 16556 | ioEE_free43 | Signed 16-bit | 0 | — | — | — | — | — |
| 16557 | ioEE_free44 | Signed 16-bit | 0 | — | — | — | — | — |
| 16558 | ioEE_free45 | Signed 16-bit | 0 | — | — | — | — | — |
| 16559 | ioEE_free46 | Signed 16-bit | 0 | — | — | — | — | — |
| 16560 | ioEE_free47 | Signed 16-bit | 0 | — | — | — | — | — |
| 16561 | ioEE_free48 | Signed 16-bit | 0 | — | — | — | — | — |
| 16562 | ioEE_free57 | Signed 16-bit | 0 | — | — | — | — | — |
| 16563 | ioEE_free58 | Signed 16-bit | 0 | — | — | — | — | — |
| 16564 | ioEE_free59 | Signed 16-bit | 0 | — | — | — | — | — |
| 16565 | ioEE_free60 | Signed 16-bit | 0 | — | — | — | — | — |
| 16566 | ioEE_free61 | Signed 16-bit | 0 | — | — | — | — | — |
| 16567 | ioEE_free62 | Signed 16-bit | 0 | — | — | — | — | — |
| 16568 | ioEE_free63 | Signed 16-bit | 0 | — | — | — | — | — |
| 16569 | ioEE_free64 | Signed 16-bit | 0 | — | — | — | — | — |
| 16570 | Calibration_exp1_AI1 | Signed 16-bit | 0 | -1000 | 1000 | — | — | Offset of expansions AI |
| 16571 | Calibration_exp1_AI2 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16572 | Calibration_exp1_AI3 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16573 | Calibration_exp1_AI4 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16574 | Calibration_exp2_AI1 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16575 | Calibration_exp2_AI2 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16576 | Calibration_exp2_AI3 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16577 | Calibration_exp2_AI4 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16578 | ioEE_free49 | Signed 16-bit | 0 | — | — | — | — | — |
| 16579 | ioEE_free50 | Signed 16-bit | 0 | — | — | — | — | — |
| 16580 | ioEE_free51 | Signed 16-bit | 0 | — | — | — | — | — |
| 16581 | ioEE_free52 | Signed 16-bit | 0 | — | — | — | — | — |
| 16582 | ioEE_free53 | Signed 16-bit | 0 | — | — | — | — | — |
| 16583 | ioEE_free54 | Signed 16-bit | 0 | — | — | — | — | — |
| 16584 | ioEE_free55 | Signed 16-bit | 0 | — | — | — | — | — |
| 16585 | ioEE_free56 | Signed 16-bit | 0 | — | — | — | — | — |
| 16586 | DI_Polarity_LogicIndex_0 | 0 = 0V = Off, 24V = On/Alarm; 1 = 0V = On/Alarm, 24V = Off | 1 | 0 | 1 | — | — | Polarity - Supply Fan Thermal |
| 16587 | DI_Polarity_LogicIndex_1 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return Fan Thermal |
| 16588 | DI_Polarity_LogicIndex_2 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - On/Off Input |
| 16589 | DI_Polarity_LogicIndex_3 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Fire Alarm |
| 16590 | DI_Polarity_LogicIndex_4 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Mode Input |
| 16591 | DI_Polarity_LogicIndex_5 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Door |
| 16592 | DI_Polarity_LogicIndex_6 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Antifreeze |
| 16593 | DI_Polarity_LogicIndex_7 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply Airflow |
| 16594 | DI_Polarity_LogicIndex_8 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return Airflow |
| 16595 | DI_Polarity_LogicIndex_9 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Humidifier Alarm |
| 16596 | DI_Polarity_LogicIndex_10 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Preheater Alarm |
| 16597 | DI_Polarity_LogicIndex_11 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Postheater Alarm |
| 16598 | DI_Polarity_LogicIndex_12 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Rotary Wheel Alarm |
| 16599 | DI_Polarity_LogicIndex_13 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 1 Alarm |
| 16600 | DI_Polarity_LogicIndex_14 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 2 Alarm |
| 16601 | DI_Polarity_LogicIndex_15 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 3 Alarm |
| 16602 | DI_Polarity_LogicIndex_16 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 4 Alarm |
| 16603 | DI_Polarity_LogicIndex_17 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply 2 Fan Th. |
| 16604 | DI_Polarity_LogicIndex_18 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return 2 Fan Th. |
| 16605 | DI_Polarity_LogicIndex_19 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply 2 Airflow |
| 16606 | DI_Polarity_LogicIndex_20 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return 2 Airflow |
| 16607 | DI_Polarity_LogicIndex_21 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Cond. Unit Alarm |
| 16608 | DI_Polarity_LogicIndex_22 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - El. Heater Alarm |
| 16609 | DI_Polarity_LogicIndex_26_29 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Cond. Unit Defrost |
| 16610 | DI_Polarity_LogicIndex_30 | Signed 16-bit | 1 | 0 | 1 | — | — | Polarity - Filter 5 Alarm |
| 16611 | ioEE_free69 | Signed 16-bit | 0 | — | — | — | — | — |
| 16612 | ioEE_free70 | Signed 16-bit | 0 | — | — | — | — | — |
| 16613 | ioEE_free71 | Signed 16-bit | 0 | — | — | — | — | — |
| 16614 | ioEE_free72 | Signed 16-bit | 0 | — | — | — | — | — |
| 16615 | DO_Polarity_LogicIndex_0 | 0=NO; 1=NC | 0 | 0 | 1 | — | — | Supply Fan - DO Polarity |
| 16616 | DO_Polarity_LogicIndex_1 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Fan - DO Polarity |
| 16617 | DO_Polarity_LogicIndex_2 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | On Off - DO Polarity |
| 16618 | DO_Polarity_LogicIndex_3 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Alarm - DO Polarity |
| 16619 | DO_Polarity_LogicIndex_4 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Mode - DO Polarity |
| 16620 | DO_Polarity_LogicIndex_5 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Ext. Dampers - DO Polarity |
| 16621 | DO_Polarity_LogicIndex_6 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Bypass Damper - DO Polarity |
| 16622 | DO_Polarity_LogicIndex_7 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Damper - DO Polarity |
| 16623 | DO_Polarity_LogicIndex_8 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Damper - DO Polarity |
| 16624 | DO_Polarity_LogicIndex_9 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump Preheat - DO Polarity |
| 16625 | DO_Polarity_LogicIndex_10 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump Postheat - DO Polarity |
| 16626 | DO_Polarity_LogicIndex_11 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Pump - DO Polarity |
| 16627 | DO_Polarity_LogicIndex_12 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 1 - DO Polarity |
| 16628 | DO_Polarity_LogicIndex_13 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 2 - DO Polarity |
| 16629 | DO_Polarity_LogicIndex_14 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 3 - DO Polarity |
| 16630 | DO_Polarity_LogicIndex_15 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 4 - DO Polarity |
| 16631 | DO_Polarity_LogicIndex_16 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump heat - DO Polarity |
| 16632 | DO_Polarity_LogicIndex_17 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 1 - DO Polarity |
| 16633 | DO_Polarity_LogicIndex_18 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 2 - DO Polarity |
| 16634 | DO_Polarity_LogicIndex_19 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 3 - DO Polarity |
| 16635 | DO_Polarity_LogicIndex_20 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 1 - DO Polarity |
| 16636 | DO_Polarity_LogicIndex_21 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 2 - DO Polarity |
| 16637 | DO_Polarity_LogicIndex_22 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 3 - DO Polarity |
| 16638 | DO_Polarity_LogicIndex_23 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 1 - DO Polarity |
| 16639 | DO_Polarity_LogicIndex_24 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 2 - DO Polarity |
| 16640 | DO_Polarity_LogicIndex_25 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 3 - DO Polarity |
| 16641 | DO_Polarity_LogicIndex_27 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Humidifier - DO Polarity |
| 16642 | DO_Polarity_LogicIndex_26 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Recovery - DO Polarity |
| 16643 | DO_Polarity_LogicIndex_28 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Fan 2 - DO Polarity |
| 16644 | DO_Polarity_LogicIndex_29 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Fan 2 - DO Polarity |
| 16645 | DO_Polarity_LogicIndex_30 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Damper 2 - DO Polarity |
| 16646 | DO_Polarity_LogicIndex_31 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Damper 2 - DO Polarity |
| 16647 | ioEE_free73 | Signed 16-bit | 0 | — | — | — | — | — |
| 16648 | ioEE_free74 | Signed 16-bit | 0 | — | — | — | — | — |
| 16649 | ioEE_free75 | Signed 16-bit | 0 | — | — | — | — | — |
| 16650 | ioEE_free76 | Signed 16-bit | 0 | — | — | — | — | — |
| 16651 | ioEE_free77 | Signed 16-bit | 0 | — | — | — | — | — |
| 16652 | ioEE_free78 | Signed 16-bit | 0 | — | — | — | — | — |
| 16653 | ioEE_free79 | Signed 16-bit | 0 | — | — | — | — | — |
| 16654 | ioEE_free80 | Signed 16-bit | 0 | — | — | — | — | — |
| 16700 | BACNET_ENABLE | Boolean | 1 | — | — | — | — | Bacnet Protocol Enable |
| 16701 | BACNET_ID | Unsigned 16-bit | 1 | 1 |  | — | — | Bacnet Device ID |
| 16702 | BACNET_BBMD_Ip1 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16703 | BACNET_BBMD_Ip2 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16704 | BACNET_BBMD_Ip3 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16705 | BACNET_BBMD_Ip4 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16706 | BACNET_BBMD_TMO | Unsigned 16-bit | 60 | — | — | sec | — | BBMD Timeout - Foreing Devices Handling |
| 16707 | BACNET_BBMD_PORT | Unsigned 16-bit | 0 | — | — | — | — | BBMD Port - Foreing Devices Handling |
| 16708 | BACNET_SUBNET | Unsigned 8-bit | 0 | 0 | 63 |  |  | Bacnet Device Subnet |
| 16710 | WEB_User_E2 | String | administrator | — | — | — | — | Web User ID |
| 16719 | WEB_PSW_E2 | String | password | — | — | — | — | Web Psw ID |
| 16730 | DayLight_Region | 0=Europe; 1=USA/Canada | 0 | 0 | 1 | — | — | Day Light Region |
| 16731 | DayLight_Enable | Boolean | 1 | — | — | — | — | Day Light Enable |
| 16740 | Unit_ForceOffAfterReboot | Boolean | 0 | — | — | — | — | Force Off keyboard after reboot |
| 16741 | Unit_RegTempType | 0=Supply; 1=Return Direct; 2=Return Cascade | 1 | 0 | 2 | — | — | Temperature Regulation Probe |
| 16742 | SP_T_MIN | Signed 16-bit | 140 | — | SP_T_MAX | °C | XXX.Y | Minimum Temperature Setpoint |
| 16743 | SP_T_MAX | Signed 16-bit | 300 | SP_T_MIN | — | °C | XXX.Y | Maximum Temperature Setpoint |
| 16744 | SP_T_Auto_E2 | Signed 16-bit | 240 | SP_T_MIN | SP_T_MAX | °C | XXX.Y | Setpoint Auto |
| 16745 | DIFF_T_AutoChangeMode | Signed 16-bit | 20 | 5 | — | °C | XXX.Y | Differential Change season (AUTO) |
| 16746 | DIFF_T_AutoEco | Signed 16-bit | 20 | 0 | — | °C | XXX.Y | Differential Economy Mode - Half Band (AUTO) |
| 16747 | SP_T_FORCESUMMER | Signed 16-bit | 240 | — | — | °C | XXX.Y | Force Summer Mode (AUTO) |
| 16748 | SP_T_FORCEWINTER | Signed 16-bit | 160 | — | — | °C | XXX.Y | Force Winter Mode (AUTO) |
| 16749 | SP_T_Cool_E2 | Signed 16-bit | 260 | SP_T_Heat_E2 | SP_T_MAX | °C | XXX.Y | Setpoint Cooling |
| 16750 | SP_T_Heat_E2 | Signed 16-bit | 200 | SP_T_MIN | SP_T_Cool_E2 | °C | XXX.Y | Setpoint Heating |
| 16751 | SP_T_CoolEco_E2 | Signed 16-bit | 280 | SP_T_Cool_E2 | SP_T_MAX | °C | XXX.Y | Setpoint Cooling Economy |
| 16752 | SP_T_HeatEco_E2 | Signed 16-bit | 180 | SP_T_MIN | SP_T_Heat_E2 | °C | XXX.Y | Setpoint Heating Economy |
| 16753 | SP_RH_MinSetpoint | Signed 16-bit | 30 | 20 | SP_RH_MaxSetpoint | %R.H. | — | Minimum relative humidity setpoint |
| 16754 | SP_RH_MaxSetpoint | Signed 16-bit | 90 | SP_RH_MinSetpoint | 100 | %R.H. | — | Maximum relative humidity setpoint |
| 16755 | SP_RH_DehumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Dehumidication setpoint (comfort) |
| 16756 | SP_RH_DehumidificationSetpointEco_E2 | Signed 16-bit | 55 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Dehumidication setpoint (eco) |
| 16757 | SP_RH_HumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Humidification setpoint (comfort) |
| 16758 | SP_RH_HumidificationSetpointEco_E2 | Signed 16-bit | 45 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Humidification setpoint (eco) |
| 16759 | SP_VOC_E2 | Signed 16-bit | 40 | 0 | 100 | % | — | VOC Air quality setpoint |
| 16760 | SP_CO2_E2 | Signed 16-bit | 800 | 0 | 2000 | ppm | — | CO2 Air quality setpoint |
| 16770 | cfgFreeCooling | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | — | FreeCooling Enable |
| 16771 | cfgFreeHeating | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | — | FreeHeating Enable |
| 16772 | FreeCHMinExtTemp | Signed 16-bit | 120 | -200 | 200 | °C | XXX.Y | Free Cooling/Heating Minimum External Temperature |
| 16773 | FreeCHBand | Signed 16-bit | 50 | 10 | 100 | °C | XXX.Y | Free Cooling/Heating Proportional Band (direct return reg) |
| 16774 | FreeCHTimeout | Unsigned 16-bit | 60 | 0 | 180 | min | — | Free Cooling/Heating Timeout |
| 16775 | FreeCHDiff | Signed 16-bit | 50 | 10 | 100 | °C | XXX.Y | Free Cooling/Heating Outside Regulation Differential |
| 16776 | FreeCHHyst | Signed 16-bit | 10 | 2 | 50 | °C | XXX.Y | Free Cooling/Heating Hysteresis |
| 16780 | cfgFireAlarm | 0=Off All; 1=All Fans-Damper On; 2=ReturnFan-Damper On | 0 | 0 | 2 | — | — | Fire Alarm Configuration |
| 16781 | FireTempSet | Signed 16-bit | 950 | 900 | — | °C | XXX.Y | Setpoint Temperature for Fire Alarm |
| 16782 | Alm_MinHumiditySens | Signed 16-bit | 20 | 0 | 1000 | %R.H. | XXX.Y | Minimum Valid Humidity Value |
| 16783 | Alm_MinVOCSens | Signed 16-bit | 20 | 0 | 1000 | % | XXX.Y | Minimum Valid VOC Value |
| 16784 | Alm_MinCO2Sens | Signed 16-bit | 40 | 0 | — | ppm | — | Minimum Valid CO2 Value |
| 16785 | Alm_MinPrSens | Signed 16-bit | 40 | 0 | — | pa | — | Minimum Valid Pr Value (Fans on) |
| 16786 | Alm_ActiveProbeBypass | Unsigned 16-bit | 30 | 0 | 600 | sec | — | Active Probe alarm bypass |
| 16787 | AFset | Signed 16-bit | 50 | -50 | 150 | °C | XXX.Y | Antifreeze Setpoint |
| 16788 | AFdiff | Signed 16-bit | 20 | 1 | 50 | °C | XXX.Y | Antifreeze Differential |
| 16789 | AFphtime | Unsigned 16-bit | 5 | 0 | 255 | min | — | Antifreeze Preheater time |
| 16800 | ExtDamperOpenDelay | Unsigned 16-bit | 60 | — | — | sec | — | External/Fan Damper Open Time |
| 16801 | ExtDamperCloseDelay | Unsigned 16-bit | 60 | — | — | sec | — | External/Fan Damper Close Time |
| 16802 | ExtDamperMinOpen | Signed 16-bit | 50 | 0 | 100 | % | — | External Damper Minimum Open |
| 16803 | ExtDamperMaxOpen | Signed 16-bit | 100 | ExtDamperMinOpen | 100 | % | — | External Damper Maximum Open |
| 16820 | VOC_Bp | Unsigned 16-bit | 300 | 1 | — | % | XXX.Y | VOC Regulator: Prop. Band |
| 16821 | VOC_Ti | Unsigned 16-bit | 0 | — | — | sec | — | VOC Regulator: Integral Time |
| 16822 | CO2_Bp | Unsigned 16-bit | 400 | 1 | — | ppm | — | CO2 Regulator: Prop. Band |
| 16823 | CO2_Ti | Unsigned 16-bit | 0 | — | — | sec | — | CO2 Regulator: Integral Time |
| 16840 | Fan_MinimumSpeed | Signed 16-bit | 250 | 0 | 500 | % | XXX.Y | Fan Minimum Speed (Pressure Regulation and limit for other speed) |
| 16841 | Fan_LowSpeed | Signed 16-bit | 300 | Fan_MinimumSpeed | 800 | % | XXX.Y | Fan Low Speed (Start Phase/Night/Min Air Q. and Defrost Speed) |
| 16842 | Fan_NominalSpeed | Signed 16-bit | 900 | Fan_LowSpeed | 1000 | % | XXX.Y | Fan Nominal/Maximum Speed |
| 16843 | Fan_ReturnSpeedCorrection | Signed 16-bit | 0 | -500 | 500 | % | XXX.Y | Fan Return Output correction (not used with 2 pressure probes) |
| 16844 | Fan_PowerUp1_Time | Unsigned 16-bit | 30 | 0 | 255 | sec | — | Fan Power Up Time at Min Speed (with Heaters) |
| 16845 | Fan_PowerUp2_Time | Unsigned 16-bit | 10 | 0 | 255 | sec | — | Fan Power Up Time at Nom Speed (with Heaters) |
| 16846 | Fan_Post_Time | Unsigned 16-bit | 40 | 0 | 255 | sec | — | Fan Post Ventilation Time (with Heaters) |
| 16847 | Fan_PreHeating_Time | Unsigned 16-bit | 180 | 0 | 600 | sec | — | Fan Preheating Time (with heating valves) |
| 16848 | Fan_PreHeatOnSet | Signed 16-bit | -50 | -200 | 100 | °C | XXX.Y | External Temperature Set forcing preheating time |
| 16849 | Fan_Swap_Time | Unsigned 16-bit | 240 | 0 | 600 | hours | — | Fan swap time (0=Disabled) |
| 16850 | Fan_SwapPolicy | 0 = If available Start always Fans 1; 1 = Start Section with less working hours (Supply + Return); 2 = Start Fans with less working hours; 3 = Start Fans with less working hours keeping parallel sections | 0 | 0 | 3 | — | — | Fan swap policy |
| 16851 | Fan_SinglePressureReturn | Boolean | 0 | — | — | — | — | In case of a unique pressure probe mounted on return section and Supply+Return Fans |
| 16852 | Fan_AlrmPressBypass | Unsigned 16-bit | 30 | 1 | 600 | Sec | — | Flow Bypass |
| 16853 | Fan_SupplyAirflowAlrmByAi | Boolean | 0 | — | — | — | — | Enable supply flow alarm by probe (pressure probe must be already enabled) |
| 16854 | Fan_ReturnAirflowAlrmByAi | Boolean | 0 | — | — | — | — | Enable return flow alarm by probe (pressure probe must be already enabled) |
| 16855 | Fan_SetMinAirflow | Signed 16-bit | 50 | — | — | Pa | — | Fan Airflow Alarm setpoint |
| 16856 | FAN_Supply_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | — | Fan Supply Prop. Band Pressure |
| 16857 | FAN_Supply_TiP | Unsigned 16-bit | 75 | — | — | sec | — | Fan Supply Integral Time Pressure |
| 16858 | FAN_Supply_TdP | Unsigned 16-bit | 0 | — | — | sec | — | Fan Supply Derivative Time Pressure |
| 16859 | FAN_Return_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | — | Fan Return Prop. Band Pressure |
| 16860 | FAN_Return_TiP | Unsigned 16-bit | 75 | — | — | sec | — | Fan Return Integral Time Pressure |
| 16861 | FAN_Return_TdP | Unsigned 16-bit | 0 | — | — | sec | — | Fan Return Derivative Time Pressure |
| 16862 | Fan_K_Supply | Unsigned 16-bit | 100 | 1 | 3000 | — | — | Fan K Supply |
| 16863 | Fan_K_Return | Unsigned 16-bit | 100 | 1 | 3000 | — | — | Fan K Return |
| 16880 | Fan_Supply_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | — | Fan Supply Regulation Unit |
| 16881 | Fan_Return_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | — | Fan Return Regulation Unit |
| 16882 | Fan_Supply_SetMinPr | Signed 16-bit | 50 | — | — | Pa | — | Fan Supply Minimum/Night Pressure Setpoint |
| 16883 | Fan_Return_SetMinPr | Signed 16-bit | 50 | — | — | Pa | — | Fan Return Minimum/Night Pressure Setpoint |
| 16884 | Fan_SetPrSupply | Signed 16-bit | 100 | Fan_Supply_SetMinPr | Fan_Supply_SetMaxPr | Pa | — | Fan Supply Pressure Setpoint |
| 16885 | Fan_SetPrReturn | Signed 16-bit | 100 | Fan_Return_SetMinPr | Fan_Return_SetMaxPr | Pa | — | Fan Return Pressure Setpoint |
| 16886 | Fan_Supply_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | — | Fan Supply Maximum Pressure Setpoint |
| 16887 | Fan_Return_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | — | Fan Return Maximum Pressure Setpoint |
| 16888 | Fan_Supply_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | — | Fan Supply Minimum/Night Flow Setpoint |
| 16890 | Fan_Return_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | — | Fan Return Minimum/Night Flow Setpoint |
| 16892 | Fan_SetFlowSupply | Signed 32-bit | 100 | Fan_Supply_SetMinFlow | Fan_Supply_SetMaxFlow | m3/h | — | Fan Supply Flow Setpoint |
| 16894 | Fan_SetFlowReturn | Signed 32-bit | 100 | Fan_Return_SetMinFlow | Fan_Return_SetMaxFlow | m3/h | — | Fan Return Flow Setpoint |
| 16896 | Fan_Supply_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | — | Fan Supply Maximum Flow Setpoint |
| 16898 | Fan_Return_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | — | Fan Return Maximum Flow Setpoint |
| 16910 | SupplyDeltaUpHeating | Signed 16-bit | 160 | 5 | 400 | °C | XXX.Y | Heating Max Supply =RegSet+SupplyDeltaUpHeating |
| 16911 | SupplyDeltaDwHeating | Signed 16-bit | 20 | 0 | 50 | °C | XXX.Y | Heating Min Supply =RegSet-SupplyDeltaDwHeating |
| 16912 | SupplyDeltaUpCooling | Signed 16-bit | 10 | 5 | 50 | °C | XXX.Y | Cooling Max Supply =RegSet+SupplyDeltaUpCooling |
| 16913 | SupplyDeltaDwCooling | Signed 16-bit | 120 | 5 | 150 | °C | XXX.Y | Cooling Min Supply =RegSet-SupplyDeltaDwCooling |
| 16914 | Pb_Cooling | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Cooling Proportional Band |
| 16915 | Pb_Heating | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Heating Proportional Band |
| 16916 | Ti_Cooling | Unsigned 16-bit | 0 | 0 | — | sec | — | Cooling Integral Time |
| 16917 | Ti_Heating | Unsigned 16-bit | 0 | 0 | — | sec | — | Heating Integral Time |
| 16918 | Pb_ReturnCooling | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Return Temp. Reg: Cooling Proportional Band (only Cascade) |
| 16919 | Pb_ReturnHeating | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Return Temp. Reg: Heating Proportional Band (only Cascade) |
| 16920 | Ti_ReturnCooling | Unsigned 16-bit | 0 | 0 | — | sec | — | Return Temp. Reg: Cooling Integral Time (only Cascade) |
| 16921 | Ti_ReturnHeating | Unsigned 16-bit | 0 | 0 | — | sec | — | Return Temp. Reg: Heating Integral Time (only Cascade) |
| 16930 | Temp_HighSupplyEn | Boolean | 0 | — | — | — | — | Temperature High Supply Limit Enable (Winter) |
| 16931 | Temp_HighSupplySet | Signed 16-bit | 350 | 0 | 1000 | °C | XXX.Y | Temperature High Supply Limit Setpoint (Winter) |
| 16932 | Temp_HighSupplyBand | Signed 16-bit | 100 | 10 | 999 | °C | XXX.Y | Temperature High Supply Band (Winter) |
| 16933 | Temp_LowSupplyEn | Boolean | 0 | — | — | — | — | Temperature Low Supply Limit Enable (Summer) |
| 16934 | Temp_LowSupplySet | Signed 16-bit | 150 | 0 | 1000 | °C | XXX.Y | Temperature Low Supply Limit Setpoint (Summer) |
| 16935 | Temp_LowSupplyBand | Signed 16-bit | 100 | 10 | 999 | °C | XXX.Y | Temperature Low Supply Band (Summer) |
| 16940 | FastHeatCoolEn | Boolean | 0 | — | — | — | — | Fast Heating/Cooling Enable |
| 16941 | FastHeatSet | Signed 16-bit | 200 | -500 | 500 | °C | XXX.Y | Maximum outside temp for Power up Fast Heating |
| 16942 | FastCoolSet | Signed 16-bit | 250 | -500 | 500 | °C | XXX.Y | Minimum outside temp for Power up Fast Cooling |
| 16943 | FastHCTimeout | Signed 16-bit | 10 | 1 | — | Min | — | Fast Heating/Cooling and StartUp timeout |
| 16950 | Pump_AntiStickingRun | Unsigned 16-bit | 20 | 0 | 255 | sec | — | Antisticking run time |
| 16951 | Pump_AntiStickingPeriod | Unsigned 16-bit | 7 | 0 | 30 | days | — | Antisticking period (0=Disabled) |
| 16952 | Pump_Post_Time | Unsigned 16-bit | 5 | 0 | 255 | min | — | Pump Post Running Time |
| 16953 | Heater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Analog Power |
| 16954 | Heater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 1 Power |
| 16955 | Heater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 2 Additional Power |
| 16956 | Heater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 3 Additional Power |
| 16957 | Heater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 4 Additional Power |
| 16958 | Heater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 5 Additional Power |
| 16959 | Heater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 6 Additional Power |
| 16960 | Heater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | El. Heater Hysteresis [% of current step] |
| 16961 | Heater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | El. Heater PWM Period |
| 16962 | PreHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Analog Power |
| 16963 | PreHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 1 Power |
| 16964 | PreHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 2 Power |
| 16965 | PreHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 3 Power |
| 16966 | PreHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 4 Power |
| 16967 | PreHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 5 Power |
| 16968 | PreHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 6 Power |
| 16969 | PreHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | PreHeater Hysteresis [% of current step] |
| 16970 | PreHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | PreHeater PWM Period |
| 16971 | PostHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Analog Power |
| 16972 | PostHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 1 Power |
| 16973 | PostHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 2 Power |
| 16974 | PostHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 3 Power |
| 16975 | PostHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 4 Power |
| 16976 | PostHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 5 Power |
| 16977 | PostHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 6 Power |
| 16978 | PostHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | PostHeater Hysteresis [% of current step] |
| 16979 | PostHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | PreHeater PWM Period |
| 16980 | CondUnitS1_Req | Signed 16-bit | 200 | 0 | 1000 | % | XXX.Y | % CondUnit Step 1 |
| 16981 | CondUnitS2_Req | Signed 16-bit | 400 | 0 | 1000 | % | XXX.Y | % CondUnit Step 2 |
| 16982 | CondUnitS3_Req | Signed 16-bit | 600 | 0 | 1000 | % | XXX.Y | % CondUnit Step 3 |
| 16983 | CondUnitS4_Req | Signed 16-bit | 800 | 0 | 1000 | % | XXX.Y | % CondUnit Step 4 |
| 16984 | CondUnitSx_Hysteresis | Signed 16-bit | 50 | 10 | 100 | % | — | Cond. Unit Hysteresis % of current Step size |
| 16985 | CondUnit_Ton | Unsigned 16-bit | 0 | 0 | 600 | sec | — | Cond Unit Step Minimum On Time |
| 16986 | CondUnit_Toff | Unsigned 16-bit | 0 | 0 | 600 | sec | — | Cond Unit Step Minimum Off Time |
| 16987 | CondUnit_Offset | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | Cond Unit AO Offset |
| 16988 | CondUnit_FanSpeedDefrost | 0=No Action 1=Low Speed 2=Fan Off | 0 | 0 | 2 |  |  | Condensing Unit: Fan Speed During Defrost |
| 16989 | MultiCondUnit_CtrlMode | FALSE=Delay TRUE=Hysteresis | 1 | 0 | 1 |  |  | Multi Condensing Unit:Control |
| 16990 | MultiCondUnit_RegHyst | Signed 16-bit | 5 | 2 | 30 | sec |  | Multi Condensing Unit regulator hysteresis |
| 16991 | MultiCondUnit_DelayOn | Unsigned 16-bit | 0 | 0 | 600 | sec |  | Multi Cond Unit Delay On |
| 16992 | MultiCondUnit_DelayOff | Unsigned 16-bit | 0 | 0 | 600 | sec |  | Multi Cond Unit Delay Off |
| 17000 | PreHeaterSetpoint | Signed 16-bit | 50 | -100 | 200 | °C | XXX.Y | Setpoint Pre Heating |
| 17001 | Pb_PreHeating | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | PreHeating Proportional Band |
| 17002 | Ti_PreHeating | Unsigned 16-bit | 300 | 0 | — | sec | — | PreHeating Integral Time |
| 17010 | RecoveryDiff_Band | Signed 16-bit | 15 | 1 | 100 | °C | XXX.Y | Recovery Diff (On/Off Case) Recovery Band (Mod Case with Direct Return control); |
| 17011 | RecoveryDeadZone | Signed 16-bit | 10 | 0 | 100 | °C | XXX.Y | Recovery Dead Zone |
| 17012 | RecoveryPower | Signed 16-bit | 250 | 0 | 1000 | % | XXX.Y | % of PI out sent to recovery (Only for Cascade or Supply control) |
| 17013 | RecoveryDefrost_SetMaxReq | Signed 16-bit | -40 | -150 | 100 | °C | XXX.Y | Recovery Defrost: Setpoint Expulsion Temperature |
| 17014 | RecoveryDefrost_Band | Signed 16-bit | 40 | 1 | 100 | °C | XXX.Y | Recovery Defrost: Band Mix Chamber/PreHeater/Supply Fan |
| 17015 | RecoveryDefrost_Cutoff | Signed 16-bit | 0 | 0 | 100 | °C | XXX.Y | Recovery Defrost: CutOff Modulating Fan |
| 17016 | RecoveryReqDuringFastHC | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | Recovery request during Fast Heating/Cooling |
| 17020 | Hum_Band | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | Humidification Band |
| 17021 | Pb_Dehum | Signed 16-bit | 100 | 2 | 200 | %R.H. | XXX.Y | Dehum. Proportional Band |
| 17022 | Ti_Dehum | Unsigned 16-bit | 0 | 0 | — | sec | — | Dehum. Integral Time |
| 17023 | Pb_Dewpoint | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | Dewpoint Dehum. Proportional Band |
| 17024 | Ti_Dewpoint | Unsigned 16-bit | 300 | 0 | — | sec | — | Dewpoint Dehum. Integral Time |
| 17025 | Offset_Post | Signed 16-bit | 10 | 4 | 50 | °C | XXX.Y | PostHeating Setpoint offset with respect to current set |
| 17026 | Dehum_WinterEn | Boolean | 0 | — | — | — | — | Enable Winter Dehumidification |
| 17027 | Dehum_WinterHumHyst | Signed 16-bit | 10 | 4 | 50 | g/Kg | XXX.Y | Winter Dehumidification Hysteresis |
| 17028 | Dehum_Req_Diff | Signed 16-bit | 50 | 1 | 150 | %R.H. | XXX.Y | Dehumidification Request Differential on Return Humidity for Winter and Dewpoint mode |
| 17029 | Hum_HighSupplyEn | Boolean | 0 | — | — | — | — | Humidification High Supply Limit Enable |
| 17030 | Hum_HighSupplySet | Signed 16-bit | 700 | 0 | 1000 | %R.H. | XXX.Y | Humidification High Supply Limit Setpoint |
| 17031 | Hum_HighSupplyBand | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | Humidification High Supply Band |
| 17032 | DeHum_LowSupplyEn | Boolean | 0 | — | — | %R.H. | — | DeHumidification Low Supply Limit Enable |
| 17033 | DeHum_LowSupplySet | Signed 16-bit | 300 | 0 | 1000 | %R.H. | XXX.Y | DeHumidification Low Supply Limit Setpoint |
| 17034 | DeHum_LowSupplyBand | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | DeHumidification Low Supply Band |
| 17040 | PostHeating4Integration | Boolean | 1 | — | — | — | — | Use the post heating also in the heating phase |
| 17041 | PostPower | Signed 16-bit | 300 | 1 | 1000 | % | XXX.Y | % of PI out sent to post (if enabled as heat integration) |
| 17042 | Pb_Post | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | PostHeating Dehum. Proportional Band |
| 17043 | Ti_Post | Unsigned 16-bit | 300 | 0 | — | sec | — | PostHeating Dehum. Integral Time |
| 17900 | LogEnable | Boolean | 0 | — | — | — | — | Logger Enable |
| 17901 | LogCycle | Unsigned 16-bit | 1 | MinLogCycle | 1439 | Min | HH:MM | Logger Period |
| 17902 | LogErrorNumber | Unsigned 32-bit | 0 | — | — | — | — | Error while try to oper or save to a file |
| 17904 | LoggedRecord | Unsigned 32-bit | 0 | — | — | — | — | Number of logged record (Rounded by 100) |
| 17906 | MinLogCycle | Signed 16-bit | 1 | 0 | 1439 | Min | HH:MM | Minimum Log Cycle |
| 17907 | FirstDownload | Boolean | 1 | — | — | — | — | — |
| 17908 | microSDPresCount | Unsigned 16-bit | 0 | — | — | — | — | microSD Presence Counter |
| 18000 | tE00_TimeBandEnable | Boolean | 0 | — | — | — | — | Time events Enable |
| 18001 | tE01_TimeProfileMonday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Monday |
| 18002 | tE02_TimeProfileTuesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Tuesday |
| 18003 | tE03_TimeProfileWednesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Wednesday |
| 18004 | tE04_TimeProfileThursday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Thursday |
| 18005 | tE05_TimeProfileFriday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Friday |
| 18006 | tE06_TimeProfileSaturday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Saturday |
| 18007 | tE07_TimeProfileSunday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Sunday |
| 18008 | tE10_TimeProfile1Event1 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #1 of profile #1 |
| 18009 | tE11_ModeProfile1Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #1 of profile #1 |
| 18010 | tE12_TimeProfile1Event2 | Signed 16-bit | 720 | 0 | 1439 | — | HH:MM | Time of event #2 of profile #1 |
| 18011 | tE13_ModeProfile1Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #2 of profile #1 |
| 18012 | tE14_TimeProfile1Event3 | Signed 16-bit | 840 | 0 | 1439 | — | HH:MM | Time of event #3 of profile #1 |
| 18013 | tE15_ModeProfile1Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #3 of profile #1 |
| 18014 | tE16_TimeProfile1Event4 | Signed 16-bit | 1080 | 0 | 1439 | — | HH:MM | Time of event #4 of profile #1 |
| 18015 | tE17_ModeProfile1Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #4 of profile #1 |
| 18016 | tE20_TimeProfile2Event1 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #1 of profile #2 |
| 18017 | tE21_ModeProfile2Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #1 of profile #2 |
| 18018 | tE22_TimeProfile2Event2 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #2 of profile #2 |
| 18019 | tE23_ModeProfile2Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #2 of profile #2 |
| 18020 | tE24_TimeProfile2Event3 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #3 of profile #2 |
| 18021 | tE25_ModeProfile2Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #3 of profile #2 |
| 18022 | tE26_TimeProfile2Event4 | Signed 16-bit | 1080 | 0 | 1439 | — | HH:MM | Time of event #4 of profile #2 |
| 18023 | tE27_ModeProfile2Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #4 of profile #2 |
| 18200 | TW00_EnableYearEvents | Boolean | 0 | — | — | — | — | Enable year events |
| 18201 | TW01_EventProfile01 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 1 |
| 18202 | TW02_EventProfile02 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 2 |
| 18203 | TW03_EventProfile03 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 3 |
| 18204 | TW04_EventProfile04 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 4 |
| 18205 | TW05_EventProfile05 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 5 |
| 18206 | TW06_EventProfile06 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 6 |
| 18207 | TW07_EventProfile07 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 7 |
| 18208 | TW08_EventProfile08 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 8 |
| 18209 | TW09_EventProfile09 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 9 |
| 18210 | TW10_EventProfile10 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 10 |
| 18211 | TW11_EventProfile11 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 11 |
| 18212 | TW12_EventProfile12 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 12 |
| 18213 | TW13_EventProfile13 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 13 |
| 18214 | TW14_EventProfile14 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 14 |
| 18215 | TW15_EventProfile15 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 15 |
| 18216 | TW16_EnEvent01 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 1 |
| 18217 | TW17_EnEvent02 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 2 |
| 18218 | TW18_EnEvent03 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 3 |
| 18219 | TW19_EnEvent04 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 4 |
| 18220 | TW20_EnEvent05 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 5 |
| 18221 | TW21_EnEvent06 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 6 |
| 18222 | TW22_EnEvent07 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 7 |
| 18223 | TW23_EnEvent08 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 8 |
| 18224 | TW24_EnEvent09 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 9 |
| 18225 | TW25_EnEvent10 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 10 |
| 18226 | TW26_EnEvent11 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 11 |
| 18227 | TW27_EnEvent12 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 12 |
| 18228 | TW28_EnEvent13 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 13 |
| 18229 | TW29_EnEvent14 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 14 |
| 18230 | TW30_EnEvent15 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 15 |
| 18231 | TW31_EventDDStart01 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 1 |
| 18232 | TW32_EventDDStart02 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 2 |
| 18233 | TW33_EventDDStart03 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 3 |
| 18234 | TW34_EventDDStart04 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 4 |
| 18235 | TW35_EventDDStart05 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 5 |
| 18236 | TW36_EventDDStart06 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 6 |
| 18237 | TW37_EventDDStart07 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 7 |
| 18238 | TW38_EventDDStart08 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 8 |
| 18239 | TW39_EventDDStart09 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 9 |
| 18240 | TW40_EventDDStart10 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 10 |
| 18241 | TW41_EventDDStart11 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 11 |
| 18242 | TW42_EventDDStart12 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 12 |
| 18243 | TW43_EventDDStart13 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 13 |
| 18244 | TW44_EventDDStart14 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 14 |
| 18245 | TW45_EventDDStart15 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 15 |
| 18246 | TW46_EventMMStart01 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 1 |
| 18247 | TW47_EventMMStart02 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 2 |
| 18248 | TW48_EventMMStart03 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 3 |
| 18249 | TW49_EventMMStart04 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 4 |
| 18250 | TW50_EventMMStart05 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 5 |
| 18251 | TW51_EventMMStart06 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 6 |
| 18252 | TW52_EventMMStart07 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 7 |
| 18253 | TW53_EventMMStart08 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 8 |
| 18254 | TW54_EventMMStart09 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 9 |
| 18255 | TW55_EventMMStart10 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 10 |
| 18256 | TW56_EventMMStart11 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 11 |
| 18257 | TW57_EventMMStart12 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 12 |
| 18258 | TW58_EventMMStart13 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 13 |
| 18259 | TW59_EventMMStart14 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 14 |
| 18260 | TW60_EventMMStart15 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 15 |
| 18261 | TW61_EventDDStop01 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 1 |
| 18262 | TW62_EventDDStop02 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 2 |
| 18263 | TW63_EventDDStop03 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 3 |
| 18264 | TW64_EventDDStop04 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 4 |
| 18265 | TW65_EventDDStop05 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 5 |
| 18266 | TW66_EventDDStop06 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 6 |
| 18267 | TW67_EventDDStop07 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 7 |
| 18268 | TW68_EventDDStop08 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 8 |
| 18269 | TW69_EventDDStop09 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 9 |
| 18270 | TW70_EventDDStop10 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 10 |
| 18271 | TW71_EventDDStop11 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 11 |
| 18272 | TW72_EventDDStop12 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 12 |
| 18273 | TW73_EventDDStop13 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 13 |
| 18274 | TW74_EventDDStop14 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 14 |
| 18275 | TW75_EventDDStop15 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 15 |
| 18276 | TW76_EventMMStop01 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18277 | TW77_EventMMStop02 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18278 | TW78_EventMMStop03 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18279 | TW79_EventMMStop04 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18280 | TW80_EventMMStop05 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18281 | TW81_EventMMStop06 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18282 | TW82_EventMMStop07 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18283 | TW83_EventMMStop08 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18284 | TW84_EventMMStop09 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18285 | TW85_EventMMStop10 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18286 | TW86_EventMMStop11 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18287 | TW87_EventMMStop12 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18288 | TW88_EventMMStop13 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18289 | TW89_EventMMStop14 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18290 | TW90_EventMMStop15 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Day Year events 1 |
| 19810 | Fan_Maintenance_Supply | Boolean | 0 | — | — | — | — | Fan Main Supply Forced Off for maintenance |
| 19811 | Fan_Maintenance_Return | Boolean | 0 | — | — | — | — | Fan Main Return Forced Off for maintenance |
| 19812 | Fan_Maintenance_SupplyBck | Boolean | 0 | — | — | — | — | Fan Supply 2 Forced Off for maintenance |
| 19813 | Fan_Maintenance_ReturnBck | Boolean | 0 | — | — | — | — | Fan Return 2 Forced Off for maintenance |
| 19814 | Fan_Maintenance_Supply1b | Boolean | 0 | — | — | — | — | Fan Main Supply b Forced Off for maintenance |
| 19815 | Fan_Maintenance_Supply1c | Boolean | 0 | — | — | — | — | Fan Main Supply c Forced Off for maintenance |
| 19816 | Fan_Maintenance_Return1b | Boolean | 0 | — | — | — | — | Fan Main Return b Forced Off for maintenance |
| 19817 | Fan_Maintenance_Return1c | Boolean | 0 | — | — | — | — | Fan Main Return c Forced Off for maintenance |
| 19818 | Fan_Maintenance_Supply2b | Boolean | 0 | — | — | — | — | Fan Main Supply 2b Forced Off for maintenance |
| 19819 | Fan_Maintenance_Supply2c | Boolean | 0 | — | — | — | — | Fan Main Supply 2c Forced Off for maintenance |
| 19820 | Fan_Maintenance_Return2b | Boolean | 0 | — | — | — | — | Fan Main Return 2b Forced Off for maintenance |
| 19821 | Fan_Maintenance_Return2c | Boolean | 0 | — | — | — | — | Fan Main Return 2c Forced Off for maintenance |
| 19822 | Fan_Modbus_Configured_E2 | Boolean | 0 |  |  |  |  | Modbus Fan have been configured |
| 19823 | udhoursCU1E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 1 Running Hours |
| 19825 | udhoursCU2E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 2 Running Hours |
| 19827 | udhoursCU3E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 3 Running Hours |
| 19829 | udhoursCU4E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 4 Running Hours |
| 19831 | CU1_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 1 Forced Off for maintenance |
| 19832 | CU2_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 2 Forced Off for maintenance |
| 19833 | CU3_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 3 Forced Off for maintenance |
| 19834 | CU4_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 4 Forced Off for maintenance |

Table 99 - Modbus EEProm Table

Modbus Status table

The following table describes the Status parameters.

| Modbus Register | Name | Device type | Def | Min | Max | Unit | Format | RW | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9213 | PSWEntry | Unsigned 16-bit | 0 | — | — | — | — | RW | Password Entry: |
| 9214 | PSWLevel | Unsigned 8-bit | — | — | — | — | — | R | Current password level |
| 9215 | PSWreset | Boolean | 0 | — | — | — | — | RW | Password Level Reset Request |
| 9216 | sysClock_seconds_WR | Unsigned 8-bit | 0 | 0 | 59 | — | — | RW | Second value to update |
| 9217 | sysClock_minutes_WR | Unsigned 8-bit | 0 | 0 | 59 | — | — | RW | Minute value to update |
| 9218 | sysClock_hours_WR | Unsigned 8-bit | 0 | 0 | 23 | — | — | RW | Hour value to update |
| 9219 | sysClock_dayweek_WR | Unsigned 8-bit | 0 | 0 | 6 | — | — | RW | Day of the week value to update |
| 9220 | sysClock_daymonth_WR | Unsigned 8-bit | 1 | 1 | 31 | — | — | RW | Day of the month value to update |
| 9221 | sysClock_month_WR | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | Month value to update |
| 9222 | sysClock_year_WR | Unsigned 8-bit | 10 | 10 | 99 | — | — | RW | Year value to update |
| 9223 | sysClock_update | 0=Current; 1=Update; 2=Modify | 0 | 0 | 2 | — | — | RW | Confirm update |
| 9224 | sv_sysUsbStatus | 0=Completed; 1=Running; 248 = 248=Open in write failed; 249 = 249=Write failed; 250 = 250=Some parameters failed; 251 = 251=File not compatible; 252 = 252=Usb not connected; 253 = 253=File too long; 254 = 254=File not present; 255 = 255=Command Failed | — | 0 | 255 | — | — | R | Usb status code |
| 9225 | sv_sysUsbCommand | Unsigned 16-bit | 0 | — | — | — | — | RW | Usb status code |
| 9226 | SaveFactoryStatus | 0=Running; 1=Done; 2=Error/Not Done | — | 0 | 2 | — | — | R | Save Factory Settings Status |
| 9227 | SaveFactoryCommand | Boolean | 0 | — | — | — | — | RW | Save Factory Settings Request |
| 9228 | RestoreFactoryStatus | 0=Completed; 1=Running; 248 = 248=Open in write failed; 249 = 249=Write failed; 250 = 250=Some parameters failed; 251 = 251=File not compatible; 252 = 252=Usb not connected; 253 = 253=File too long; 254 = 254=File not present; 255 = 255=Command Failed | — | 0 | 255 | — | — | R | Restore Factory Settings Status |
| 9229 | RestoreFactoryCommand | Boolean | 0 | — | — | — | — | RW | Restore Factory Settings Request |
| 9299 | Unit_ApplicationCode | Unsigned 16-bit | 1 |  |  |  |  | R | Unit Application Code |
| 9300 | Unit_Version | Unsigned 16-bit | 0 | — | — | — | XX.YY | RW | Unit Application Version |
| 9301 | Unit_BMS_OnOff | Boolean | 1 | — | — | — | — | RW | Unit On/Off via Modbus |
| 9302 | Unit_Status | 0=OFF; 1=STANDBY; 2=RUN | — | 0 | 2 | — | — | R | Unit Status |
| 9303 | Unit_Mode_Status | 0=Cool; 1=Heat; 2=Auto | — | 0 | 2 | — | — | R | Unit Mode |
| 9304 | Unit_EcoCmfNight_Status | 1=Economy; 2=Comfort; 3=Night | — | 1 | 3 | — | — | R | Unit Mode |
| 9305 | Unit_Alarm | Boolean | — | — | — | — | — | R | Unit Alarm |
| 9306 | T_RegulationProbe | Signed 16-bit | — | — | — | °C | XXX.Y | R | Temperature Regulation Probe |
| 9307 | T_CurrentSetpointByPar | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Setpoint by parameter based on selected mode |
| 9308 | T_CurrentSupplySetpoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Supply Setpoint |
| 9309 | T_CurrentReturnSetpoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Return Setpoint |
| 9310 | T_DewPointSetPoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Dewpoint Setpoint |
| 9311 | RH_CurrentSetpoint | Signed 16-bit | — | — | — | %R.H. | — | R | Current Return Setpoint |
| 9312 | AirQ_CurrentSetpointVOC | Signed 16-bit | — | — | — | % | — | R | Current Setpoint VOC |
| 9313 | AirQ_CurrentSetpointCO2 | Signed 16-bit | — | — | — | ppm | — | R | Current Setpoint CO2 |
| 9314 | Pr_CurrentSupplySetpoint | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Supply Setpoint - Units depends on Fan_Supply_Pressure_Flow |
| 9316 | Pr_CurrentReturnSetpoint | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Return Setpoint - Units depends on Fan_Return_Pressure_Flow |
| 9318 | RH_RegulationProbe | Signed 16-bit | — | — | — | %R.H. | — | R | Humdity Regulation Probe |
| 9319 | AirQ_RegulationProbe | Signed 16-bit | — | — | — | %/ppm | — | R | Air Quality Regulation Probe |
| 9320 | Pr_Flow_Supply | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| 9322 | Pr_Flow_Return | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| 9350 | OnOffRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit On/Off via request via Web/Modbus |
| 9351 | ChangeSeasonRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit Season Change request via Web/Modbus |
| 9352 | ComfortEcoNightRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit Comfort/Eco/Night request via Web/Modbus |
| 9480 | History000 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9481 | History001 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9482 | History002 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9483 | History003 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9484 | HistoricalPosition | Unsigned 16-bit | 0 | — | — | — | — | RW | Historical Postion Required |
| 9485 | Historical_Value_Code | 0 = ---; 1 = A01-Supply Pr.; 2 = A02-Return Pr.; 3 = A03-External Pr.; 4 = A04-Expulsion Pr.; 5 = A05-Preheating Pr.; 6 = A06-Saturation Pr.; 7 = A07-Antifreeze Pr.; 8 = A08-CO2 Pr.; 9 = A09-Supply Press. Pr.; 10 = A10-Return Press. Pr.; 11 = A11-Hum. Supply Pr.; 12 = A12-Hum. Return Pr.; 13 = A13-VOC Pr.; 14 = A14-Hum. External Pr.; 15 = A15-; 16 = A16-; 17 = A17-; 18 = A18-; 19 = A19-; 20 = A20-; 21 = A21-; 22 = A22-; 23 = A23-; 24 = A24-; 25 = A25-; 26 = A26-Airflow Prb Sup.; 27 = A27-Airflow Prb Ret.; 28 = A28-Airflow Prb Sup.2; 29 = A29-Airflow Prb Ret.2; 30 = A30-Fan Supply; 31 = A31-Fan Return; 32 = A32-Fire; 33 = A33-Door; | — | 0 | 65 | — | — | R | Historical: Alarm Code |
| 9485 | Historical_Value_Code | 34 = A34-Antifreeze; 35 = A35-Airflow Supply; 36 = A36-Airflow Return; 37 = A37-Humidifier; 38 = A38-Preheater; 39 = A39-Heater; 40 = A40-Postheater; 41 = A41-Recovery; 42 = A42-Filter 1; 43 = A43-Filter 2; 44 = A44-Filter 3; 45 = A45-Filter 4; 46 = A46-Fan Supply 2; 47 = A47-Fan Return 2; 48 = A48-Airflow Supply 2; 49 = A49-Airflow Return 2; 50 = A50-Cond. Unit; 51 = A51-Real Time Clock; 52 = A52-Fan Maintenance; 53 = A53-Modbus Fan Config. Timeout 54 = A54-Modbus Fan Supply Communication; 55 = A55-Modbus Fan Return Communication; 56 = A56-Modbus Fan Supply 2 Communication; 57 = A57-Modbus Fan Return 2 Communication; 58 = A58-Filter 5; 59 = A59-; 60 = A60-Log Error; 61 = A61-Can Expansion 1; 62 = A62-Can Expansion 2; 63 = A63-Can Expansion 3; 64 = A64-Can Expansion 4; 65 = A65-Can Expansion 5 66 = A66-Cond. Unit 2 67 = A67-Cond. Unit 3 68 =A68-Cond. Unit 4 | — | 0 | 65 | — | — | R | Historical: Alarm Code |
| 9486 | Historical_Value_Date | Signed 16-bit | — | — | — | — | XX.YY | R | Historical: Alarm Date |
| 9487 | Historical_Value_Time | Signed 16-bit | — | — | — | — | HH:MM | R | Historical: Alarm Time |
| 9488 | Historical_Value_SecStatus | Signed 16-bit | — | — | — | — | XX.YY | R | Historical: Alarm Seconds and Status: 100x+seconds (x=0 restored, x=1 active, x=2 wait for reset) |
| 9489 | Historical_Number_alarms | Signed 16-bit | — | — | — | — | — | R | Historical: Number of stored alarms |
| 9490 | Historical_Reset | Boolean | 0 | — | — | — | — | RW | Historical: Reset Request |
| 9491 | Historical_Value_Sec | Signed 16-bit | — | — | — | — | — | R | Historical: Alarm Time Seconds |
| 9492 | Historical_Value_Status | AlarmEnum | — | — | — | — | — | R | Historical: Alarm Status |
| 9520 | Alxx_Reset | Boolean | — | — | — | — | — | RW | Alarm reset request command via Modbus |
| 9521 | Al01_SupplyProbe | 0=Not Active; 1=Active; 2=Manual Reset | — | 0 | 2 | — | — | R | Al01-Supply Temperature Probe Error |
| 9522 | Al02_ReturnProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A02-Return Temperature Probe Error |
| 9523 | Al03_ExternalProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A03-External Temperature Probe Error |
| 9524 | Al04_ExpulsionProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A04-Expulsion Temperature Probe Error |
| 9525 | Al05_PreHeatingProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A05-Preheating Temperature Probe Error |
| 9526 | Al06_SaturationProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A06-Saturation Temperature Probe Error |
| 9527 | Al07_AntifreezeProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A07-Antifreeze Temperature Probe Error |
| 9528 | Al08_AirQualityProbe_CO2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A08-CO2 Probe Error |
| 9529 | Al09_SupplyPressureProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A09-Supply Pressure Probe Error |
| 9530 | Al10_ReturnPressureProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A10-Return Pressure Probe Error |
| 9531 | Al11_SupplyHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A11-Hum. Supply Probe Error |
| 9532 | Al12_ReturnHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A12-Hum. Return Probe Error |
| 9533 | Al13_AirQualityProbe_VOC | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A13-VOC Probe Error |
| 9534 | Al14_ExternalHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A14-Hum. External Probe Error |
| 9535… 9545 | Future use | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Future Usse |
| 9546 | Al26_SensAirFlowSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A26-Supply Airflow by Probe |
| 9547 | Al27_SensAirFlowReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A27-Return Airflow by Probe |
| 9548 | Al28_SensAirFlowSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A28-Airflow Prb Sup.2 |
| 9549 | Al29_SensAirFlowReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A29-Airflow Prb Ret.2 |
| 9550 | Al30_FanThermalSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A30-Fan Supply |
| 9551 | Al31_FanThermalReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A31-Fan Return |
| 9552 | Al32_Fire | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A32-Fire |
| 9553 | Al33_Door | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A33-Door |
| 9554 | Al34_Antifreeze | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A34-Antifreeze |
| 9555 | Al35_AirFlowSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A35-Airflow Supply |
| 9556 | Al36_AirFlowReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A36-Airflow Return |
| 9557 | Al37_Humidifier | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A37-Humidifier |
| 9558 | Al38_PreHeater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A38-Preheater |
| 9559 | Al39_Heater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A39-Heater |
| 9560 | Al40_PostHeater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A40-Postheater |
| 9561 | Al41_RotaryWheel | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A41-Recovery |
| 9562 | Al42_Filter1 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A42-Filter 1 |
| 9563 | Al43_Filter2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A43-Filter 2 |
| 9564 | Al44_Filter3 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A44-Filter 3 |
| 9565 | Al45_Filter4 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A45-Filter 4 |
| 9566 | Al46_FanThermalSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A46-Fan Supply 2 |
| 9567 | Al47_FanThermalReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A47-Fan Return 2 |
| 9568 | Al48_AirFlowSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A48-Airflow Supply 2 |
| 9569 | Al49_AirFlowReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A49-Airflow Return 2 |
| 9570 | Al50_CondUnit | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A50-Cond. Unit |
| 9571 | Al51_RTC | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A51-Real Time Clock |
| 9572 | Al52_FanMaintenance | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A52-Fan Maintenance |
| 9573 | Al53_ModbusFanCfg | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A53-Modbus Fan Config. Timeout |
| 9574 | Al54_FanSupplyCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A54-Modbus Fan Supply Communication |
| 9575 | Al55_FanReturnCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A55-Modbus Fan Return Communication |
| 9576 | Al56_FanSupplyBckCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A56-Modbus Fan Supply 2 Communication |
| 9577 | Al57_FanReturnBckCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A57-Modbus Fan Return 2 Communication |
| 9578 | Al58_Filter5 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A58-Filter 5 |
| 9579 | Al59_ | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | — |
| 9580 | Al60_LogError | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A60-Log Error |
| 9581 | Al61_Exp1 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A61-Can Expansion 1 |
| 9582 | Al62_Exp2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A62-Can Expansion 2 |
| 9583 | Al63_Exp3 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A63-Can Expansion 3 |
| 9584 | Al64_Exp4 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A64-Can Expansion 4 |
| 9585 | Al65_Exp5 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A65-Can Expansion 5 |
| 9586… 9618 | Future use |  |  |  |  |  |  | R | Future use |
| 9619 | Al99_FanSupply_1b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al99-Fan Supply 1b Com Alarm |
| 9620 | Al100_FanSupply_1c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al100-Fan Supply 1c Com Alarm |
| 9621 | Al101_FanReturn_1b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al101-Fan Return 1b Com Alarm |
| 9622 | Al102_FanReturn_1c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al102-Fan Return 1c Com Alarm |
| 9623 | Al103_FanSupply_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al103-Fan Supply 2b Com Alarm |
| 9624 | Al104_FanSupply_2c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al104-Fan Supply 2c Com Alarm |
| 9625 | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al105-Fan Return 2b Com Alarm |
| 9626 | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al106-Fan Return 2c Com Alarm |
| 9670 | AI_Exp1_1 | Signed 16-bit | — | — | — | — | — | R | Physical Input 1 Exp1 |
| 9671 | AI_Exp1_2 | Signed 16-bit | — | — | — | — | — | R | Physical Input 2 Exp1 |
| 9672 | AI_Exp1_3 | Signed 16-bit | — | — | — | — | — | R | Physical Input 3 Exp1 |
| 9673 | AI_Exp1_4 | Signed 16-bit | — | — | — | — | — | R | Physical Input 4 Exp1 |
| 9674 | AI_Exp2_1 | Signed 16-bit | — | — | — | — | — | R | Physical Input 1 Exp2 |
| 9675 | AI_Exp2_2 | Signed 16-bit | — | — | — | — | — | R | Physical Input 2 Exp2 |
| 9676 | AI_Exp2_3 | Signed 16-bit | — | — | — | — | — | R | Physical Input 3 Exp2 |
| 9677 | AI_Exp2_4 | Signed 16-bit | — | — | — | — | — | R | Physical Input 4 Exp2 |
| 9720 | AI_LogicIndex_0 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Supply Temperature |
| 9721 | AI_LogicIndex_1 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Return Temperature |
| 9722 | AI_LogicIndex_2 | Signed 16-bit | — | — | — | °C | XXX.Y | R | External Temperature |
| 9723 | AI_LogicIndex_3 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Expulsion Temperature |
| 9724 | AI_LogicIndex_4 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Preheating Temp, |
| 9725 | AI_LogicIndex_5 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Saturation Temperature |
| 9726 | AI_LogicIndex_6 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Antifreeze Temperature |
| 9727 | AI_LogicIndex_7 | Signed 16-bit | — | — | — | ppm | — | R | Air Quality - VOC |
| 9728 | AI_LogicIndex_8 | Signed 16-bit | — | — | — | % | XXX.Y | R | Air Quality - CO2 |
| 9729 | AI_LogicIndex_9 | Signed 16-bit | — | — | — | pa | — | R | Supply Pressure |
| 9730 | AI_LogicIndex_10 | Signed 16-bit | — | — | — | pa | — | R | Return Pressure |
| 9731 | AI_LogicIndex_11 | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Humidity |
| 9732 | AI_LogicIndex_12 | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Humidity |
| 9733 | AI_LogicIndex_13 | Signed 16-bit | — | — | — | % | XXX.Y | R | External Humidity |
| 9734 | AI_LogicIndex_14 | Signed 32-bit | — | — | — | m3/h | — | R | Supply Flow Testing |
| 9736 | AI_LogicIndex_15 | Signed 32-bit | — | — | — | m3/h | — | R | Return Flow Testing |
| 9738 | AI_free4 | Signed 16-bit | — | — | — | — | — | R | — |
| 9739 | AI_free5 | Signed 16-bit | — | — | — | — | — | R | — |
| 9740 | AI_free6 | Signed 16-bit | — | — | — | — | — | R | — |
| 9741 | AI_free7 | Signed 16-bit | — | — | — | — | — | R | — |
| 9742 | AI_free8 | Signed 16-bit | — | — | — | — | — | R | — |
| 9743 | AI_free9 | Signed 16-bit | — | — | — | — | — | R | — |
| 9744 | AI_free10 | Signed 16-bit | — | — | — | — | — | R | — |
| 9745 | DI_Voltage_LogicIndex_0 | 0 = 0V; 1 = 24V; 2 = Not Used | — | 0 | 2 | — | — | R | Supply Fan Thermal - Physical Status |
| 9746 | DI_Voltage_LogicIndex_1 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan Thermal - Physical Status |
| 9747 | DI_Voltage_LogicIndex_2 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | On/Off Input - Physical Status |
| 9748 | DI_Voltage_LogicIndex_3 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Fire Alarm - Physical Status |
| 9749 | DI_Voltage_LogicIndex_4 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Mode Input - Physical Status |
| 9750 | DI_Voltage_LogicIndex_5 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Door - Physical Status |
| 9751 | DI_Voltage_LogicIndex_6 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Antifreeze - Physical Status |
| 9752 | DI_Voltage_LogicIndex_7 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Airflow - Physical Status |
| 9753 | DI_Voltage_LogicIndex_8 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Airflow - Physical Status |
| 9754 | DI_Voltage_LogicIndex_9 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Humidifier Alarm - Physical Status |
| 9755 | DI_Voltage_LogicIndex_10 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Preheater Alarm - Physical Status |
| 9756 | DI_Voltage_LogicIndex_11 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Postheater Alarm - Physical Status |
| 9757 | DI_Voltage_LogicIndex_12 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Rotary Wheel Alarm - Physical Status |
| 9758 | DI_Voltage_LogicIndex_13 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 1 Alarm - Physical Status |
| 9759 | DI_Voltage_LogicIndex_14 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 2 Alarm - Physical Status |
| 9760 | DI_Voltage_LogicIndex_15 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 3 Alarm - Physical Status |
| 9761 | DI_Voltage_LogicIndex_16 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 4 Alarm - Physical Status |
| 9762 | DI_Voltage_LogicIndex_17 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 Th. - Physical Status |
| 9763 | DI_Voltage_LogicIndex_18 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 Th. - Physical Status |
| 9764 | DI_Voltage_LogicIndex_19 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 Airflow - Physical Status |
| 9765 | DI_Voltage_LogicIndex_20 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 Airflow - Physical Status |
| 9766 | DI_Voltage_LogicIndex_21 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Cond. Unit Alarm - Physical Status |
| 9767 | DI_Voltage_LogicIndex_22 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | El. Heater Alarm - Physical Status |
| 9768 | DI_Voltage_LogicIndex_23 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 2 Alarm - Physical Status |
| 9769 | DI_Voltage_LogicIndex_24 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 3 Alarm - Physical Status |
| 9770 | DI_Voltage_LogicIndex_25 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 4 Alarm - Physical Status |
| 9771 | DI_Voltage_LogicIndex_26 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 1 Defrost - Physical Status |
| 9772 | DI_Voltage_LogicIndex_27 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 2 Defrost - Physical Status |
| 9773 | DI_Voltage_LogicIndex_28 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 3 Defrost - Physical Status |
| 9774 | DI_Voltage_LogicIndex_29 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 4 Defrost - Physical Status |
| 9775 | DI_Voltage_LogicIndex_30 | Signed 16-bit | — | — | — | — | — | R | Filter 5 Alarm - Physical Status |
| 9776 | DI_free9 | Signed 16-bit | — | — | — | — | — | R | — |
| 9777 | DI_free10 | Signed 16-bit | — | — | — | — | — | R | — |
| 9778 | DO_LogicIndex_0 | 0 = Off; 1 = On; 2 = Not Used | — | 0 | 2 | — | — | R | Supply Fan - Logic Status |
| 9779 | DO_LogicIndex_1 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan - Logic Status |
| 9780 | DO_LogicIndex_2 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | On Off - Logic Status |
| 9781 | DO_LogicIndex_3 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Alarm - Logic Status |
| 9782 | DO_LogicIndex_4 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Mode - Logic Status |
| 9783 | DO_LogicIndex_5 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Ext. Dampers - Logic Status |
| 9784 | DO_LogicIndex_6 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Bypass Damper - Logic Status |
| 9785 | DO_LogicIndex_7 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Damper - Logic Status |
| 9786 | DO_LogicIndex_8 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Damper - Logic Status |
| 9787 | DO_LogicIndex_9 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pump Preheat - Logic Status |
| 9788 | DO_LogicIndex_10 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pump Postheat - Logic Status |
| 9789 | DO_LogicIndex_11 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Pump - Logic Status |
| 9790 | DO_LogicIndex_12 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 1 - Logic Status |
| 9791 | DO_LogicIndex_13 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 2 - Logic Status |
| 9792 | DO_LogicIndex_14 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 3 - Logic Status |
| 9793 | DO_LogicIndex_15 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 4 - Logic Status |
| 9794 | DO_LogicIndex_16 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heat Pump - Logic Status |
| 9795 | DO_LogicIndex_17 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 1 - Logic Status |
| 9796 | DO_LogicIndex_18 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 2 - Logic Status |
| 9797 | DO_LogicIndex_19 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 3 - Logic Status |
| 9798 | DO_LogicIndex_20 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 1 - Logic Status |
| 9799 | DO_LogicIndex_21 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 2 - Logic Status |
| 9800 | DO_LogicIndex_22 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 3 - Logic Status |
| 9801 | DO_LogicIndex_23 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 1 - Logic Status |
| 9802 | DO_LogicIndex_24 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 2 - Logic Status |
| 9803 | DO_LogicIndex_25 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 3 - Logic Status |
| 9804 | DO_LogicIndex_26 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Humidifier - Logic Status |
| 9805 | DO_LogicIndex_27 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Rotary Wheel / Exchanger - Logic Status |
| 9806 | DO_LogicIndex_28 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 - Logic Status |
| 9807 | DO_LogicIndex_29 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 - Logic Status |
| 9808 | DO_LogicIndex_30 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Damper 2 - Logic Status |
| 9809 | DO_LogicIndex_31 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Damper 2 - Logic Status |
| 9810 | DO_free1 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9811 | DO_free2 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9812 | DO_free3 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9813 | DO_free4 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9814 | DO_free5 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9815 | DO_free6 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9816 | DO_free7 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9817 | DO_free8 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9818 | DO_free9 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9819 | DO_free10 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9820 | AO_LogicIndex_0 | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Fan |
| 9821 | AO_LogicIndex_1 | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Fan |
| 9822 | AO_LogicIndex_2 | Signed 16-bit | — | — | — | % | XXX.Y | R | Ext. Dampers |
| 9823 | AO_LogicIndex_3 | Signed 16-bit | — | — | — | % | XXX.Y | R | Bypass Damper |
| 9824 | AO_LogicIndex_4 | Signed 16-bit | — | — | — | % | XXX.Y | R | Cool - C/H Valve |
| 9825 | AO_LogicIndex_5 | Signed 16-bit | — | — | — | % | XXX.Y | R | Heat Valve |
| 9826 | AO_LogicIndex_6 | Signed 16-bit | — | — | — | % | XXX.Y | R | Pre Heater |
| 9827 | AO_LogicIndex_7 | Signed 16-bit | — | — | — | % | XXX.Y | R | Post Heater |
| 9828 | AO_LogicIndex_8 | Signed 16-bit | — | — | — | % | XXX.Y | R | Rotary Wheel / Exchanger |
| 9829 | AO_LogicIndex_9 | Signed 16-bit | — | — | — | % | XXX.Y | R | Humidifier |
| 9830 | AO_free1 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9831 | AO_free2 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9832 | AO_free3 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9833 | AO_free4 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9834 | AO_free5 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9835 | AO_free6 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9836 | AO_free7 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9837 | AO_free8 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9838 | AO_free9 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9839 | AO_free10 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9840 | AI_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9841 | AI_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9842 | AI_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9843 | AI_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9844 | AI_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9845 | AI_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9846 | AI_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9847 | AI_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9848 | AI_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9849 | AI_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9850 | AI_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9851 | AI_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9852 | AI_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9853 | AI_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9854 | AI_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9855 | AI_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9856 | AI_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9857 | AI_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9858 | AI_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9859 | AI_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9860 | AI_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9861 | AI_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9862 | AI_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9863 | DI_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9864 | DI_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9865 | DI_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9866 | DI_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9867 | DI_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9868 | DI_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9869 | DI_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9870 | DI_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9871 | DI_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9872 | DI_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9873 | DI_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9874 | DI_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9875 | DI_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9876 | DI_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9877 | DI_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9878 | DI_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9879 | DI_Map_LogicIndex_16 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9880 | DI_Map_LogicIndex_17 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9881 | DI_Map_LogicIndex_18 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9882 | DI_Map_LogicIndex_19 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9883 | DI_Map_LogicIndex_20 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9884 | DI_Map_LogicIndex_21 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9885 | DI_Map_LogicIndex_22 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9886 | DI_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9887 | DI_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9888 | DI_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9889 | DI_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9890 | DI_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9891 | DI_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9892 | DI_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9893 | DI_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9894 | DI_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9895 | DI_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9896 | DO_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9897 | DO_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9898 | DO_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9899 | DO_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9900 | DO_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9901 | DO_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9902 | DO_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9903 | DO_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9904 | DO_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9905 | DO_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9906 | DO_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9907 | DO_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9908 | DO_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9909 | DO_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9910 | DO_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9911 | DO_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9912 | DO_Map_LogicIndex_16 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9913 | DO_Map_LogicIndex_17 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9914 | DO_Map_LogicIndex_18 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9915 | DO_Map_LogicIndex_19 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9916 | DO_Map_LogicIndex_20 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9917 | DO_Map_LogicIndex_21 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9918 | DO_Map_LogicIndex_22 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9919 | DO_Map_LogicIndex_23 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9920 | DO_Map_LogicIndex_24 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9921 | DO_Map_LogicIndex_25 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9922 | DO_Map_LogicIndex_26 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9923 | DO_Map_LogicIndex_27 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9924 | DO_Map_LogicIndex_28 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9925 | DO_Map_LogicIndex_29 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9926 | DO_Map_LogicIndex_30 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9927 | DO_Map_LogicIndex_31 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9928 | DO_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9929 | DO_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9930 | DO_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9931 | DO_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9932 | DO_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9933 | DO_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9934 | DO_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9935 | DO_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9936 | DO_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9937 | DO_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9938 | AO_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9939 | AO_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9940 | AO_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9941 | AO_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9942 | AO_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9943 | AO_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9944 | AO_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9945 | AO_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9946 | AO_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9947 | AO_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9948 | AO_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9949 | AO_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9950 | AO_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9951 | AO_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9952 | AO_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9953 | AO_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9954 | AO_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9955 | AO_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9956 | AO_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9957 | AO_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9980 | Unit_DD | Unsigned 16-bit | — | — | — | days | — | R | Unit Working Days |
| 9981 | Unit_HH | Unsigned 16-bit | — | — | — | hours | — | R | Unit Working Hours |
| 9982 | FanSupply_DD | Unsigned 16-bit | — | — | — | days | — | R | Supply Fan Working Days |
| 9983 | FanSupply_HH | Unsigned 16-bit | — | — | — | hours | — | R | Supply Fan Working Hours |
| 9984 | FanReturn_DD | Unsigned 16-bit | — | — | — | days | — | R | Return Fan Working Days |
| 9985 | FanReturn_HH | Unsigned 16-bit | — | — | — | hours | — | R | Return Fan Working Hours |
| 9986 | FanSupplyBck_DD | Unsigned 16-bit | — | — | — | days | — | R | Supply Fan 2 Working Days |
| 9987 | FanSupplyBck_HH | Unsigned 16-bit | — | — | — | hours | — | R | Supply Fan 2 Working Hours |
| 9988 | FanReturnBck_DD | Unsigned 16-bit | — | — | — | days | — | R | Return Fan 2 Working Days |
| 9989 | FanReturnBck_HH | Unsigned 16-bit | — | — | — | hours | — | R | Return Fan 2 Working Hours |
| 10000 | Status_PlantMode | 0=Cool; 1=Heat; 2=Auto | — | 0 | 2 | — | — | R | Unit Working Mode |
| 10001 | Status_PID_TSupplyCool | Signed 16-bit | — | — | — | % | — | R | Cooling Regulator Request |
| 10002 | Status_PID_TSupplyHeat | Signed 16-bit | — | — | — | % | — | R | Heating Regulator Request |
| 10003 | Status_PID_Humid | Signed 16-bit | — | — | — | % | — | R | Hmidification Regulator Request |
| 10004 | Status_PID_DeHumid | Signed 16-bit | — | — | — | % | — | R | Dehumidification Regulator Request |
| 10005 | Status_PID_AirQ | Signed 16-bit | — | — | — | % | — | R | Air Quality Regulator Request |
| 10006 | Status_PID_PrSupply | Signed 16-bit | — | — | — | % | — | R | Supply Fan Regulator Request |
| 10007 | Status_PID_PrReturn | Signed 16-bit | — | — | — | % | — | R | Return Fan Regulator Request |
| 10008 | Status_PID_PreHeater | Signed 16-bit | — | — | — | % | — | R | Preheater Regulator Request |
| 10009 | Status_OutCool | Signed 16-bit | — | — | — | % | — | R | Cooling Output |
| 10010 | Status_OutPre | Signed 16-bit | — | — | — | % | — | R | Preheating Output |
| 10011 | Status_OutHeat | Signed 16-bit | — | — | — | % | — | R | Heating Output |
| 10012 | Status_OutPost | Signed 16-bit | — | — | — | % | — | R | Post Heating Output |
| 10013 | Status_OutRec | Signed 16-bit | — | — | — | % | — | R | Recovery Output |
| 10014 | Status_OutHum | Signed 16-bit | — | — | — | % | — | R | Humidifier Output |
| 10015 | Status_FanSupply | Signed 16-bit | — | — | — | % | — | R | Fan Supply Speed |
| 10016 | Status_FanReturn | Signed 16-bit | — | — | — | % | — | R | Fan Return Speed |
| 10017 | Status_ExtDamper | Signed 16-bit | — | — | — | % | — | R | External Damper Status |
| 10018 | Status_FreeCooling | Boolean | — | — | — | — | — | R | Free Cooling Status |
| 10019 | Status_FreeHeating | Boolean | — | — | — | — | — | R | Free Heating Status |
| 10020 | Status_ActuatorsOffbyFCH | Boolean | — | — | — | — | — | R | Actuators off by Free Cooling/Heating |
| 10021 | Status_FCHreq | Signed 16-bit | — | — | — | % | — | R | Free Cooling/Heating Request |
| 10022 | Status_RecoveryCooling | Boolean | — | — | — | — | — | R | Cooling Recovery Status |
| 10023 | Status_RecoveryHeating | Boolean | — | — | — | — | — | R | Heating Recovery Status |
| 10024 | Status_DefrostFan | Boolean | — | — | — | — | — | R | Defrost with Fan Status |
| 10025 | Status_DefrostDamper | Boolean | — | — | — | — | — | R | Defrost with Damper Status |
| 10026 | Status_DefrostPreHeat | Boolean | — | — | — | — | — | R | Defrost with Preheating Status |
| 10027 | Status_DefrostFanRed | Signed 16-bit | — | — | — | % | XXX.Y | R | Defrost Supply Fan Speed Reduction |
| 10028 | Status_LowTempSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | Low Supply Limit Regulator Request |
| 10029 | Status_HighTempSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Supply Limit Regulator Request |
| 10030 | Status_HighTempPreHeatLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Preheater Limit Regulator Request |
| 10031 | Status_HighHumSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Humidity Limit Regulator Request |
| 10032 | Status_ExtSHum | Signed 16-bit | — | — | — | g/Kg | XXX.Y | R | External Specific Humidity |
| 10033 | Status_RetSHum | Signed 16-bit | — | — | — | g/Kg | XXX.Y | R | Return Specific Humidity |
| 10034 | Status_Supply1_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Supply Ziehl/EBM Speed |
| 10035 | Status_Supply1_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Supply Ziehl/EBM DC Voltage |
| 10036 | Status_Supply1_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Supply Ziehl/EBM Current |
| 10037 | Status_Supply1_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Supply ATV212 Speed |
| 10038 | Status_Supply1_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply ATV212 DC Voltage |
| 10039 | Status_Supply1_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Supply ATV212 DC Current |
| 10040 | Status_Supply2_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Supply Backup Ziehl/EBM Speed |
| 10041 | Status_Supply2_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Supply Backup Ziehl/EBM DC Voltage |
| 10042 | Status_Supply2_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Supply Backup Ziehl/EBM Current |
| 10043 | Status_Supply2_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Supply Backup ATV212 Speed |
| 10044 | Status_Supply2_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Backup ATV212 DC Voltage |
| 10045 | Status_Supply2_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Supply Backup ATV212 DC Current |
| 10046 | Status_Return1_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Return Ziehl/EBM Speed |
| 10047 | Status_Return1_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Return Ziehl/EBM DC Voltage |
| 10048 | Status_Return1_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Return Ziehl/EBM Current |
| 10049 | Status_Return1_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Return ATV212 Speed |
| 10050 | Status_Return1_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Return ATV212 DC Voltage |
| 10051 | Status_Return1_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Return ATV212 DC Current |
| 10052 | Status_Return2_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Return Backup Ziehl/EBM Speed |
| 10053 | Status_Return2_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Return Backup Ziehl/EBM DC Voltage |
| 10054 | Status_Return2_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Return Backup Ziehl/EBM Current |
| 10055 | Status_Return2_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Return Backup ATV212 Speed |
| 10056 | Status_Return2_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Backup ATV212 DC Voltage |
| 10057 | Status_Return2_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Return Backup ATV212 DC Current |
| 10100 | StartMonth | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | Start Month - Log Period Export to USB |
| 10101 | EndMonth | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | End Month - Log Period Export to USB |
| 10102 | StartYear | Unsigned 8-bit | 16 | 0 | 99 | — | — | RW | Start Year - Log Period Export to USB |
| 10103 | EndYear | Unsigned 8-bit | 16 | 0 | 99 | — | — | RW | End Year - Log Period Export to USB |
| 10104 | SavingInProgress | Boolean | — | — | — | — | — | R | Log Export to usb ongoing - Log Export to USB |
| 10105 | SaveOk | Unsigned 16-bit | — | — | — | — | — | R | Number of files correctly exported- Log Export to USB |
| 10106 | SaveFailed | Unsigned 16-bit | — | — | — | — | — | R | Number of files not exported- Log Export to USB |
| 10107 | SavePercent | Unsigned 16-bit | — | — | — | — | — | R | Percentage of exported files- Log Export to USB |
| 10108 | SavingAllowed | Boolean | — | — | — | — | — | R | Export can start - Log Export to USB |
| 10109 | LoggingError | Boolean | — | — | — | — | — | R | Log Error- Log Export to USB |
| 10110 | FileDimension | Unsigned 32-bit | — | — | — | — | — | R | Size of the current log file- Log Export to USB |
| 10112 | TotalRecordE2retain | Unsigned 32-bit | — | — | — | — | — | R | Record saved - Log Export to USB |
| 10114 | microSdMounted | Boolean | — | — | — | — | — | R | microSD Mounted |
| 10115 | microSdError | Boolean | — | — | — | — | — | R | microSD Error |
| 10116 | microSdStatus | 0=Not present; 1=Unsafe Removed; 2=Not Mounted; 3=Mounted | — | 0 | 3 | — | — | R | microSd Status |
| 10117 | microSdInfo | 0=...; 1=Release SD; 2=Ready to remove/mount; 3=Ready for log; 4=...; 5=insert SD..; 6=Release SD; 7=Retry command..; 8=Yet mounted | — | 0 | 8 | — | — | R | microSd Info |
| 10498 | BridgeStatus | Boolean | — | — | — | — | — | R | Bridge Function Status |
| 11500 | MdbZiehlSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11501 | MdbZiehlReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11502 | MdbZiehlSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11503 | MdbZiehlReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11504 | MdbEBMSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11505 | MdbEBMReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11506 | MdbEBMSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11507 | MdbEBMReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11508 | MdbATVSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11509 | MdbATVReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11510 | MdbATVSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11511 | MdbATVReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11512 | MdbZiehlSupply_1b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11513 | MdbZiehlReturn_1b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11514 | MdbZiehlSupply_2b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11515 | MdbZiehlReturn_2b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11516 | MdbZiehlSupply_1c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11517 | MdbZiehlReturn_1c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11518 | MdbZiehlSupply_2c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11519 | MdbZiehlReturn_2c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11600 | CondUnit1_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 1 Working Days |
| 11601 | CondUnit1_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 1 Working Hours |
| 11602 | CondUnit2_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 2 Working Days |
| 11603 | CondUnit2_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 2 Working Hours |
| 11604 | CondUnit3_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 3 Working Days |
| 11605 | CondUnit3_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 3 Working Hours |
| 11606 | CondUnit4_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 4 Working Days |
| 11607 | CondUnit4_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 4 Working Hours |

Table 100 - Modbus Status Table