Air Handling Unit

FREE Advance

1.	Introduction	5

1.1.	Aim and usage of the manual	5

1.2.	Reference documentation	5

1.3.	Consulting the manual	5

1.4.	Glossary	6

1.5.	Formulation of intellectual property rights	6

2.	Product description	7

2.1.	Configurability in pairs of analogical inputs	7

2.2.	FREE Studio Device development environment	8

3.	Preliminary operations	9

3.1.	Power supply	10

3.2.	Programming the controller	11

3.2.1.	Programming from the Device	11

3.2.2.	Display programming	13

3.3.	Authentication with level 2 password	14

3.3.1.	Authentication from Device	14

3.3.2.	Authentication from the display	16

4.	Controller configuration	17

4.1.	Configuration from the Device	18

4.1.1.	“U-Oem_UnitConfiguration” Folder	19

4.1.2.	“O3-I/O_Allocate” Folder	20

4.1.3.	“O1-I/O_Polarity” Folder	23

4.1.4.	“O2-I/O_TestOutput” Folder	24

4.1.5.	“S5-Service_Log” Folder	24

4.1.6.	“S6-Service_Def” Folder	25

4.1.7.	Folders relative to the EEProm parameters	26

4.2.	Configuration from the display	28

4.3.	Example of configuration	30

5.	Modbus Tables	35

5.1.	Modbus EEProm table	35

5.2.	Modbus Status Table	36

Introduction

Aim and usage of the manual

This manual is an integral part of the product and is to be solely used by the Air Handling Unit (AHU) Manufacturer.

This manual aims to provide all the information needed to:

correctly carry out all the operations foreseen during the product configuration stages

guarantee the health safety and protection of staff working on the product in different roles.

This Manual must be read carefully in its entirety before carrying out any operation on the product. If in doubt regarding the correct interpretation of the instructions found herein, contact the Manufacturer for further clarification.

This manual must be stored in a safe place for the entire lifespan of the product. Only the Manufacturer can keep it and it must be stored in a place protected against atmospheric agents, heat, humidity and corrosive agents; care must be taken when consulting it to prevent it getting damaged, pages should not be removed nor its content changed in any way.

Reference documentation

Reference is made further on in this Manual to the following documents.

| Document name | Document Code |
| --- | --- |
| Air Handling Unit FREE Advance | 9MA10026 (ENG) ¦ 9MA00276 (ITA) |
| User Guide FREE Studio | 9MA10055 (ENG) ¦ 9MA00255 (ITA) |
| User Guide FREE Advance | 9MA10065 (ENG) ¦ 9MA00265 (ITA) |

Table 1 - Reference documentation

Consulting the manual

The information in the Manual is arranged as follows:

chapters,

sub-chapters,

paragraphs,

sub-paragraphs

and these can easily be found by consulting the Index at the start of this Manual.

In order to capture the user's attention so that the product is used properly and safely, the following convention is adopted in the Manual:

NOTE: The symbol is used to supply regulations or updates that are useful to the users.

Glossary

| Term | Meaning | References for further information |
| --- | --- | --- |
| Allocation | Assigning specific configurations to inputs and/or outputs of a programmable controller | User Guide FREE Advance Air Handling Unit FREE Advance |
| Base board | Base board relative to the ADV8400 programmable controller and ADV12600 programmable controller | User Guide FREE Advance |
| Upper board | Upper board relative to the ADV12600 programmable controller | User Guide FREE Advance |
| Hidden parameters | Parameters hidden from the user and installer but visible to the Manufacturer | 5 Modbus Tables on pag. 35 |
| Visible parameters | Parameters visible to the user, installer and the Manufacturer | Air Handling Unit FREE Advance 5 Modbus Tables on pag. 35 |
| Memory volume (of the controller) | Physical allocation of a memorisation unit relative to a programmable controller | / |

Table 2 - Glossary

Formulation of intellectual property rights

This publication is the exclusive property of the Manufacturer, who completely prohibits any reproduction or distribution if not expressly authorised by the Manufacturer himself.

Every care has been taken in the preparation of this Manual; however the Manufacturer and any person or company involved in its creation and writing cannot accept any liability arising from the use thereof. The Manufacturer reserves the right to make changes or improvements at any time without notice.

Product description

The product is an AVD controller programmed for application on Air Handling Units (AHU).

The programmed AVD controller can be one of the two described in the following table.

| AVD8400 | FREE Advance with display, 28 I/Os |
| --- | --- |
| AVD12600 | FREE Advance with display, 42 I/Os |

Table 3 - Programmed AVD controller

The following can be applied to the programmed AVD controller:

up to two EVE4200 expansions

up to two remote graphic EVK1000 terminals.

The choice of the programmed AVD controller and the number and kind of devices possibly applied to it is a function of the Air Handling Unit hardware configuration (for further reference see Air Handling Unit FREE Advance).

NOTE: In the continuation of this Manual:

the programmed AVD controller will be shown with the term “controller”

the Air Handling Unit will be indicated with the term “AHU” or “UTA” (in \path\ and PLC name)

the application on AHU with which the controller is programmed will be indicated with the term “applicative”.

Alternatively, the controller can be handled:

via controller display and keyboard (see User Guide FREE Advance and Air Handling Unit FREE Advance)

via FREE Studio Device development environment (see 2.2 FREE Studio Device development environment on pag. 8).

Configurability in pairs of analogical inputs

The programmed AVD controller is fitted with inputs and outputs that can be configured to handle signals.

Both the AVD8400 and AVD12600 controllers are fitted with the following analogical inputs:

AI1, AI2, AI3, AI4, AI5, AI6, AI7, AI8.

The AVD12600 controller alone is also fitted with the following analogical inputs:

AI9, AI10, AI11, AI12.

As described in the following table, the relative analogical inputs:

on the base board can be configured in pairs

on the upper board have a configuration fixed by the applicative.

NOTE: The AVD8400 controller is fitted with the single base board, the AVD12600 controller is fitted with both base board and upper board.

| Pairs of analogical inputs | Board on which the analogical input pairs can be found | Configurability of the pairs of analogical inputs |
| --- | --- | --- |
| AI1, AI2 | Base board | Configurable |
| AI3, AI4 | Base board | Configurable |
| AI5, AI6 | Base board | Configurable |
| AI7, AI8 | Base board | Configurable |
| AI9, AI10 | Upper board | Configurable |
| AI11, AI12 | Upper board | Configurable |
| AI1, AI2 | EVE4200 | Fixed equal to NTC (103AT) |
| AI3, AI4 | EVE4200 | Fixed equal to 0-10V |

Table 4 - Configurability in pairs of analogical inputs

For each pair of configurable analogical inputs, not all signals can be purchased simultaneously (for further information see User Guide FREE Advance).

FREE Studio Device development environment

In the case of configuration via FREE Studio suite software, the version used must be 3.6 or higher.

FREE Studio Device development environment allows for:

the management of previously developed IEC applications

the IEC applications to be transferred onto the controller (target)

the controller parameters to be changed by a serial communication port (USB, Ethernet, RS485)

the volume of the controller to be changed where the applicative is downloaded (see 3.2.1.1. Download of parts of an applicative on pag.11).

NOTE: At a later date in this Manual, the FREE Studio Device development environment will be indicated with the term “Device”.

NOTE: For further information on the Device see the User Guide FREE Studio.

NOTE: The applicative does not support the LON (LonWorks) protocol.

Preliminary operations

The switch-on procedure foresees:

power supply of the controller referring to 3.1 Power supply on pag.10

possible programming of the controller referring to 3.2 Programming of the controller on pag.11

authentication with a level 2 password and with reference to 3.3 Authentication with level 2 password on pag.14.

The controller foresees three different levels of password, depending on the operations permitted to the relative user, as indicated in the following table.

| Password level | User | User password (default values) |
| --- | --- | --- |
| 0 | User | - |
| 1 | Installer | 10 |
| 2 | Manufacturer | 220 |

Table 5 - Password levels

NOTE: Access to password level 2 is only permitted when the AHU is in the OFF status.

NOTE: At a later date in this Manual, the following will respectively be indicated with the term “value camp”:

for the Device settings, the cell (1 - Fig 1 -  on pag. 9) of the value column in correspondence with a parameter

for the controller settings, the data (2 - Fig 1 -  on pag. 9) shown after a parameter.

A parameter whose value field can be viewed from a drop down menu on Device is normally associated with an enumeration on the controller display.

Fig 1 - Value field

Power supply

In order to power the controller, connect the controller to the PC via a USB cable fitted with the following two connectors at the ends:

Type-A male connector

mini-B connector

NOTE: If the controller is powered directly from the PC via the USB cable, during the next configuration (see 4.1 Configuration from Device on pag. 18) it is forbidden to carry out other operations on the controller. As an alternative to the connection via USB cable, it is possible to power the controller via 24 Vac/dc power and connect via Ethernet port or RS485 port.

Programming the controller

In order to programme from the Device see 3.2.1. Programming from the Device on pag.11.

In order to programme from the display see 3.2.2. Programming from the display on pag.13.

Programming from the Device

In the event of further use of the Device, carry out the following operations in this order:

- start Device

open the “UTA.CFN” file

connect the controller to the Device

activate the Auto refresh mode

NOTE: in the even of de-activation of the Auto refresh mode, it is essential to supply a W written command after changing each value in Device.

if you wish to use the datalogging:

insert a microSD in the relative slot on the controller

empty the web browser cache

select the “FileSystem Volumes” folder (see User Guide FREE Advance) in the “UTA/Advance_UTA/BIOS parameters/
All parameters” path

select “1=microSD card” in the value field of the HTTP_volume parameter to save the WebServer on microSD

NOTE: The log data and WebServer need to be saved in the same saving volume: in the event of datalogging activation, both the log data and the WebServer need to be saved on microSD. It is only possible to change the file system of the HTTP volume from the Device (for further information see 3.2.1.1 Download of the parts of an applicative on pag. 11).

Download of the parts of an applicative

Each controller applicative is made up of the following parts (1 - Fig 2 - on pag. 12):

PLC

HMI

Remote HMI

Cfg files

Web site.

It is possible to download each part in one of the two memory volumes (2 - Fig 2 - on pag. 12) shown below:

NOR, memory volume inside the controller

SD, memory volume on the microSD board out-with the controller.

NOTE: The memories map, NOR and SD, where each part of an applicative is saved following a download onto the controller is defined as “Download settings”.

To download the parts of an applicative, carry out the following operations in this order:

- select “Advance_UTA” in the Device Project panel

in the drop down menu of the “Download settings” box:

select “Use target settings” (3 - Fig 2 - on pag. 12) to use the Download settings defined in the AVD controller

select “Use manual settings” (4 - Fig 2 - on pag. 12) to manually change the Download settings

if “Use manual settings” has already been selected, click the flags that correspond with “NOR” or “SD” to manually select the volume of memory in which each part of the applicative is downloaded

click “Download All” to download the applicative parts onto the controller.

Fig 2 - “Download settings” box

Display programming

Carry out the following operations in order:

- copy the files found in the USB_AVD8400 or USB_AVD12600 folder onto a USB stick, depending on the controller model

insert the USB key in the USB port on the controller

wait until automatic download of the files onto the controller is complete.

Authentication with level 2 password

In order to authenticate from the Device see 3.3.1. Authentication from the Device on pag.14.

In order to authenticate from the display see 3.3.2. Authentication from the display on pag.16.

Authentication from Device

Carry out the following operations in order:

- select the “G-Password_Entry” folder in the “UTA/Advance_UTA/Application/PLC” path of the Device Project panel

Fig 3 - “G-Password_Entry” Folder

visually read the level of current password in the value field of the PSWLevel parameter (1 - Fig 3 - on pag. 14);

in the event of a password level that is not 2, select the “W-Oem_Password” folder in the “UTA/Advance_UTA/Application/PLC” path of the Device Project panel

Fig 4 - “W-Oem_Password” Folder

NOTE: The “W-Oem_Password” folder (Fig 4 - on pag. 14) allows for the password to be managed and the “Factory.raw” configuration file in the file system to be saved. For further information on “Factory.raw” file, see 3.3.1.1 “Factory.raw” File on pag.15.

visually read the value field of the PSW2 parameter (2 - Fig 4 - on pag. 14),visualised in hexadecimal format

calculate the completion of the value field previously read visually in correspondence with the PSW2 parameter

select the “G-Password_Entry” folder

edit the value previously calculated on the value field of the PSWEntry parameter (3 - Fig 3 - on pag. 14) in decimal format.

NOTE: For example, if the PSW2 parameter value field is equal to “FF23” (hexadecimal), in order to access level 2 password, write “220” (decimal) in the PSWEntry parameter value field.

For further information on the parameters found in the previous folders see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

“Factory.raw” File

The “factory.raw” file is a text file with the same formatting as the param.dat files that hold all the configuration parameters. In order to create this file, click “True” in the SaveFactoryCommand in the “W-Oem_Password” folder in the parameter value field. This file is saved in the controller’s internal file system (NOR) and can be used:

to archive the parameter configuration

to reset a specific controller configuration.

This file contains the configuration of all the parameters or a sub-group of them if manually created by the Manufacturer.

NOTE: The header of the “factory.raw” file and more generally speaking of the param.dat files, depends on the kind of controller, as this differs between AVD8400 and AVD12600.

For additional information consult the Air Handling Unit FREE Advance.

Authentication from the display

For information on the parameters which are referred to in the different menus of the controller, see Air Handling Unit FREE Advance.

Carry out the following operations in order:

- select the “G-Password” menu

visually read the level of current password in the value field of the PSWLevel parameter

if the password level is not 2, select the “W-Password” menu

visually read the value field of the PSW2 parameter, visibly displayed in decimal format

calculate the completion of the value field previously read visually in correspondence with the PSW2 parameter

select the “G-Password” menu

edit the value previously calculated on the value field of the PSWEntry parameter in decimal format.

NOTE: For example, if the PSW2 parameter value field is equal to “FF23” (hexadecimal), in order to access level 2 password, write “220” (decimal) in the PSWEntry parameter value field.

NOTE: For further information on the parameters found in these menus, see Air Handling Unit FREE Advance.

Controller configuration

In order to configure the controller, the following is required:

that the controller has been previously programmed with the applicative

if you wish to use the data-logging, that a microSD has been inserted in the relative controller slot (see 3.2.1 Programming from the Device on pag. 11).

The controller can be configured with an automatic procedure that allocates the inputs and outputs according to the AHU configuration set; to set the AHU configuration, see 3.2.1 “U-Oem_UnitConfiguration” Folder on pag.19. After setting the AHU configuration, it is possible to allocate the resources automatically (see 3.2.2 “O3-I/O_Allocate” Folder on pag. 20).

The controller can be configured in one of the following two ways:

from the Device

from the display.

The configuration from the Device foresees the setting of the parameters in the Device Project panel folders (for further information see User Guide FREE Advance and User Guide AHU).

Configuration from the display foresees setting parameters on the controller display, in the menus and sub-menus of the “H-System” menu (for further information see User Guide AHU).

A menu or sub-menu of the “H-System” menu corresponds with each folder in the Project panel, as described in the table below.

| Device Project panel folder | Controller menu or sub-menu |
| --- | --- |
| G-Password_Entry | G-Password |
| U-Oem_UnitConfiguration | U-Unit Configuration (sub-menu of the “H-System” menu) |
| O3-I/O_Allocate | O3-I/O Allocation (sub-menu of the “H-System” menu) |
| O1-I/O_Polarity | O1-Polarity (sub-menu of the “H-System” menu) |
| O2-I/O_TestOutput | O2-Test Out (sub-menu of the “H-System” menu) |
| W-Oem_Password | W-Password (sub-menu of the “H-System” menu) |
| S5-Service_Log | S5-Data Logger (sub-menu of the “H-System” menu) |
| S6-Service_Def | S6-Restore Factory (sub-menu of the “H-System” menu) |

Table 6 - Correspondence between Device and display

NOTE: The “O3-I/O_Allocate” folder contains the parameters stored in the RAM relative to the allocations of the I/O: to allocate them effectively in the controller, they need to be saved in EEProm. The I/Os effectively allocated in the controller are relative to the parameters stored in the EEProm and found in the following folders:

HIDDEN_EEPROM_SAVED_IO_Allocation

Lower Board

Upper board.

For further information see 3.2.7 Folders relative to EEProm parameters on pag. 26.

In order to configure the controller from the Device see 4.1 Configuration from the Device on pag. 18.

In order to configure the controller from the display see 4.2 Configuration from the display on pag. 28.

Configuration from the Device

For information on the parameters which are referred to in the different menus of the controller, see Air Handling Unit FREE Advance and User Guide FREE Studio.

The configuration from the Device foresees one or more of the following configurations to be activated:

AHU hardware definition

Allocation and definition of types and controller input and output ranges

Definition of input and output polarities

For each possible kind of configuration to be activated, carry out the following operations in order:

- select the corresponding folder shown in the following table

carry out the operations shown in the reference paragraph of the selected folder

| Configuration type | Folder | Folder path (Device Project panel) | Reference paragraph |
| --- | --- | --- | --- |
| A | U-Oem_UnitConfiguration | UTA/Advance_UTA/Application/PLC | 3.2.1 “U-Oem_UnitConfiguration” Folder on pag. 19 |
| B | O3-I/O_Allocate | UTA/Advance_ UTA /Application/PLC | 3.2.2 “O3-I/O_Allocate” Folder on pag. 20 |
| C | O1-I/O_Polarity | UTA/Advance_ UTA /Application/PLC | 3.2.3 “O1-I/O_Polarity” Folder on pag. 23 |

Table 7 - Configuration types

NOTE: It is possible (but not recommended) to allocate and define input and output types and ranges on the following folders (see 3.2.7 Folders relative to EEProm parameters on pag.26):

“HIDDEN_EEPROM_SAVED_IO_Allocation” folder

“Lower Board” folder

“Upper Board” folder

inside of which are the same parameters of the “O3-I/O_Allocate” folder, but any possible change carried out within this cannot be restored.

if you wish to carry out tests on the outputs:

select the “O2-I/O_TestOutput” folder (see 3.2.4 “O2-I/O_TestOutput” Folder on pag. 24) in the “UTA/Advance_UTA/
Application/PLC” path of the Device Project panel

carry out the operations shown in the reference paragraph of the selected folder

if you wish to create/overwrite the “factory.raw” file:

select the “W-Oem_Password” folder (see 3.3.1 Authentication from Device on pag. 14) in the “UTA/Advance_UTA/
Application/PLC” path of the Device Project panel

select “True” in the value field of the SaveFactoryCommand parameter

NOTE: For further information on “factory.raw” file, see 3.3.1.1 “Factory.raw” File on pag.15.

if you wish to activate the datalogging:

select the “S5-Service_Log” folder (see 3.2.5 “S5-Service_Log” Folder on pag. 24) in the “UTA/Advance_UTA/
Application/PLC” path of the Device Project panel

select “True” from the parameter value “LogEnable” field to activate the datalogging.

if you wish to reset the parameters of the default values:

select the “S6-Service_Def” folder (see 3.2.6 “S6-Service_Def” Folder on pag. 25) in the “UTA/Advance_UTA/
Application/PLC” path of the Device Project panel

select “True” in the value field of the RestoreFactoryCommand parameter.

In 4.3 Example of configuration on pag. 29 a configuration example of the controller from Device is given.

“U-Oem_UnitConfiguration” Folder

The “U-Oem_UnitConfiguration” Folder (Fig 5 - on pag. 19) allows for the management of AHU hardware configuration.

Fig 5 - “U-Oem_UnitConfiguration” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

It is possible to change the parameters in the “U-Oem_UnitConfiguration” folder using the USB stick only if the level of password set is 2.

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

“O3-I/O_Allocate” Folder

The “O3-I/O_Allocate” Folder (Fig 6 - on pag. 20) allows for the management of the allocations and definition of input and output types and ranges.

Fig 6 - “O3-I/O_Allocate” Folder

In order to allocate the inputs and/or outputs, carry out the following operations in order:

- in the central panel, click on the value field of the AllocationCmdSet parameter to view the relative drop down menu described in the following table:

| Commands in the drop down menu | Description |
| --- | --- |
| 1=Load Stored | Load the last configuration of the allocation of the I/Os saved on the controller |
| 2=Auto Allocation | Allocate all the default I/Os requested by the configuration selected automatically |
| 3=Save into Stored | Save the current configuration of the allocation of the I/Os in EEProm |
| 4=Clear All | Delete the current configuration of the allocation of the I/Os |
| 18=Auto Allocation AI | Allocate all the default analogical inputs requested by the configuration selected automatically |
| 19=Save Allocation AI | Save the current configuration of the allocation of the analogical inputs in EEProm |
| 20=Clear AI | Delete the current configuration of the allocation of the analogical inputs |
| 34=Auto Allocation DI | Allocate all the default analogical inputs requested by the configuration selected automatically |
| 35=Save Allocation DI | Save the current configuration of the allocation of the digital inputs in EEProm |
| 36=Clear DI | Delete the current configuration of the allocation of the digital inputs |
| 50=Auto Allocation DO | Allocate all the default digital outputs requested by the configuration selected automatically |
| 51=Save Allocation DO | Save the current configuration of the allocation of the digital outputs in EEProm |
| 52=Clear DO | Delete the current configuration of the allocation of the digital outputs |
| 66=Auto Allocation AO | Allocate all the default analogical outputs requested by the configuration selected automatically |
| 67=Save Allocation AO | Save the current configuration of the allocation of the analogical outputs in EEProm |
| 68=Clear AO | Delete the current configuration of the allocation of the analogical outputs |

Table 8 - Commands in the drop down menu - “AllocationCmdSet” parameter

NOTE: For further information:

about the automatic allocation commands described in the previous table, see 3.2.2.1 Automatic allocation commands on pag.22

about the saving commands described in the previous table, see 3.2.2.2 Saving commands in EEProm on pag.22

about the loading command described in the previous table, see 3.2.2.3 Loading command in RAM on pag.22.

in the previous drop down menu selected, click the command required

wait a few seconds until you see the value “0=Idle” in the value field

in the event of automatic allocation:

check compatibility of the configuration obtained with the configuration desired and the Configurability in pairs of the analogical inputs (see 2.1 Configurability in pairs of analogical inputs on pag. 7)

in the event of incompatibility of the configuration obtained with the desired configuration, manually allocate the inputs and/or outputs until you obtain the required configuration (see User Guide FREE Advance)

for each analogical voltage/ current input, define the relative range of acquisition:

edit the start of scale value in correspondence with the value field of the relative parameter with “min” suffix

edit the end of scale value in correspondence with the value field of the relative parameter with “max” suffix.

NOTE: It is not necessary to allocate all the inputs and outputs defined by the applicative; for example:

in the case of hot actuators or cold actuators, it is possible to activate the moto-condensation via the only analogical output or alternatively the only digital output

in the event of summer/winter mode change, if the relative digital input is allocated, the relative key does not appear on the display (see User Guide FREE Advance and Air Handling Unit FREE Advance).

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

Automatic allocation commands

The automatic allocation commands described in the previous table:

2=Auto Allocation,

18=Auto Allocation AI,

34=Auto Allocation DI,

50=Auto Allocation DO,

66=Auto Allocation DO

do not attribute the types of input and/or output according to the kind of sensor. The controller automatic inputs can be configured in pairs (see 2.1 Configurability in pairs of analogical inputs on pag. 7), so in the case of automatic allocation that regards analogical inputs ("2=Auto Allocation” and “18=Auto Allocation AI” commands) it is always advisable to check the compatibility of the configuration obtained with the configurations issued by the controller.

Saving commands in EEProm

The saving commands described in the previous table allow you to write the value fields of the parameters obtained in the “O3-I/O_Allocate” (RAM) folder in the value fields of the parameters found in the following folders (EEProm):

HIDDEN_EEPROM_SAVED_IO_Allocation,

Lower Board,

Upper board

NOTE: For further information on the folders relative to the EEProm parameters see 3.2.7 Folders relative to EEProm parameters on pag. 26.

Loading commands in RAM

The loading command described in the previous table allows you to write the value fields of the parameters found in the following folders (EEProm):

HIDDEN_EEPROM_SAVED_IO_Allocation,

Lower Board,

Upper board

in the value fields of the parameters found in the “O3-I/O_Allocate” (RAM) folder.

NOTE: For further information on the folders relative to the EEProm parameters see 3.2.7 Folders relative to EEProm parameters on pag. 26.

“O1-I/O_Polarity” Folder

The “O1-I/O_Polarity” Folder (Fig 7 - on pag. 23) allows for the management of the input and output polarities.

Fig 7 - “O1-I/O_Polarity” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

“O2-I/O_TestOutput” Folder

The “O2-I/O_TestOutput” folder (Fig 8 - on pag. 24) allow for tests to be carried out on the outputs.

Fig 8 - “O2-I/O_TestOutput” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

“S5-Service_Log” Folder

The “S5-Service_Log” (Fig 9 - on pag. 24) allows for the enabling and configuring of the sample time of the data-logging.

Fig 9 - “S5-Service_Log” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

“S6-Service_Def” Folder

The “S6-Service_Def” folder (Fig 10 - on pag. 25) allows for the parameters found in the Factory.raw file to be reset. The command is carried out only if the level 1 password is active.

Fig 10 - “S6-Service_Def” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding menus of the controller described in Air Handling Unit FREE Advance.

Folders relative to the EEProm parameters

Device allows you to view the folders relative to the EEProm parameters. The following is a description of the folders that allow for the management of the allocations and definition of input and output types and ranges.

“HIDDEN_EEPROM_SAVED_IO_Allocation” Folder

The “HIDDEN_EEPROM_SAVED_IO_Allocation” Folder (Fig 11 - on pag. 26) allows for the management of the allocations and definition of input and output types with irreversible changes.

Fig 11 - “HIDDEN_EEPROM_SAVED_IO_Allocation” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see Air Handling Unit FREE Advance.

“Lower Board” folder

The “Lower Board” folder (Fig 12 - on pag. 27) permits the management of base board inputs and outputs.

Fig 12 - “Base board” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding controller menu described in the User Guide FREE Advance.

“Upper Board” Folder

The “Upper Board” folder (Fig 13 - on pag. 27) permits the management of upper board inputs and outputs.

Fig 13 - “Upper board” Folder

In order to set each item, according to the kind of parameter, select the drop down menu or edit the number in correspondence with the relative value field.

NOTE: For further information on the parameters found in this folder, see the corresponding controller menu described in the User Guide FREE Advance.

Configuration from the display

For information on the parameters which are referred to in the different menus of the controller, see Air Handling Unit FREE Advance.

The configuration from the display foresees one or more of the following configurations to be activated:

- AHU hardware definition

- Allocation and definition of types and controller input and output ranges

- Definition of input and output polarities

For each kind of configuration, carry out the following operations in order:

- select the corresponding menu shown in the following table

select the parameter you want to change

press OK to enter the edit mode

press the controller UP/DOWN keys to increase/decrease the value

press the controller OK key to confirm or keep the LEFT key pressed down to cancel

| Configuration type | Menu | On-screen display |
| --- | --- | --- |
| A | U-Unit Configuration |  |
| B | O3-I/O Allocation |  |
| C | O1-Polarity |  |

Table 9 - Configuration types

NOTE: It is possible to change the parameters in the “U-Oem_UnitConfiguration” menu using the USB stick only if the level of password set is 2.

if you wish to carry out tests on the outputs:

select the “O2-I/O_TestOutput” folder

select the parameter you want to change

press OK to enter the edit mode

press the controller UP/DOWN keys to increase/decrease the value

press the controller OK key to confirm or keep the LEFT key pressed down to cancel

NOTE: The configuration stored in the EEProm memory can be saved on a USB stick to archive or copy it onto another device.

if you wish to create/overwrite the “factory.raw” file containing the current configuration:

select the “W-Password” menu

press the “Save Factory” key

NOTE: For further information on the “factory.raw” file, see 3.3.1.1 “Factory.raw” File on pag. 15.

if you wish to start the data-logging:

select the “S5-Data Logger” menu

select “True” from the parameter value “LogEnable” field to activate the datalogging.

if you wish to reset the parameters of the default values:

select the “S6-Service_Def” menu

press the “Restore” key.

Example of configuration

The following table provides an example of hardware configuration for each part of the AHU.

| AHU components | Hardware configuration |
| --- | --- |
| Discharge fan | ON/OFF without back-up |
| Recovery fan | ON/OFF without back-up |
| Multi-purpose hot/cold battery | Modulating valve |
| Post-heating battery | Modulating valve |
| Recovery unit flows overlapping with the bypass damper | Proportional to batteries |
| External dampers | ON/OFF |

Table 10 - Example of hardware configuration

NOTE: For further information on the AHU hardware configuration, see Air Handling Unit FREE Advance.

The controller software defines the I/Os requested according to the components and the hardware configuration of the AHU. The I/Os requested according to the example of hardware configuration are shown in the following table.

| Components of the AHU configuration | DI | AI (NTC) | AI (UNIV) | DO | AO |
| --- | --- | --- | --- | --- | --- |
| Discharge fans (in ON/OFF configuration without back-up) | — | — | — | 1 | — |
| Recovery fans (in ON/OFF configuration without back-up) | — | — | — | 1 | — |
| Multi-purpose hot/cold battery (in configuration modulating valve) | — | — | — | — | 1 |
| Post-heating battery (in configuration modulating valve) | — | — | — | — | 1 |
| Overlapping flow recovery unit (in configuration proportional to the batteries) | — | — | — | 1 | 1 |
| External dampers | — | — | — | 1 | — |

Table 11 - I/Os requested according to the example of hardware configuration

In order to implement the hardware configuration example via Device, carry out the following operations in order:

- carry out the switch on procedure from the Device referring to 3.2 Controller programming on pag.11

change the following parameters on the “U-Oem_UnitConfiguration” folder (Fig 14 -  on pag. 31) compared to the default configuration as indicated in the following table

Fig 14 - Example of configuration - “U-Oem_UnitConfiguration” folder

| Reference | Components of the AHU configuration | Parameter to be configured | Value field selected |
| --- | --- | --- | --- |
| 1 | Discharge fan + recovery fan | cfgFans | 1=Supply+Return |
| 2 | Hot battery and cold battery (single components) | cfgCoolHeatModules | 4=Cool/Heat Single Out |
| 3 | Post-heating battery | cfgPostHeating | 1=Modulating Valve |
| 4 | Overlapping flow recovery unit | cfgHeatRecovery | 6=Exchanger mode |

Table 12 - Parameter settings relative to the “U-Oem_UnitConfiguration” folder

set the parameters in the “O3-I/O_Allocate” folder (Fig 15 -  on pag. 32 and Fig 16 -  on pag. 33) as indicated in the following table

Fig 15 - Example of configuration - “O3-I/O_Allocate”-1 folder

Fig 16 - Example of configuration - “O3-I/O_Allocate”-2 folder

| Reference | Components of the AHU configuration | Parameter to be configured | Value field selected |
| --- | --- | --- | --- |
| 1 | Temperature discharge probe | ioSV_base_AI_01 | 0=Supply Temp. |
| 2 | Temperature recovery probe | ioSV_base_AI_02 | 1=Return Temp. |
| 3 | Temperature external probe | ioSV_base_AI_03 | 2=External Temp. |
| 4 | Remote ON / OFF input | ioSV_base_DI_01 | 2=On Off |
| 5 | Fire alarm | ioSV_base_DI_02 | 3=Fire Alarm |
| 6 | Discharge fan protection alarm | ioSV_base_DI_03 | 0=Supply Fan Th.Prot. |
| 7 | Recovery fan protection alarm | ioSV_base_DI_04 | 1=Return Fan Th.Prot. |
| 8 | Rotating recovery alarm | ioSV_base_DI_05 | 12=Rotary Heat Exch. Alarm |
| 9 | ON/OFF AHU status | ioSV_base_DO_01 | 2=On Off |
| 10 | Alarm | ioSV_base_DO_02 | 3=Alarm |
| 11 | Discharge fan | ioSV_base_DO_03 | 0=Supply Fan |
| 12 | Recovery fan | ioSV_base_DO_04 | 1=Return Fan |
| 13 | External dampers | ioSV_base_DO_05 | 5=Ext. Dampers |
| 14 | Modulating valve | ioSV_base_AO_01 | 4=Cool / Cool-Heat |
| 15 | Post-heating valve | ioSV_base_AO_02 | 7=Post Heater |
| 16 | Recovery unit | ioSV_base_AO_03 | 8=Recovery |

Table 13 - Settings of parameters relative to the “O3-I/O_Allocate” folder

click “Download All”.

NOTE: The ON/OFF and Fire inputs and the alarm and ON/OFF alarms are always allocated by default.

NOTE: In the case of a cooling battery in moto-condensation configuration:

the number of digital outputs allocated by the controller equals the cfgCoolHeat_NumSteps parameter

the only possible analogical output cannot be allocated automatically but only manually.

Modbus Tables

NOTE: In the following tables:

in the case of XXX.Y format, divide the value found in the relative register by 10

in the case of XXX.YY format, divide the value found in the relative register by 100.

Modbus EEProm table

The following table describes the hidden EEProm parameters.

NOTE: For visible EEProm parameters, see chapter on Modbus Tables in Air Handling Unit FREE Advance.

| Modbus Register | Name | Device Type | Def | Unit | Description |
| --- | --- | --- | --- | --- | --- |
| 18499...19499 | — | — | — | — | Area reserved for alarm archive |
| 19504 | EE_RTCerror | Unsigned 8-bit | 0 | — | — |
| 19799 | ENDINTERNAL | Boolean | 0 | — | — |
| 19800 | UnitHoursE2 | Unsigned 32-bit | 0 | Hours | Unit Hours |
| 19802 | FanSupplyHoursE2 | Unsigned 32-bit | 0 | Hours | Fan Supply Running Hours |
| 19804 | FanReturnHoursE2 | Unsigned 32-bit | 0 | Hours | Fan Return Running Hours |
| 19806 | FanSupplyBckHoursE2 | Unsigned 32-bit | 0 | Hours | Fan Supply Backup Running Hours |
| 19808 | FanReturnBckHoursE2 | Unsigned 32-bit | 0 | Hours | Fan Return Backup Running Hours |

Table 14 - Modbus EEProm Table

Modbus Status Table

The following table describes the hidden Status parameters.

NOTE: Per i parametri Stati di tipo visible fare riferimento al capitolo Tabelle Modbus in Air Handling Unit FREE Advance.

| Modbus Register | Name | Device type | Def | Min | Max | Unit | Format | RW | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 8960 | Allocation CmdSet | 0 = 0=Idle; 1 = 1=Load Stored; 2 = 2=Auto Allocation; 3 = 3=Save into Stored; 4 = 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | — | — | — | — | RW | Allocation command |
| 8961 | Allocation NextResReq | Signed 16-bit | -1 | — | — | — | — | RW | Used by HMI to get the next available logic resource |
| 8962 | ioSV_base_AI_01 | -1 = -1=Not Used; 0 = 0=Supply Temp.; 1 = 1=Return Temp.; 2 = 2=External Temp.; 3 = 3=Expulsion Temp.; 4 = 4=Preheat Temp.; 5 = 5=Saturation Temp.; 6 = 6=Antifreeze; 7 = 7=Air Quality CO2; 8 = 8=Air Quality VOC; 9 = 9=Pressure 1; 10 = 10=Pressure 2; 11 = 11=Supply Hum.; 12 = 12=Return Hum.; 13 = 13=External Hum.; 14 = 14=Flow Tuning 1; 15 = 15=Flow Tuning 2 | -1 | — | — | — | — | RW | Temporary: Logic Allocation of the physical input |
| 8963 | ioSV_base_AI_02 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8964 | ioSV_base_AI_03 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | Save command required to be effective |
| 8965 | ioSV_base_AI_04 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8966 | ioSV_base_AI_05 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8967 | ioSV_base_AI_06 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8968 | ioSV_base_AI_07 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8969 | ioSV_base_AI_08 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8970 | ioSV_base_AI_09 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8971 | ioSV_base_AI_10 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8972 | ioSV_base_AI_11 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8973 | ioSV_base_AI_12 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8974 | ioSV_exp1_AI_01 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8975 | ioSV_exp1_AI_02 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8976 | ioSV_exp1_AI_03 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8977 | ioSV_exp1_AI_04 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8978 | ioSV_exp2_AI_01 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8979 | ioSV_exp2_AI_02 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8980 | ioSV_exp2_AI_03 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8981 | ioSV_exp2_AI_04 | See ioSV_base_AI_01 | -1 | — | — | — | — | RW | — |
| 8982 | ioSV_free1 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8983 | ioSV_free2 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8984 | ioSV_free3 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8985 | ioSV_free4 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8986 | ioSV_free5 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8987 | ioSV_free6 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8988 | ioSV_free7 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8989 | ioSV_free8 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 8990 | ioSV_base_DI_01 | -1 = -1=Not Used; 0 = 0=Supply Fan Th.Prot.; 1 = 1=Return Fan Th.Prot.; 2 = 2=On Off; 3 = 3=Fire Alarm; 4 = 4=Mode; 5 = 5=Door; 6 = 6=Antifreeze Alarm; 7 = 7=Airflow Alarm Supply; 8 = 8=Airflow Alarm Return; 9 = 9=Humidifier Alarm; 10 = 10=Pre Heater A | -1 | — | — | — | — | RW | — |
| 8991 | ioSV_base_DI_02 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8992 | ioSV_base_DI_03 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8993 | ioSV_base_DI_04 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8994 | ioSV_base_DI_05 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8995 | ioSV_base_DI_06 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8996 | ioSV_base_DI_07 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8997 | ioSV_base_DI_08 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8998 | ioSV_base_DI_09 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 8999 | ioSV_base_DI_10 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9000 | ioSV_base_DI_11 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9001 | ioSV_base_DI_12 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9002 | ioSV_exp1_DI_01 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9003 | ioSV_exp1_DI_02 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9004 | ioSV_exp1_DI_03 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9005 | ioSV_exp1_DI_04 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9006 | ioSV_exp2_DI_01 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9007 | ioSV_exp2_DI_02 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9008 | ioSV_exp2_DI_03 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9009 | ioSV_exp2_DI_04 | See ioSV_base_DI_01 | -1 | — | — | — | — | RW | — |
| 9010 | ioSV_free9 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9011 | ioSV_free10 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9012 | ioSV_free11 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9013 | ioSV_free12 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9014 | ioSV_free13 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9015 | ioSV_free14 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9016 | ioSV_free15 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9017 | ioSV_free16 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9018 | ioSV_base_DO_01 | -1 = -1=Not Used; 0 = 0=Supply Fan; 1 = 1=Return Fan; 2 = 2=On Off; 3 = 3=Alarm; 4 = 4=Mode; 5 = 5=Ext. Dampers; 6 = 6=Bypass Damper; 7 = 7=Supply Damper; 8 = 8=Return Damper; 9 = 9=Pump Preheat; 10 = 10=Pump Postheat; 11 = 11=Cool / Cool-Heat Pump; 12 = 12=Cool / Cool-Heat Step 1; 13 = 13=Cool / Cool-Heat Step 2; 14 = 14=Cool / Cool-Heat Step 3; 15 = 15=Cool / Cool-Heat Step 4; 16 = 16=Heat Pump; 17 = 17=Heater Step 1; 18 = 18=Heater Step 2; 19 = 19=Heater Step 3; 20 = 20=Pre Heater Step 1; | -1 | — | — | — | — | RW | Temporary: Logic Allocation of the physical output |
| 9018 | ioSV_base_DO_01 | 21 = 21=Pre Heater Step 2; 22 = 22=Pre Heater Step 3; 23 = 23=Post Heater Step 1; 24 = 24=Post Heater Step 2; 25 = 25=Post Heater Step 3; 26 = 26=Humidifier; 27 = 27=Recovery; 28 = 28=Supply Fan 2; 29 = 29=Return Fan 2; 30 = 30=Supply Damper 2; 31 = 31=Return Damper 2 | -1 | — | — | — | — | RW | Temporary: Logic Allocation of the physical output |
| 9019 | ioSV_base_DO_02 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | Save command required to be effective |
| 9020 | ioSV_base_DO_03 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9021 | ioSV_base_DO_04 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9022 | ioSV_base_DO_05 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9023 | ioSV_base_DO_06 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9024 | ioSV_base_DO_07 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9025 | ioSV_base_DO_08 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9026 | ioSV_base_DO_09 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9027 | ioSV_base_DO_10 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9028 | ioSV_base_DO_11 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9029 | ioSV_base_DO_12 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9031 | ioSV_exp1_DO_02 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9030 | ioSV_exp1_DO_01 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9032 | ioSV_exp1_DO_03 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9033 | ioSV_exp1_DO_04 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9034 | ioSV_exp2_DO_01 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9035 | ioSV_exp2_DO_02 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9036 | ioSV_exp2_DO_03 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9037 | ioSV_exp2_DO_04 | See ioSV_base_DO_01 | -1 | — | — | — | — | RW | — |
| 9039 | ioSV_free18 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9038 | ioSV_free17 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9040 | ioSV_free19 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9041 | ioSV_free20 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9042 | ioSV_free21 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9043 | ioSV_free22 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9044 | ioSV_free23 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9045 | ioSV_free24 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9046 | ioSV_base_AO_01 | -1 = -1=Not Used; 0 = 0=Supply Fan; 1 = 1=Return Fan; 2 = 2=Ext. Dampers; 3 = 3=Byp. Damper; 4 = 4=Cool / Cool-Heat; 5 = 5=Heat; 6 = 6=Pre Heater; 7 = 7=Post Heater; 8 = 8=Recovery; 9 = 9=Humidifier | -1 | — | — | — | — | RW | — |
| 9047 | ioSV_base_AO_02 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9048 | ioSV_base_AO_03 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9049 | ioSV_base_AO_04 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9050 | ioSV_base_AO_05 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9051 | ioSV_base_AO_06 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9052 | ioSV_exp1_AO_01 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9053 | ioSV_exp1_AO_02 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9054 | ioSV_exp2_AO_01 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9055 | ioSV_exp2_AO_02 | See ioSV_base_AO_01 | -1 | — | — | — | — | RW | — |
| 9056 | ioSV_free25 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9057 | ioSV_free26 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9058 | ioSV_free27 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9059 | ioSV_free28 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9060 | ioSV_free29 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9061 | ioSV_free30 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9062 | ioSV_free31 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9063 | ioSV_free32 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9064 | ioSV_base_AI_0102 | 0 = 0=NTC(NK103); 2 = 2=NTC(103AT); 3 = 3=4...20mA; 4 = 4=0-10V; 5 = 5=Ratiometric; 6 = 6=PT1000; 9 = 9=PTC; 10 = 10=0-5V; 11 = 11=0...20mA | 2 | — | — | — | — | RW | Temporary: AI probe configuration |
| 9065 | ioSV_base_AI_0304 | See ioSV_base_AI_0102 | 2 | — | — | — | — | RW | Save command required to be effective |
| 9066 | ioSV_base_AI_0506 | See ioSV_base_AI_0102 | 2 | — | — | — | — | RW | — |
| 9067 | ioSV_base_AI_0708 | See ioSV_base_AI_0102 | 4 | — | — | — | — | RW | — |
| 9068 | ioSV_base_AI_0910 | See ioSV_base_AI_0102 | 2 | — | — | — | — | RW | — |
| 9069 | ioSV_base_AI_1112 | See ioSV_base_AI_0102 | 4 | — | — | — | — | RW | — |
| 9070 | ioSV_exp1_AI_0102 | See ioSV_base_AI_0102 | — | — | — | — | — | R | — |
| 9071 | ioSV_exp1_AI_0304 | See ioSV_base_AI_0102 | — | — | — | — | — | R | — |
| 9072 | ioSV_exp2_AI_0102 | See ioSV_base_AI_0102 | — | — | — | — | — | R | — |
| 9073 | ioSV_exp2_AI_0304 | See ioSV_base_AI_0102 | — | — | — | — | — | R | — |
| 9074 | ioSV_free33 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9075 | ioSV_free34 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9076 | ioSV_free35 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9077 | ioSV_free36 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9078 | ioSV_free37 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9079 | ioSV_free38 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9080 | ioSV_free39 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9081 | ioSV_free40 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9082 | ioSV_base_AI01_min | Signed 16-bit | 0 | — | — | digit | — | RW | Temporary: AI ranges |
| 9083 | ioSV_base_AI01_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | Save command required to be effective |
| 9084 | ioSV_base_AI02_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9085 | ioSV_base_AI02_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9086 | ioSV_base_AI03_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9087 | ioSV_base_AI03_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9088 | ioSV_base_AI04_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9089 | ioSV_base_AI04_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9090 | ioSV_base_AI05_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9091 | ioSV_base_AI05_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9092 | ioSV_base_AI06_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9093 | ioSV_base_AI06_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9094 | ioSV_base_AI07_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9095 | ioSV_base_AI07_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9096 | ioSV_base_AI08_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9097 | ioSV_base_AI08_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9098 | ioSV_base_AI09_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9099 | ioSV_base_AI09_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9100 | ioSV_base_AI10_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9101 | ioSV_base_AI10_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9102 | ioSV_base_AI11_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9103 | ioSV_base_AI11_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9104 | ioSV_base_AI12_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9105 | ioSV_base_AI12_max | Unsigned 16-bit | 1000 | — | — | digit | — | RW | — |
| 9106 | ioSV_exp1_AI01_min | Signed 16-bit | -500 | — | — | digit | — | RW | — |
| 9107 | ioSV_exp1_AI01_max | Signed 16-bit | 1100 | — | — | digit | — | RW | — |
| 9109 | ioSV_exp1_AI02_max | Signed 16-bit | 1100 | — | — | digit | — | RW | — |
| 9108 | ioSV_exp1_AI02_min | Signed 16-bit | -500 | — | — | digit | — | RW | — |
| 9110 | ioSV_exp1_AI03_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9111 | ioSV_exp1_AI03_max | Signed 16-bit | 1000 | — | — | digit | — | RW | — |
| 9112 | ioSV_exp1_AI04_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9113 | ioSV_exp1_AI04_max | Signed 16-bit | 1000 | — | — | digit | — | RW | — |
| 9114 | ioSV_exp2_AI01_min | Signed 16-bit | -500 | — | — | digit | — | RW | — |
| 9115 | ioSV_exp2_AI01_max | Signed 16-bit | 1100 | — | — | digit | — | RW | — |
| 9116 | ioSV_exp2_AI02_min | Signed 16-bit | -500 | — | — | digit | — | RW | — |
| 9117 | ioSV_exp2_AI02_max | Signed 16-bit | 1100 | — | — | digit | — | RW | — |
| 9118 | ioSV_exp2_AI03_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9119 | ioSV_exp2_AI03_max | Signed 16-bit | 1000 | — | — | digit | — | RW | — |
| 9120 | ioSV_exp2_AI04_min | Signed 16-bit | 0 | — | — | digit | — | RW | — |
| 9121 | ioSV_exp2_AI04_max | Signed 16-bit | 1000 | — | — | digit | — | RW | — |
| 9122 | ioSV_free41 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9123 | ioSV_free42 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9124 | ioSV_free43 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9125 | ioSV_free44 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9126 | ioSV_free45 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9127 | ioSV_free46 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9128 | ioSV_free47 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9129 | ioSV_free48 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9130 | ioSV_free49 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9131 | ioSV_free50 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9132 | ioSV_free51 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9133 | ioSV_free52 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9134 | ioSV_free53 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9135 | ioSV_free54 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9136 | ioSV_free55 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9137 | ioSV_free56 | Signed 16-bit | 0 | — | — | — | — | RW | — |
| 9138 | EnableTest Output | 0 = 0=Disabled; 1 = 1=On From HMI; 2 = 2=On From Device | 0 | — | — | — | — | RW | Enable test output |
| 9139 | aoTst_Visibility1 | Unsigned 16-bit | — | — | — | — | %04x | R | Test AO visibility bit - Word 1 |
| 9140 | aoTst_Visibility2 | Unsigned 16-bit | — | — | — | — | %04x | R | Test AO visibility bit - Word 2 |
| 9141 | aoTst_Visibility3 | Unsigned 16-bit | — | — | — | — | %04x | R | Test AO visibility bit - Word 3 |
| 9142 | aoTst_EnManual1 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test AO Force/ Auto bit - Word 1 |
| 9143 | aoTst_EnManual2 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test AO Force/ Auto bit - Word 2 |
| 9144 | aoTst_EnManual3 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test AO Force/ Auto bit - Word 3 |
| 9145 | aoTst_Logic Index_0 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Supply Fan |
| 9146 | aoTst_Logic Index_1 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Return Fan |
| 9147 | aoTst_Logic Index_2 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Ext. Dampers |
| 9148 | aoTst_Logic Index_3 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Bypass Damper |
| 9149 | aoTst_Logic Index_4 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Cool - C/H Valve |
| 9150 | aoTst_Logic Index_5 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Heat Valve |
| 9151 | aoTst_Logic Index_6 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Pre Heater |
| 9152 | aoTst_Logic Index_7 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Post Heater |
| 9153 | aoTst_Logic Index_8 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Rotary Wheel / Exchanger |
| 9154 | aoTst_Logic Index_9 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | Test AO - Humidifier |
| 9155 | aoTst_free1 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9156 | aoTst_free2 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9157 | aoTst_free3 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9158 | aoTst_free4 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9159 | aoTst_free5 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9160 | aoTst_free6 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9161 | aoTst_free7 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9162 | aoTst_free8 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9163 | aoTst_free9 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9164 | aoTst_free10 | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | RW | — |
| 9165 | doTst_Visibility1 | Unsigned 16-bit | — | — | — | — | %04x | R | Test DO visibility bit - Word 1 |
| 9166 | doTst_Visibility2 | Unsigned 16-bit | — | — | — | — | %04x | R | Test DO visibility bit - Word 2 |
| 9167 | doTst_Visibility3 | Unsigned 16-bit | — | — | — | — | %04x | R | Test DO visibility bit - Word 3 |
| 9168 | doTst_EnManual1 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test DO Force/ Auto bit - Word 1 |
| 9169 | doTst_EnManual2 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test DO Force/ Auto bit - Word 2 |
| 9170 | doTst_EnManual3 | Unsigned 16-bit | — | — | — | — | %04x | RW | Test DO Force/ Auto bit - Word 3 |
| 9171 | doTst_Logic Index_0 | Boolean | 0 | — | — | — | — | RW | Test DO - Supply Fan |
| 9172 | doTst_Logic Index_1 | Boolean | 0 | — | — | — | — | RW | Test DO - Return Fan |
| 9173 | doTst_Logic Index_2 | Boolean | 0 | — | — | — | — | RW | Test DO - On Off |
| 9174 | doTst_Logic Index_3 | Boolean | 0 | — | — | — | — | RW | Test DO - Alarm |
| 9175 | doTst_Logic Index_4 | Boolean | 0 | — | — | — | — | RW | Test DO - Mode |
| 9176 | doTst_Logic Index_5 | Boolean | 0 | — | — | — | — | RW | Test DO - Ext. Dampers |
| 9177 | doTst_Logic Index_6 | Boolean | 0 | — | — | — | — | RW | Test DO - Bypass Damper |
| 9178 | doTst_Logic Index_7 | Boolean | 0 | — | — | — | — | RW | Test DO - Supply Damper |
| 9179 | doTst_Logic Index_8 | Boolean | 0 | — | — | — | — | RW | Test DO - Return Damper |
| 9180 | doTst_Logic Index_9 | Boolean | 0 | — | — | — | — | RW | Test DO - Pump Preheat |
| 9181 | doTst_Logic Index_10 | Boolean | 0 | — | — | — | — | RW | Test DO - Pump Postheat |
| 9182 | doTst_Logic Index_11 | Boolean | 0 | — | — | — | — | RW | Test DO - Cool/ CH Pump |
| 9183 | doTst_Logic Index_12 | Boolean | 0 | — | — | — | — | RW | Test DO - Cool/ CH Step 1 |
| 9184 | doTst_Logic Index_13 | Boolean | 0 | — | — | — | — | RW | Test DO - Cool/ CH Step 2 |
| 9185 | doTst_Logic Index_14 | Boolean | 0 | — | — | — | — | RW | Test DO - Cool/ CH Step 3 |
| 9186 | doTst_Logic Index_15 | Boolean | 0 | — | — | — | — | RW | Test DO - Cool/ CH Step 4 |
| 9187 | doTst_Logic Index_16 | Boolean | 0 | — | — | — | — | RW | Test DO - Heat Pump |
| 9188 | doTst_Logic Index_17 | Boolean | 0 | — | — | — | — | RW | Test DO - Heater Step 1 |
| 9189 | doTst_Logic Index_18 | Boolean | 0 | — | — | — | — | RW | Test DO - Heater Step 2 |
| 9190 | doTst_Logic Index_19 | Boolean | 0 | — | — | — | — | RW | Test DO - Heater Step 3 |
| 9191 | doTst_Logic Index_20 | Boolean | 0 | — | — | — | — | RW | Test DO - Pre Heater Step 1 |
| 9192 | doTst_Logic Index_21 | Boolean | 0 | — | — | — | — | RW | Test DO - Pre Heater Step 2 |
| 9193 | doTst_Logic Index_22 | Boolean | 0 | — | — | — | — | RW | Test DO - Pre Heater Step 3 |
| 9194 | doTst_Logic Index_23 | Boolean | 0 | — | — | — | — | RW | Test DO - Post Heater Step 1 |
| 9195 | doTst_Logic Index_24 | Boolean | 0 | — | — | — | — | RW | Test DO - Post Heater Step 2 |
| 9196 | doTst_Logic Index_25 | Boolean | 0 | — | — | — | — | RW | Test DO - Post Heater Step 3 |
| 9197 | doTst_Logic Index_26 | Boolean | 0 | — | — | — | — | RW | Test DO - Humidifier |
| 9198 | doTst_Logic Index_27 | Boolean | 0 | — | — | — | — | RW | Test DO - Rotary Wheel / Exchanger |
| 9199 | doTst_Logic Index_28 | Boolean | 0 | — | — | — | — | RW | Test DO - Supply Fan 2 |
| 9200 | doTst_Logic Index_29 | Boolean | 0 | — | — | — | — | RW | Test DO - Return Fan 2 |
| 9201 | doTst_Logic Index_30 | Boolean | 0 | — | — | — | — | RW | Test DO - Supply Damper 2 |
| 9202 | doTst_Logic Index_31 | Boolean | 0 | — | — | — | — | RW | Test DO - Return Damper 2 |
| 9203 | doTst_free1 | Boolean | 0 | — | — | — | — | RW | — |
| 9204 | doTst_free2 | Boolean | 0 | — | — | — | — | RW | — |
| 9205 | doTst_free3 | Boolean | 0 | — | — | — | — | RW | — |
| 9206 | doTst_free4 | Boolean | 0 | — | — | — | — | RW | — |
| 9207 | doTst_free5 | Boolean | 0 | — | — | — | — | RW | — |
| 9208 | doTst_free6 | Boolean | 0 | — | — | — | — | RW | — |
| 9209 | doTst_free7 | Boolean | 0 | — | — | — | — | RW | — |
| 9210 | doTst_free8 | Boolean | 0 | — | — | — | — | RW | — |
| 9211 | doTst_free9 | Boolean | 0 | — | — | — | — | RW | — |
| 9212 | doTst_free10 | Boolean | 0 | — | — | — | — | RW | — |
| 9500... 9518 | Area riservata | — | — | — | — | — | — | — | — |
| 13000...13009 | Area riservata | — | — | — | — | — | — | — | — |
| 9700... 9719 | Area riservata | — | — | — | — | — | — | — | — |
| 10499 | SendModbusFanConfiguration | Boolean | 0 |  | — | — | — | RW | — |
| 10500 | Supply1_Ziehl_Basic_CMODE | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10501 | Supply1_Ziehl_Basic_D1 | Unsigned 16-bit | 0 | — | — | — | — | RW | — |
| 10502 | Supply1_Ziehl_Basic_PIN | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10503 | Supply1_Ziehl_Basic_ControlCmd | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10504 | Supply1_Ziehl_Basic_SpeedCmd | Unsigned 16-bit | — | — | — | 1/32767 | — | R | — |
| 10505 | Supply1_Ziehl_Basic_Status | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10506 | Supply1_Ziehl_Basic_ErrorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | Ziehl MB Input Register 13 = error status |
| 10507 | Supply1_Ziehl_Basic_ActualSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | — |
| 10508 | Supply1_Ziehl_Basic_Current | Unsigned 16-bit | — | — | — | A | XX.YY | R | — |
| 10509 | Supply1_Ziehl_Basic_Voltage | Unsigned 16-bit | — | — | — | V | — | R | — |
| 10510 | Supply1_Ziehl_Basic_PINread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10511 | Supply1_Ziehl_Basic_CMODEread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10512 | Supply1_Ziehl_Basic_D1 read | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10513 | Supply1_Ziehl_Basic_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10514 | Supply1_Ziehl_Basic_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10515 | Supply1_Ziehl_Basic_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10516 | Return1_Ziehl_Basic_CMODE | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10517 | Return1_Ziehl_Basic_D1 | Unsigned 16-bit | 0 | — | — | — | — | RW | — |
| 10518 | Return1_Ziehl_Basic_PIN | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10519 | Return1_Ziehl_Basic_ControlCmd | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10520 | Return1_Ziehl_Basic_SpeedCmd | Unsigned 16-bit | — | — | — | 1/32767 | — | R | — |
| 10521 | Return1_Ziehl_Basic_Status | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10522 | Return1_Ziehl_Basic_ErrorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | Ziehl MB Input Register 13 = error status |
| 10523 | Return1_Ziehl_Basic_ActualSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | — |
| 10524 | Return1_Ziehl_Basic_Current | Unsigned 16-bit | — | — | — | A | XX.YY | R | — |
| 10525 | Return1_Ziehl_Basic_Voltage | Unsigned 16-bit | — | — | — | V | — | R | — |
| 10526 | Return1_Ziehl_Basic_PINread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10527 | Return1_Ziehl_Basic_CMODEread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10528 | Return1_Ziehl_Basic_D1 read | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10529 | Return1_Ziehl_Basic_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10530 | Return1_Ziehl_Basic_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10531 | Return1_Ziehl_Basic_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10532 | Supply2_Ziehl_Basic_CMODE | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10533 | Supply2_Ziehl_Basic_D1 | Unsigned 16-bit | 0 | — | — | — | — | RW | — |
| 10534 | Supply2_Ziehl_Basic_PIN | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10535 | Supply2_Ziehl_Basic_ControlCmd | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10536 | Supply2_Ziehl_Basic_SpeedCmd | Unsigned 16-bit | — | — | — | 1/32767 | — | R | — |
| 10537 | Supply2_Ziehl_Basic_Status | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10538 | Supply2_Ziehl_Basic_ErrorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | Ziehl MB Input Register 13 = error status |
| 10539 | Supply2_Ziehl_Basic_ActualSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | — |
| 10540 | Supply2_Ziehl_Basic_Current | Unsigned 16-bit | — | — | — | A | XX.YY | R | — |
| 10541 | Supply2_Ziehl_Basic_Voltage | Unsigned 16-bit | — | — | — | V | — | R | — |
| 10542 | Supply2_Ziehl_Basic_PINread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10543 | Supply2_Ziehl_Basic_CMODEread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10544 | Supply2_Ziehl_Basic_D1 read | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10545 | Supply2_Ziehl_Basic_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10546 | Supply2_Ziehl_Basic_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10547 | Supply2_Ziehl_Basic_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10548 | Return2_Ziehl_Basic_CMODE | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10549 | Return2_Ziehl_Basic_D1 | Unsigned 16-bit | 0 | — | — | — | — | RW | — |
| 10550 | Return2_Ziehl_Basic_PIN | Unsigned 16-bit | — | — | — | — | — | RW | — |
| 10551 | Return2_Ziehl_Basic_ControlCmd | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10552 | Return2_Ziehl_Basic_SpeedCmd | Unsigned 16-bit | — | — | — | 1/32767 | — | R | — |
| 10553 | Return2_Ziehl_Basic_Status | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10554 | Return2_Ziehl_Basic_ErrorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | Ziehl MB Input Register 13 = error status |
| 10555 | Return2_Ziehl_Basic_ActualSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | — |
| 10556 | Return2_Ziehl_Basic_Current | Unsigned 16-bit | — | — | — | A | XX.YY | R | — |
| 10557 | Return2_Ziehl_Basic_Voltage | Unsigned 16-bit | — | — | — | V | — | R | — |
| 10558 | Return2_Ziehl_Basic_PINread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10559 | Return2_Ziehl_Basic_CMODEread | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10560 | Return2_Ziehl_Basic_D1 read | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10561 | Return2_Ziehl_Basic_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10562 | Return2_Ziehl_Basic_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10563 | Return2_Ziehl_Basic_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10600 | Supply1_EBM_SourceSetValue | Unsigned 16-bit | 1 | — | — | — | — | RW | D101+1 |
| 10601 | Supply1_EBM_Running Dir | Unsigned 16-bit | — | — | — | — | — | RW | D102+1 |
| 10602 | Supply1_EBM_StoreSet Value | Unsigned 16-bit | 0 | — | — | — | — | RW | D103+1 |
| 10603 | Supply1_EBM_ControlModeDay | Unsigned 16-bit | 2 | — | — | — | — | RW | D106+1 |
| 10604 | Supply1_EBM_ControlModeNight | Unsigned 16-bit | 2 | — | — | — | — | RW | D107+1 |
| 10605 | Supply1_EBM_MotorStopEnableDay | Unsigned 16-bit | 1 | — | — | — | — | RW | D112+1 |
| 10606 | Supply1_EBM_MotorStopEnableNight | Unsigned 16-bit | 1 | — | — | — | — | RW | D113+1 |
| 10607 | Supply1_EBM_SourceSetValueRead | Unsigned 16-bit | — | — | — | — | — | R | D101+1 |
| 10608 | Supply1_EBM_Running DirRead | Unsigned 16-bit | — | — | — | — | — | R | D102+1 |
| 10609 | Supply1_EBM_StoreSet ValueRead | Unsigned 16-bit | — | — | — | — | — | R | D103+1 |
| 10610 | Supply1_EBM_ControlModeDayRead | Unsigned 16-bit | — | — | — | — | — | R | D106+1 |
| 10611 | Supply1_EBM_ControlModeNightRead | Unsigned 16-bit | — | — | — | — | — | R | D107+1 |
| 10612 | Supply1_EBM_MotorStopEnableDay Read | Unsigned 16-bit | — | — | — | — | — | R | D112+1 |
| 10613 | Supply1_EBM_MotorStopEnableNightRead | Unsigned 16-bit | — | — | — | — | — | R | D113+1 |
| 10614 | Supply1_EBM_MaxSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | D119+1 |
| 10615 | Supply1_EBM_Reset | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10616 | Supply1_EBM_SpecifiedSet | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10617 | Supply1_EBM_ActualSpeed | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10618 | Supply1_EBM_MotorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | EBM D011+1 : Motor status |
| 10619 | Supply1_EBM_Warning | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10620 | Supply1_EBM_DCLinkVoltage | Unsigned 16-bit | — | — | — | 1/256 Uz | — | R | — |
| 10621 | Supply1_EBM_DCLinkCurrent | Unsigned 16-bit | — | — | — | 1/256 Iz | — | R | — |
| 10622 | Supply1_EBM_DCLinkVRef | Unsigned 16-bit | — | — | — | 20mV | — | R | — |
| 10623 | Supply1_EBM_DCLinkCRef | Unsigned 16-bit | — | — | — | 2mA | — | R | — |
| 10624 | Supply1_EBM_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10625 | Supply1_EBM_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10626 | Return1_EBM_SourceSetValue | Unsigned 16-bit | 1 | — | — | — | — | RW | D101+1 |
| 10627 | Return1_EBM_RunningDir | Unsigned 16-bit | — | — | — | — | — | RW | D102+1 |
| 10628 | Return1_EBM_StoreSet Value | Unsigned 16-bit | 0 | — | — | — | — | RW | D103+1 |
| 10629 | Return1_EBM_ControlModeDay | Unsigned 16-bit | 2 | — | — | — | — | RW | D106+1 |
| 10630 | Return1_EBM_ControlModeNight | Unsigned 16-bit | 2 | — | — | — | — | RW | D107+1 |
| 10631 | Return1_EBM_MotorStopEnableDay | Unsigned 16-bit | 1 | — | — | — | — | RW | D112+1 |
| 10632 | Return1_EBM_MotorStopEnableNight | Unsigned 16-bit | 1 | — | — | — | — | RW | D113+1 |
| 10633 | Return1_EBM_SourceSetValueRead | Unsigned 16-bit | — | — | — | — | — | R | D101+1 |
| 10634 | Return1_EBM_Running DirRead | Unsigned 16-bit | — | — | — | — | — | R | D102+1 |
| 10635 | Return1_EBM_StoreSet ValueRead | Unsigned 16-bit | — | — | — | — | — | R | D103+1 |
| 10636 | Return1_EBM_ControlModeDayRead | Unsigned 16-bit | — | — | — | — | — | R | D106+1 |
| 10637 | Return1_EBM_ControlModeNightRead | Unsigned 16-bit | — | — | — | — | — | R | D107+1 |
| 10638 | Return1_EBM_MotorStopEnableDay Read | Unsigned 16-bit | — | — | — | — | — | R | D112+1 |
| 10639 | Return1_EBM_MotorStopEnableNightRead | Unsigned 16-bit | — | — | — | — | — | R | D113+1 |
| 10640 | Return1_EBM_MaxSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | D119+1 |
| 10641 | Return1_EBM_Reset | Unsigned 16-bit | — | — | — |  | — | R | — |
| 10642 | Return1_EBM_SpecifiedSet | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10643 | Return1_EBM_ActualSpeed | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10644 | Return1_EBM_MotorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | EBM D011+1 : Motor status |
| 10645 | Return1_EBM_Warning | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10646 | Return1_EBM_DCLinkVoltage | Unsigned 16-bit | — | — | — | 1/256 Uz | — | R | — |
| 10647 | Return1_EBM_DCLinkCurrent | Unsigned 16-bit | — | — | — | 1/256 Iz | — | R | — |
| 10648 | Return1_EBM_DCLinkVRef | Unsigned 16-bit | — | — | — | 20mV | — | R | — |
| 10649 | Return1_EBM_DCLinkCRef | Unsigned 16-bit | — | — | — | 2mA | — | R | — |
| 10650 | Return1_EBM_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10651 | Return1_EBM_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10652 | Supply2_EBM_SourceSetValue | Unsigned 16-bit | 1 | — | — | — | — | RW | D101+1 |
| 10653 | Supply2_EBM_Running Dir | Unsigned 16-bit | — | — | — | — | — | RW | D102+1 |
| 10654 | Supply2_EBM_StoreSet Value | Unsigned 16-bit | 0 | — | — | — | — | RW | D103+1 |
| 10655 | Supply2_EBM_ControlModeDay | Unsigned 16-bit | 2 | — | — | — | — | RW | D106+1 |
| 10656 | Supply2_EBM_ControlModeNight | Unsigned 16-bit | 2 | — | — | — | — | RW | D107+1 |
| 10657 | Supply2_EBM_MotorStopEnableDay | Unsigned 16-bit | 1 | — | — | — | — | RW | D112+1 |
| 10658 | Supply2_EBM_MotorStopEnableNight | Unsigned 16-bit | 1 | — | — | — | — | RW | D113+1 |
| 10659 | Supply2_EBM_SourceSetValueRead | Unsigned 16-bit | — | — | — | — | — | R | D101+1 |
| 10660 | Supply2_EBM_Running DirRead | Unsigned 16-bit | — | — | — | — | — | R | D102+1 |
| 10661 | Supply2_EBM_StoreSet ValueRead | Unsigned 16-bit | — | — | — | — | — | R | D103+1 |
| 10662 | Supply2_EBM_ControlModeDayRead | Unsigned 16-bit | — | — | — | — | — | R | D106+1 |
| 10663 | Supply2_EBM_ControlModeNightRead | Unsigned 16-bit | — | — | — | — | — | R | D107+1 |
| 10664 | Supply2_EBM_MotorStopEnableDay Read | Unsigned 16-bit | — | — | — | — | — | R | D112+1 |
| 10665 | Supply2_EBM_MotorStopEnableNightRead | Unsigned 16-bit | — | — | — | — | — | R | D113+1 |
| 10666 | Supply2_EBM_MaxSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | D119+1 |
| 10667 | Supply2_EBM_Reset | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10668 | Supply2_EBM_SpecifiedSet | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10669 | Supply2_EBM_ActualSpeed | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10670 | Supply2_EBM_MotorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | EBM D011+1 : Motor status |
| 10671 | Supply2_EBM_Warning | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10672 | Supply2_EBM_DCLinkVoltage | Unsigned 16-bit | — | — | — | 1/256 Uz | — | R | — |
| 10673 | Supply2_EBM_DCLinkCurrent | Unsigned 16-bit | — | — | — | 1/256 Iz | — | R | — |
| 10674 | Supply2_EBM_DCLinkVRef | Unsigned 16-bit | — | — | — | 20mV | — | R | — |
| 10675 | Supply2_EBM_DCLinkCRef | Unsigned 16-bit | — | — | — | 2mA | — | R | — |
| 10676 | Supply2_EBM_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10677 | Supply2_EBM_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10678 | Return2_EBM_SourceSetValue | Unsigned 16-bit | 1 | — | — | — | — | RW | D101+1 |
| 10679 | Return2_EBM_Running Dir | Unsigned 16-bit | — | — | — | — | — | RW | D102+1 |
| 10680 | Return2_EBM_StoreSet Value | Unsigned 16-bit | 0 | — | — | — | — | RW | D103+1 |
| 10681 | Return2_EBM_ControlModeDay | Unsigned 16-bit | 2 | — | — | — | — | RW | D106+1 |
| 10682 | Return2_EBM_ControlModeNight | Unsigned 16-bit | 2 | — | — | — | — | RW | D107+1 |
| 10683 | Return2_EBM_MotorStopEnableDay | Unsigned 16-bit | 1 | — | — | — | — | RW | D112+1 |
| 10684 | Return2_EBM_MotorStopEnableNight | Unsigned 16-bit | 1 | — | — | — | — | RW | D113+1 |
| 10685 | Return2_EBM_SourceSetValueRead | Unsigned 16-bit | — | — | — | — | — | R | D101+1 |
| 10686 | Return2_EBM_Running DirRead | Unsigned 16-bit | — | — | — | — | — | R | D102+1 |
| 10687 | Return2_EBM_StoreSet ValueRead | Unsigned 16-bit | — | — | — | — | — | R | D103+1 |
| 10688 | Return2_EBM_ControlModeDayRead | Unsigned 16-bit | — | — | — | — | — | R | D106+1 |
| 10689 | Return2_EBM_ControlModeNightRead | Unsigned 16-bit | — | — | — | — | — | R | D107+1 |
| 10690 | Return2_EBM_MotorStopEnableDay Read | Unsigned 16-bit | — | — | — | — | — | R | D112+1 |
| 10691 | Return2_EBM_MotorStopEnableNightRead | Unsigned 16-bit | — | — | — | — | — | R | D113+1 |
| 10692 | Return2_EBM_MaxSpeed | Unsigned 16-bit | — | — | — | rpm | — | R | D119+1 |
| 10693 | Return2_EBM_Reset | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10694 | Return2_EBM_SpecifiedSet | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10695 | Return2_EBM_ActualSpeed | Unsigned 16-bit | — | — | — | 1/64000 | — | R | — |
| 10696 | Return2_EBM_MotorStatus | Unsigned 16-bit | — | — | — | hex | %04X | R | EBM D011+1 : Motor status |
| 10697 | Return2_EBM_Warning | Unsigned 16-bit | — | — | — | hex | %04X | R | — |
| 10698 | Return2_EBM_DCLinkVoltage | Unsigned 16-bit | — | — | — | 1/256 Uz | — | R | — |
| 10699 | Return2_EBM_DCLinkCurrent | Unsigned 16-bit | — | — | — | 1/256 Iz | — | R | — |
| 10700 | Return2_EBM_DCLinkVRef | Unsigned 16-bit | — | — | — | 20mV | — | R | — |
| 10701 | Return2_EBM_DCLinkCRef | Unsigned 16-bit | — | — | — | 2mA | — | R | — |
| 10702 | Return2_EBM_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10703 | Return2_EBM_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10800 | Supply1_ATV212_CMOD | Unsigned 16-bit | 2 | — | — | — | — | RW | ATV212: 3+1 |
| 10801 | Supply1_ATV212_FMOD | Unsigned 16-bit | 4 | — | — | — | — | RW | ATV212: 4+1 |
| 10802 | Supply1_ATV212_Timeout | Unsigned 16-bit | 10 | — | — | sec | — | RW | ATV212: 2051+1 |
| 10803 | Supply1_ATV212_F732 | Unsigned 16-bit | 1 | — | — | — | — | RW | ATV212: 1842+1 |
| 10804 | Supply1_ATV212_CMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 3+1 |
| 10805 | Supply1_ATV212_FMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 4+1 |
| 10806 | Supply1_ATV212_Timeout read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 2051+1 |
| 10807 | Supply1_ATV212_F732 read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 1842+1 |
| 10808 | Supply1_ATV212_FreqMin | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 19+1 |
| 10809 | Supply1_ATV212_FreqMax | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 20+1 |
| 10810 | Supply1_ATV212_Command | Unsigned 16-bit | — | — | — | — | %04x | R | ATV212: 64000+1 FA00 |
| 10811 | Supply1_ATV212_Cmd Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64001+1 FA01 |
| 10812 | Supply1_ATV212_Current Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64768+1 Fd00 |
| 10813 | Supply1_ATV212_Status | Unsigned 16-bit | — | — | — | hex | %04x | R | ATV212: 64769+1 Fd01 |
| 10814 | Supply1_ATV212_Trip | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64656+1 FC90 |
| 10815 | Supply1_ATV212_Alarm | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64657+1 FC91 |
| 10816 | Supply1_ATV212_DCVoltage | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65028+1 FE04 |
| 10817 | Supply1_ATV212_Current | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65027+1 FE03 |
| 10818 | Supply1_ATV212_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10819 | Supply1_ATV212_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10820 | Supply1_ATV212_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10821 | Supply1_ATV212_Dummy4 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10822 | Return1_ATV212_CMOD | Unsigned 16-bit | 2 | — | — | — | — | RW | ATV212: 3+1 |
| 10823 | Return1_ATV212_FMOD | Unsigned 16-bit | 4 | — | — | — | — | RW | ATV212: 4+1 |
| 10824 | Return1_ATV212_Timeout | Unsigned 16-bit | 10 | — | — | sec | — | RW | ATV212: 2051+1 |
| 10825 | Return1_ATV212_F732 | Unsigned 16-bit | 1 | — | — | — | — | RW | ATV212: 1842+1 |
| 10826 | Return1_ATV212_CMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 3+1 |
| 10827 | Return1_ATV212_FMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 4+1 |
| 10828 | Return1_ATV212_Timeout read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 2051+1 |
| 10829 | Return1_ATV212_F732 read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 1842+1 |
| 10830 | Return1_ATV212_FreqMin | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 19+1 |
| 10831 | Return1_ATV212_FreqMax | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 20+1 |
| 10832 | Return1_ATV212_Command | Unsigned 16-bit | — | — | — |  | %04x | R | ATV212: 64000+1 FA00 |
| 10833 | Return1_ATV212_Cmd Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64001+1 FA01 |
| 10834 | Return1_ATV212_Current Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64768+1 Fd00 |
| 10835 | Return1_ATV212_Status | Unsigned 16-bit | — | — | — | hex | %04x | R | ATV212: 64769+1 Fd01 |
| 10836 | Return1_ATV212_Trip | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64656+1 FC90 |
| 10837 | Return1_ATV212_Alarm | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64657+1 FC91 |
| 10838 | Return1_ATV212_DCVoltage | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65028+1 FE04 |
| 10839 | Return1_ATV212_Current | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65027+1 FE03 |
| 10840 | Return1_ATV212_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10841 | Return1_ATV212_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10842 | Return1_ATV212_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10843 | Return1_ATV212_Dummy4 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10844 | Supply2_ATV212_CMOD | Unsigned 16-bit | 2 | — | — | — | — | RW | ATV212: 3+1 |
| 10845 | Supply2_ATV212_FMOD | Unsigned 16-bit | 4 | — | — | — | — | RW | ATV212: 4+1 |
| 10846 | Supply2_ATV212_Timeout | Unsigned 16-bit | 10 | — | — | sec | — | RW | ATV212: 2051+1 |
| 10847 | Supply2_ATV212_F732 | Unsigned 16-bit | 1 | — | — | — | — | RW | ATV212: 1842+1 |
| 10848 | Supply2_ATV212_CMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 3+1 |
| 10849 | Supply2_ATV212_FMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 4+1 |
| 10850 | Supply2_ATV212_Timeout read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 2051+1 |
| 10851 | Supply2_ATV212_F732 read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 1842+1 |
| 10852 | Supply2_ATV212_FreqMin | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 19+1 |
| 10853 | Supply2_ATV212_FreqMax | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 20+1 |
| 10854 | Supply2_ATV212_Command | Unsigned 16-bit | — | — | — | — | %04x | R | ATV212: 64000+1 FA00 |
| 10855 | Supply2_ATV212_Cmd Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64001+1 FA01 |
| 10856 | Supply2_ATV212_Current Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64768+1 Fd00 |
| 10857 | Supply2_ATV212_Status | Unsigned 16-bit | — | — | — | hex | %04x | R | ATV212: 64769+1 Fd01 |
| 10858 | Supply2_ATV212_Trip | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64656+1 FC90 |
| 10859 | Supply2_ATV212_Alarm | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64657+1 FC91 |
| 10860 | Supply2_ATV212_DCVoltage | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65028+1 FE04 |
| 10861 | Supply2_ATV212_Current | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65027+1 FE03 |
| 10862 | Supply2_ATV212_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10863 | Supply2_ATV212_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10864 | Supply2_ATV212_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10865 | Supply2_ATV212_Dummy4 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10866 | Return2_ATV212_CMOD | Unsigned 16-bit | 2 | — | — | — | — | RW | ATV212: 3+1 |
| 10867 | Return2_ATV212_FMOD | Unsigned 16-bit | 4 | — | — | — | — | RW | ATV212: 4+1 |
| 10868 | Return2_ATV212_Timeout | Unsigned 16-bit | 10 | — | — | sec | — | RW | ATV212: 2051+1 |
| 10869 | Return2_ATV212_F732 | Unsigned 16-bit | 1 | — | — | — | — | RW | ATV212: 1842+1 |
| 10870 | Return2_ATV212_CMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 3+1 |
| 10871 | Return2_ATV212_FMODread | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 4+1 |
| 10872 | Return2_ATV212_Timeout read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 2051+1 |
| 10873 | Return2_ATV212_F732 read | Unsigned 16-bit | — | — | — | — | — | R | ATV212: 1842+1 |
| 10874 | Return2_ATV212_FreqMin | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 19+1 |
| 10875 | Return2_ATV212_FreqMax | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 20+1 |
| 10876 | Return2_ATV212_Command | Unsigned 16-bit | — | — | — | — | %04x | R | ATV212: 64000+1 FA00 |
| 10877 | Return2_ATV212_Cmd Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64001+1 FA01 |
| 10878 | Return2_ATV212_Current Freq | Unsigned 16-bit | — | — | — | Hz | XX.YY | R | ATV212: 64768+1 Fd00 |
| 10879 | Return2_ATV212_Status | Unsigned 16-bit | — | — | — | hex | %04x | R | ATV212: 64769+1 Fd01 |
| 10880 | Return2_ATV212_Trip | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64656+1 FC90 |
| 10881 | Return2_ATV212_Alarm | Unsigned 16-bit | — | — | — | hex | %04X | R | ATV212: 64657+1 FC91 |
| 10882 | Return2_ATV212_DCVoltage | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65028+1 FE04 |
| 10883 | Return2_ATV212_Current | Unsigned 16-bit | — | — | — | % | XX.YY | R | ATV212: 65027+1 FE03 |
| 10884 | Return2_ATV212_Dummy1 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10885 | Return2_ATV212_Dummy2 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10886 | Return2_ATV212_Dummy3 | Unsigned 16-bit | — | — | — | — | — | R | — |
| 10887 | Return2_ATV212_Dummy4 | Unsigned 16-bit | — | — | — | — | — | R | — |

Table 15 - Modbus Status Table