Unità Trattamento Aria

FREE Advance

1.	Introduzione	5

1.1.	Dati identificativi del Fabbricante	5

1.2.	Documentazione allegata	5

1.3.	Scopo e utilizzo del manuale	5

1.4.	Aggiornamento del manuale	5

1.5.	Consultazione del manuale	5

1.6.	Glossario	6

1.7.	Formulazione dei diritti di proprietà intellettuale	6

2.	Descrizione del prodotto	7

2.1.	Controllore	8

2.2.	Funzionalità principali del Menu Display	10

2.2.1.	Blocco tastiera	14

2.3.	Uso previsto	15

2.3.1.	Componenti principali dell'UTA	15

2.4.	Uso scorretto ragionevolmente prevedibile	18

2.5.	Mappa I/O e componenti	19

3.	Funzioni	24

3.1.	ON/OFF	26

3.1.1.	Accensione	26

3.1.2.	Spegnimento	27

3.2.	Setpoint	28

3.3.	Modi di funzionamento	29

3.3.1.	Configurazione hardware dell’UTA per realizzare il cambio modo	29

3.3.2.	Modalità per eseguire il cambio modo	29

3.3.3.	Funzionamento del modo auto	30

3.4.	Fasce orarie ed eventi	31

3.4.1.	Fasce orarie	31

3.4.2.	Eventi	31

3.5.	Regolazione di temperatura	32

3.5.1.	Boost	33

3.5.2.	Regolatore di preriscaldo	33

3.5.3.	Limiti in mandata della temperatura	33

3.6.	Regolazione di umidità	34

3.6.1.	Regolazione umidificazione	34

3.6.2.	Regolazione deumidificazione	34

3.7.	Free-cooling e free-heating	36

3.8.	Recupero di calore	37

3.8.1.	Recupero di calore con regolazione in ripresa	38

3.8.2.	Recupero di calore con regolazione in mandata o in cascata	40

3.9.	Serrande esterne e serrande di ricircolo	41

3.10.	Attuatori per raffrescamento	42

3.11.	Attuatori per riscaldamento	44

3.11.1.	Relè attivati e numero di step	46

3.12.	Pompe	48

3.13.	Ventilatori	49

3.13.1.	Ventilatori ON/OFF	50

3.13.2.	Ventilatori modulanti (con inverter)	50

3.13.3.	Ventilatori di backup	51

3.13.4.	Ventilatori Modbus	51

3.14.	Qualità aria: sonda CO2 e sonda VOC	53

3.15.	Regolazione a portata costante	54

3.16.	Regolazione a pressione costante	54

3.17.	Test output	54

4.	Menu Impostazioni Utente	55

4.1.	A-Unit	56

4.2.	B-Clock & Events	58

4.3.	C-Languages	66

4.4.	D-Alarms	66

4.5.	E-User Settings	71

4.5.1.	E1-Setpoints	71

4.5.2.	E2-Work Hours	72

4.5.3.	E3-Data Logger	73

4.5.4.	E4-Web Server	74

4.5.5.	E5-Regulator	75

4.6.	F-I/O	76

4.7.	G-Password	79

4.8.	H-System	79

4.8.1.	S-Service	79

4.8.2.	O-I/O	97

4.8.3.	P-Serial ports	110

4.8.4.	Q-USB	111

4.8.5.	U-Unit Configuration	112

4.8.6.	W-Password	114

5.	Datalogger	115

6.	Protocolli BMS	117

6.1.	Modbus RTU	117

6.2.	Modbus TCP	117

6.3.	Bacnet	117

7.	Web Server	119

8.	Allarmi	125

8.1.	Allarme incendio	127

8.2.	Allarme sonda qualità aria	127

8.3.	Allarme sonda pressione	127

8.4.	Allarme flusso aria	128

8.5.	Allarme protezione ventilatori	128

8.6.	Allarme manutenzione ventilatori	128

8.7.	Allarme antigelo	129

9.	Smaltimento	130

10.	Informazioni di sicurezza	131

11.	Schema elettrico	133

12.	Tabelle Modbus	134

12.1.	Tabella Modbus EEProm	134

12.2.	Tabella Modbus Stati	165

Introduzione

Dati identificativi del Fabbricante

Eliwell Controls s.r.l.

Via dell’Industria, 15 • Z.I. Paludi

32010 Pieve d’Alpago (BL) ITALY

Telefono: +39 0437 986 111

Fax: +39 0437 989 066

www.eliwell.it

Documentazione allegata

A corredo del presente Manuale vengono forniti i seguenti documenti.

| Nome documento | Codice documento |
| --- | --- |
| User Guide FREE Advance | 9MA10265 (ENG) 9MA00265 (ITA) |

Tabella 1 - Documentazione allegata

Scopo e utilizzo del manuale

Il presente Manuale è parte integrante del prodotto ed è destinato a tutte le persone che operano sul prodotto o che interagiscono con gli utilizzatori del prodotto stesso. Ha lo scopo di fornire tutte le informazioni necessarie per:

identificare rapidamente tutte le parti di cui è costituito il prodotto;

eseguire in modo corretto tutte le operazioni previste durante le fasi di utilizzo e gestione del prodotto;

garantire la sicurezza e la tutela della salute del personale che a diverso titolo opera sul prodotto;

assicurare il funzionamento efficiente del prodotto.

Il presente Manuale deve essere letto attentamente in ogni sua parte prima di eseguire qualsiasi operazione sul prodotto. Nel caso di dubbi sulla corretta interpretazione delle istruzioni contenute in esso contenute, contattare il Fabbricante per ottenere i necessari chiarimenti.

Il presente Manuale deve essere conservato con cura per tutta la vita del prodotto e deve accompagnare il prodotto stesso in tutti i suoi trasferimenti, a qualsiasi titolo, ad altri utenti. Deve essere posto nelle vicinanze del prodotto, in un luogo luogo protetto da agenti atmosferici, calore, umidità, agenti corrosivi e facilmente accessibile e noto a tutti gli utilizzatori; deve essere consultato facendo attenzione a non danneggiarlo, a non asportare pagine, a non modificare il suo contenuto in nessun modo.

Aggiornamento del manuale

Se in seguito a modifiche costruttive che comportano un cambiamento del funzionamento del prodotto si rendesse necessario un aggiornamento del presente Manuale, il Fabbricante provvederà a fornire al Cliente una revisione del Manuale stesso che sostituirà a tutti gli effetti la precedente.

Consultazione del manuale

All’interno del Manuale le informazioni sono organizzate in:

capitoli,

sottocapitoli,

paragrafi,

sottoparagrafi

e sono facilmente rintracciabili consultando il Sommario posto all’inizio del Manuale stesso.

Per richiamare l’attenzione degli utilizzatori ai fini di un uso corretto e in sicurezza del prodotto, si adotta nel presente Manuale la seguente convenzione:

NOTA: Il simbolo è utilizzato per fornire prescrizioni o approfondimenti utili per l'utilizzatore.

Glossario

| AI (Analogue Input) | Acronimo di ingresso analogico. |
| --- | --- |
| AO (Analogue Output) | Acronimo di uscita analogica. |
| ATTUATORE CALDO | Componente che riscalda l'aria. |
| ATTUATORE FREDDO | Componente che raffredda l'aria. |
| BACNET (Building Automation and Control NETwork) | Protocollo di comunicazione basato su standard ASHRAE, ANSI e ISO 16484-5 per le reti di building automation. |
| BMS (Building Management System) | Sistema di controllo/monitoraggio di apparati meccanici ed elettrici installati in un ambiente. |
| CO2 | Diossido di carbonio (anidride carbonica). |
| DATALOGGER | Registratore di dati. |
| DI (Digital Input) | Acronimo di ingresso digitale. |
| DO (Digital Output) | Acronimo di uscita digitale. |
| FILESYSTEM | Insieme dei tipi di dati astratti necessari per la gestione dei dati. |
| REGOLATORE P | Regolatore ad azione Proporzionale. |
| REGOLATORE PI | Regolatore ad azione Proporzionale-Integrale. |
| REGOLATORE PID | Regolatore ad azione Proporzionale-Integrale-Derivativa. |
| SCADA (Supervisory Control And Data Acquisition) | Acronimo di controllo di supervisione e acquisizione dati. |
| SUPERVISORE | Sistema di controllo/monitoraggio di apparati meccanici ed elettrici. |
| VOC (Volatile Organic Compound) | Composto organico volatile. |

Tabella 2 - Glossario

Formulazione dei diritti di proprietà intellettuale

La presente pubblicazione è di esclusiva proprietà del Fabbricante, il quale pone il divieto assoluto di riproduzione e divulgazione se non espressamente autorizzata dal Fabbricante stesso.

Ogni cura è stata posta nella realizzazione del presente Manuale; tuttavia il Fabbricante e ogni persona o società coinvolta nella sua creazione e stesura non possono assumersi alcuna responsabilità derivante dall’utilizzo dello stesso. Il Fabbricante si riserva il diritto di apportare qualsiasi modifica, estetica o funzionale, senza preavviso alcuno ed in qualsiasi momento.

Descrizione del prodotto

Il prodotto è un controllore AVD programmato per applicazione su Unità di Trattamento Aria (UTA).

Il controllore AVD programmato può essere uno tra i due descritti nella seguente tabella.

| AVD8400 | FREE Advance con display, 28 I/Os |
| --- | --- |
| AVD12600 | FREE Advance con display, 42 I/Os |

Tabella 3 – Controllore AVD programmato

Al controllore AVD programmato possono essere applicati:

fino a due espansioni EVE4200;

terminale grafico remoto EVK1000.

NOTA: Per ulteriori informazioni fare riferimento a 1.2 Documentazione allegata a pag. 5.

NOTA: Nel prosieguo del presente Manuale:

il controllore AVD programmato sarà indicato con il termine "controllore";

l'Unità di Trattamento Aria sarà indicata con il termine "UTA".

Controllore

Il controllore (Fig 1 - a pag. 8) è dotato dei seguenti componenti:

tastiera (T);

display (D);

LED di segnalazione (L);

connettori (S).

Fig 1 - Componenti del controllore

La tastiera (T) è composta dai seguenti tasti:

| Tasto | Simbolo | Nome | Descrizione |
| --- | --- | --- | --- |
| 1 |  | UP | - Incrementa/modifica un valore - Seleziona etichetta successiva |
| 2 |  | DOWN | - Decrementa/modifica un valore - Seleziona etichetta precedente |
| 3 |  | RIGHT | - Sposta il cursore verso destra (in modalità edit) - Seleziona oggetto successivo - Visualizza pagina successiva (nelle liste parametri) |
| 4 |  | LEFT | - Sposta il cursore verso sinistra (in modalità edit) - Seleziona oggetto precedente - Visualizza pagina precedente (nelle liste parametri) - (mantenuto premuto) esce dalla modalità edit senza salvare - (mantenuto premuto) esce dalla pagina/torna alla pagina precedente |
| 5 |  | OK | - Esegue operazione associata a un tasto grafico - Conferma (in modalità edit) - Ingresso modalità edit |

Tabella 4 - Tastiera

Il display (D) consente di visualizzare e gestire i menu per l'utilizzo dell'UTA. Per la descrizione dei diversi menu fare riferimento a 2.2 Menu Display a pag. 10. Per ulteriori informazioni fare riferimento a 1.2 Documentazione allegata a pag. 5.

I LED di segnalazione (L) sono quattro, ciascuno dei quali può assumere uno o più stati per segnalare un'informazione.

| LED | Colore | Stato | Significato |
| --- | --- | --- | --- |
| P | Verde | Acceso | Controllore alimentato |
|  |  | Spento | Controllore non alimentato |
| A | Rosso | Spento | Nessun allarme |
|  |  | Acceso | Presente almeno un allarme attivo; fare riferimento a 8 Allarmi a pag. 125. |
|  |  | Lampeggiante | Presenti almeno un allarme resettabile e nessun allarme attivo (o a riarmo manuale); fare riferimento a 8 Allarmi a pag. 125. |
| B | Giallo | Acceso | Scrittura su filesystem da datalogger o acquisizione dati da porta USB |
| C | Verde | Spento | UTA in stato OFF |
|  |  | Acceso | UTA in stato ON |
|  |  | Lampeggiante | UTA in stato stand-by |

Tabella 5 - LED di segnalazione

NOTA: L'UTA è in stato stand-by se l'UTA è accesa e non è attivata alcuna regolazione.

I connettori (S) consentono la connessione di:

alimentazione;

ingressi/uscite;

porte di comunicazione;

MicroSD.

Per ulteriori informazioni sui connettori fare riferimento a 1.2 Documentazione allegata a pag. 5.

Funzionalità principali del Menu Display

Per selezionare una delle icone presenti nel display premere i tasti UP, DOWN, RIGHT, LEFT su tastiera.

L'icona selezionata inverte la propria colorazione passando da nera su sfondo bianco a bianca su sfondo nero.

Alla pressione del tasto OK si accede alla funzionalità relativa all'icona selezionata.

All'accensione il controllore visualizza a display il menu "Start splash".

Dal menu "Start splash", alla pressione di un tasto qualsiasi si accede al menu "Main":

il menu "Main" sotto riportata si riferisce al caso di UTA in stato ON;

il menu "Main" sotto riportata si riferisce al caso di UTA in stato OFF.

NOTA: Le icone visualizzate nel menu "Main" dipendono dalla configurazione hardware dell'UTA (fare riferimento a 2.2.1.2 Configurazione hardware dell'UTA a pag. 17).

I parametri del menu "Main" sono riportati nella seguente tabella.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | Unit_KbdOnOff | Boolean | 0 | — | — | — | On/Off status from keyboard |
| - - - | Unit_ForceOffAfterReboot | Boolean | 0 | — | — | — | Force Off keyboard after reboot |
| - - - | Unit_KbdMode_E2 | 0=Cool; 1=Heat; 2=Auto | 0 | 0 | 2 | — | Mode status from keyboard |
| - - - | Unit_KbdEco_E2 | 1=Economy; 2=Comfort; 3=Night | 2 | 1 | 3 | — | Comfort/Economy/Night status from keyboard |
| - - - | Unit_RegTempType | 0=Supply; 1=Return Direct; 2=Return Cascade | 1 | 0 | 2 | — | Temperature Regulation Probe |
| - - - | Unit_BMS_OnOff | Boolean | 1 | — | — | — | Unit On/Off via Modbus |
| - - - | Unit_Status | 0=OFF; 1=STANDBY; 2=RUN | — | 0 | 2 | — | Unit Status |
| - - - | T_RegulationProbe | Signed 16-bit | — | — | — | °C | Temperature Regulation Probe |
| - - - | T_CurrentSetpointByPar | Signed 16-bit | — | — | — | °C | Current Setpoint by parameter based on selected mode |
| - - - | RH_RegulationProbe | Signed 16-bit | — | — | — | %R.H. | Humdity Regulation Probe |
| - - - | AirQ_RegulationProbe | Signed 16-bit | — | — | — | %/ppm | Air Quality Regulation Probe |

Tabella 6 - Main

Le icone previste per il menu "Main" sono descritte nella seguente tabella.

| Icona | Descrizione |
| --- | --- |
|  | Tasto di accesso al menu "Action:" per modificare lo stato dell'UTA. |
|  | Tasto di impostazione modo di funzionamento (se abilitato). |
|  | Tasto di visualizzazione presenza allarme. Se abilitato, tasto di accesso al menu "D1-Alarms". |
|  | Tasto di impostazione cambio profilo: economy, night, comfort. |
|  | Campo di visualizzazione della temperatura di regolazione: temperatura acquisita da sonda mandata o sonda ripresa, a seconda del tipo di regolazione. |
|  | Campo di visualizzazione eventi settimanali e/o annuali abilitati. |
|  | Campo di visualizzazione messa a regime o boost attivati. |
|  | Campo di visualizzazione attivazione (da sinistra a destra) di: recuperatore, attuatori freddo, attuatori caldo, ventilatori, deumidificazione. |
|  | Campo di visualizzazione controllo SCADA di almeno un parametro. |
|  | Campo di visualizzazione di datalogger attivato. |
|  | Tasto di accesso al menu "Setpoint" per impostare il setpoint temperatura. Sul tasto viene visualizzato il setpoint di temperatura impostato. |
|  | Tasto di accesso al menu "Setpoint" per impostare il setpoint umidità. Sul tasto viene visualizzato il setpoint di umidità impostato. |
|  | Tasto di accesso al menu "Setpoint" per impostare il setpoint qualità aria. Sul tasto viene visualizzato il setpoint di qualità aria impostato. |

Tabella 7 - Icone del menu "Main"

Alla pressione del tasto  si accede alla pagina "Action:" come descritto a seguire.

NOTA: In caso di UTA in stato stand-by, il tasto consente di:

portare l'UTA in stato OFF mediante il tasto Off;

portare l'UTA in stato ON mediante il tasto Override.

Alla pressione del tasto  si accede al menu "Setpoint" riferito a setpoint di temperatura come descritto a seguire.

|  |  | Menu "Setpoint" |  |  |
| --- | --- | --- | --- | --- |

Alla pressione del tasto  si accede al menu "Setpoint" riferito a setpoint umidità come descritto a seguire.

|  |  | Menu "Setpoint" |  |  |
| --- | --- | --- | --- | --- |

Alla pressione del tasto  si accede al menu "Setpoint" riferito a setpoint qualità aria come descritto a seguire.

|  |  | Menu "Setpoint" |  |  |
| --- | --- | --- | --- | --- |

NOTA: Alcune pagine riportano in alto a destra il numero progressivo di pagina corrente rispetto al numero di pagine totali (esempio: 1/2). Per cambiare la pagina corrente visualizzata premere il tasto LEFT o il tasto RIGHT.

Mantenere premuto il tasto UP per almeno 2 secondi per accedere al menu "Events".

|  |  | Menu "Events" |  |  |
| --- | --- | --- | --- | --- |

Mantenere premuto il tasto RIGHT per almeno 2 secondi per accedere a "Menu Impostazioni Utente".

NOTA: Per ulteriori informazioni sul Menu Impostazioni Utente fare riferimento a 4 Menu Impostazioni Utente a pag. 55.

|  |  | "Menu Impostazioni Utente" |  |  |
| --- | --- | --- | --- | --- |

Mantenere premuto il tasto LEFT per almeno 2 secondi per accedere al menu "Start Splash".

|  |  | Menu "Start splash" |  |  |
| --- | --- | --- | --- | --- |

Blocco tastiera

In caso di mancata pressione di alcun tasto per un tempo superiore a un'ora, si attiva automaticamente il blocco tastiera.

Se presente il blocco tastiera, il display visualizza il messaggio .

Per rimuovere il blocco tastiera, mantenere premuto il tasto UP; in questo caso, il blocco tastiera si riattiva automaticamente dopo 5 minuti di inattività.

Per disabilitare il blocco tastiera, mantenere premuto il tasto LEFT; in questo caso, il blocco tastiera si riattiva automaticamente dopo 60 minuti di inattività.

Uso previsto

Il controllore è destinato al controllo di UTA per la regolazione delle condizioni ambientali.

Componenti principali dell'UTA

L'UTA (Fig 2 - a pag. 16) è costituita dai componenti riportati nella seguente tabella.

NOTA: Il numero, il tipo e la conformazione dei componenti illustrati in Fig 2 - a pag. 16 e riportati nella seguente tabella sono puramente indicativi.

| 1 | Serranda esterna di aspirazione |
| --- | --- |
| 2 | Serranda esterna di espulsione |
| 3 | Filtro ripresa |
| 4 | Filtro mandata |
| / | Serrande ventilatori |
| 5 | Serrande di ricircolo |
| 6 | Recuperatore di calore |
| 7 | Serranda recuperatore |
| 8 | Batteria di preriscaldo |
| 9 | Batteria caldo |
| 10 | Batteria freddo |
| 11 | Batteria di postriscaldo |
| 12 | Umidificatore |
| 13 | Ventilatori mandata, azionati dal motore mandata |
| 14 | Ventilatori ripresa, azionati dal motore ripresa |
| 15 | Sonda ripresa |
| 16 | Sonda mandata |
| 17 | Sonda esterna |
| 18 | Sonda espulsione |
| / | Sonda antigelo, relativa alla batteria caldo e alla batteria freddo |
| / | Sonda CO2 |
| / | Sonda VOC |
| / | Sonda preriscaldo |
| / | Sonda saturazione |
| / | Sonda di pressione 0-10 V |

Tabella 8 - Componenti principali dell'UTA

NOTA: In Fig 2 - a pag. 16 il recuperatore illustrato è a flussi incrociati con serranda di bypass.

NOTA: Le sonde di temperatura sono di tipo NTC.

Fig 2 - Componenti principali dell'UTA

Convenzioni UTA

Nel prosieguo del presente Manuale si adottano le convenzioni riportate nella seguente tabella.

| Batterie principali | - Batteria caldo - batteria freddo |
| --- | --- |
| Serrande esterne | - Serranda esterna di espulsione - serranda esterna di aspirazione |
| Sonde qualità aria | - Sonda CO2 - sonda VOC |
| Ventilatori di backup | - Ventilatore mandata di backup - ventilatore ripresa di backup |
| Ventilatori mandata | - Ventilatore mandata principale - ventilatore mandata di backup |
| Ventilatori principali | - Ventilatore mandata principale - ventilatore ripresa principale |
| Ventilatori ripresa | - Ventilatore ripresa principale - ventilatore ripresa di backup |
| Ventilatori Modbus | - Ventilatore EBM - Ventilatore ATV - ventilatore Ziehl |

Tabella 9 – Convenzioni

Configurazione hardware dell'UTA

Le configurazioni hardware dell'UTA sono descritte nella seguente tabella.

| Componente | Caratteristica | Configurazione hardware |
| --- | --- | --- |
| Ventilatori | Numero ventilatori | Ventilatore mandata; ventilatore mandata + ventilatore ripresa. |
|  | Tipologia ventilatori | ON/OFF; modulanti; ON/OFF con backup; modulanti con backup; ATV; ATV con backup; EBM; EBM con backup; Ziehl; Ziehl con backup. |
|  | Regolazione ventilatori | A velocità costante; qualità aria; a pressione costante; a portata costante. |
|  | Allarme ventilatori (non Modbus) | Termico; termico + flussostato ON/OFF. |
|  | Allarme ventilatori (Modbus) | Nessuno; flussostato ON/OFF. |
| Batterie | Tipologia batteria di preriscaldo (1) | Nessuna; valvola modulante; valvola modulante + pompa; resistenza elettrica ON/OFF a step; resistenza elettrica 0-10 V + step; resistenza elettrica PWM + step. |
|  | Tipologia batterie principali | Nessuna; batteria freddo; batteria caldo; batteria freddo + batteria caldo; batteria promiscua. |
|  | Tipologia batteria freddo (2) | Valvola modulante; valvola modulante + pompa; motocondensante fino a 4 step o 4 unità modulanti in parallelo. |
|  | Tipologia batteria caldo (2) | Valvola modulante; valvola modulante + pompa; motocondensante fino a 4 step o 4 unità modulanti in parallelo; resistenza elettrica ON/OFF a step; resistenza elettrica 0-10 V + step; resistenza elettrica PWM + step. |
|  | Tipologia batteria promiscua (3) | Modulante; modulante + pompa; motocondensante fino a 4 step o 4 unità modulanti in parallelo. |
|  | Tipologia batteria di postriscaldo (1) – (4) | Nessuna; valvola modulante; valvola modulante + pompa; resistenza elettrica ON/OFF a step; resistenza elettrica 0-10 V + step; resistenza elettrica PWM + step. |
|  | Tipologia sonda antigelo | Nessuna; ON/OFF; NTC. |
| Recuperatore | Tipologia recuperatore (5) | Nessuno; ON/OFF a flussi incrociati con serranda di bypass; ON/OFF rotativo; ON/OFF a batterie; proporzionale a flussi incrociati con serranda di bypass; proporzionale rotativo; proporzionale a batterie. |
|  | Tipologia sbrinamento recuperatore | Nessuno; ventilatore mandata; a resistenza. |
| Umidificatore | Attivazione umidificatore | Nessuno; ON/OFF; proporzionale. |
| Deumidificazione | Tipologia deumidificazione | Nessuno; standard; a punto di rugiada; standard + invernale; a punto di rugiada + invernale. |
| Serrande | Tipologia serrande esterne | Nessuna; ON/OFF; ON/OFF + miscela 0-10 V |
|  | Tipologia serrande ventilatori | Nessuna; ventilatore mandata; ventilatore ripresa; ventilatore mandata + ventilatore ripresa. |
| Sonde qualità aria | Tipologia sonda qualità aria | Nessuna; CO2; VOC; CO2 + VOC. |
| Camera di miscela tra serrande esterne e batteria di preriscaldo | Attivazione camera di miscela (6) | Nessuna; attiva. |

Tabella 10 - Configurazione hardware dell'UTA

NOTA (1): La batteria di preriscaldo e la batteria di postriscaldo in configurazione valvola modulante sono gestite da un'uscita analogica 0-10 V per la modulazione della richiesta.

NOTA (2): La batteria freddo e la batteria caldo in configurazione valvola modulante sono gestite da un'uscita analogica 0-10 V per la modulazione della richiesta.

NOTA (3): La batteria promiscua è una batteria la cui funzione di riscaldamento/raffreddamento dipende dal modo impostato.

NOTA (4): La batteria di postriscaldo si utilizza soprattutto:

in riscaldamento, per deumidificare l'aria;

in raffreddamento, come integrazione alla batteria caldo per riscaldare l'aria se l'azione della batteria caldo non risulta sufficiente.

NOTA (5): La logica di funzionamento delle diverse tipologie di recuperatore è la medesima, ma nel caso di recuperatore a flussi incrociati con serranda di bypass la polarità è invertita rispetto la polarità delle altre due tipologie di recuperatore.

NOTA (6): L'attivazione camera di miscela consente di chiudere le serrande esterne quando viene accesa la batteria di preriscaldo.

Uso scorretto ragionevolmente prevedibile

Qualsiasi impiego del sistema diverso da quanto indicato in 2.3 Uso previsto a pag. 15 e secondo le indicazioni fornite nel presente Manuale è da considerarsi come USO IMPROPRIO e il Fabbricante declina ogni responsabilità in relazione a danni eventualmente provocati a persone o cose e ritiene decaduta la garanzia sul prodotto.

Per maggiori informazioni riguardo alla sicurezza, si veda il paragrafo 10. Informazioni di sicurezza.

Mappa I/O e componenti

Il software del controllore definisce gli I/O richiesti in funzione dei componenti e della configurazione hardware dell'UTA. La mappa I/O e componenti è descritta nelle seguenti tabelle, rispettivamente per:

serrande;

attuatori;

motori;

sonde e altri segnali.

NOTA: Per gli I/O fare riferimento alla documentazione allegata.

NOTA: Per le configurazioni hardware fare riferimento a 2.2.1.2 Configurazione hardware dell'UTA a pag. 17.

In ogni caso tutti gli I/O possono essere allocati manualmente da controllore (fare riferimento a 4.8.2 O-I/O a pag. 96).

NOTA: È possibile non allocare un ingresso o un'uscita anche se la configurazione hardware ne prevede l'allocazione.

Gli I/O richiesti in funzione della configurazione hardware relativa alle serrande è riportata nella seguente tabella.

NOTA: Nella colonna più a destra è indicato con "X" se il componente è sempre presente.

| Componente | Configurazione hardware | DI | AI (NTC) | AI (UNIV) | DO | AO | Sempre presente |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Serrande esterne | ON/OFF | — | — | — | 1 | — | — |
|  | Modulanti + Ricircolo | — | — | — | — | 1 | — |
| Serranda by-pass | Tipologia recuperatore: a flussi incrociati con serranda di bypass | — | — | — | 1 | 1 | — |
| Serrande ventilatori | Serranda: ventilatore mandata; Serranda: ventilatore ripresa; Serranda ventilatore mandata + ventilatore ripresa | — | — | — | 1…4 | — | — |

Tabella 11 - Mappa I/O e componenti - serrande

Gli I/O richiesti in funzione della configurazione hardware relativa agli attuatori è riportata nella seguente tabella.

NOTA: Nella colonna più a destra è indicato con "X" se il componente è sempre presente.

| Componente | Configurazione hardware | DI | AI (NTC) | AI (UNIV) | DO | AO | Sempre presente |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Recuperatore | Tipologia recuperatore: rotativo | 1 | — | — | 1 | 1 | — |
| Batteria di preriscaldo | Tipologia batteria di preriscaldo: resistenza elettrica ON/OFF a step | 1 | — | — | 1 | — | — |
|  | Tipologia batteria di preriscaldo: resistenza elettrica ON/OFF a step + modulante | 1 | — | — | 1 | 1 | — |
|  | Tipologia batteria di preriscaldo: valvola modulante | — | — | — | 1 | 1 | — |
|  | Tipologia batteria di preriscaldo: valvola modulante + pompa | — | — | — | — | 1 | — |
| Batteria freddo |  | Tipologia batteria freddo: motocondensante fino a 4 step o 4 unità parallele | 1…4 | — |  |  | — |  | 1…4 |  | 1…4 |  | — |  |  |
|  | Tipologia batteria freddo: valvola modulante | — | — | — | — | 1 | — |
|  | Tipologia batteria freddo: valvola modulante + pompa | — | — | — | 1 | 1 | — |
| Batteria caldo |  | Tipologia batteria caldo: motocondensante fino a 4 step o 4 unità parallele | 1…4 | — |  |  | — |  | 1…4 |  | 1…4 |  | — |  |  |
|  | Tipologia batteria caldo: resistenza elettrica ON/OFF a step | 1 | — | — | 1…3 | — | — |
|  | Tipologia batteria caldo: resistenza elettrica ON/OFF a step + modulante | 1 | — | — | 1…3 | 1 | — |
|  | Tipologia batteria caldo: valvola modulante | — | — | — | — | 1 | — |
|  | Tipologia batteria caldo: valvola modulante + pompa | — | — | — | 1 | 1 | — |
| Batteria promiscua |  | Tipologia batteria promiscua: motocondensante fino a 4 step o 4 unità parallele | 1…4 | — |  |  | — |  | 1…4 |  | 1…4 |  | — |  |  |
|  | Tipologia batteria promiscua: valvola modulante | — | — | — | — | 1 | — |
|  | Tipologia batteria promiscua: valvola modulante + pompa | — | — | — | 1 | 1 | — |
| Batteria di postriscaldo | Tipologia batteria di postriscaldo: valvola modulante | — | — | — | — | 1 | — |
|  | Tipologia batteria di postriscaldo: valvola modulante + pompa | — | — | — | 1 | 1 | — |
|  | Tipologia batteria di postriscaldo: resistenza elettrica ON/OFF a step | 1 | — | — | 1…3 | 1 | — |
| Umidificatore | Attivazione umidificatore: ON/OFF | 1 | — | — | 1 | — | — |
|  | Attivazione umidificatore: proporzionale | 1 | — | — | 1 | 1 | — |

Tabella 12 – Mappa I/O e componenti – attuatori

Gli I/O richiesti in funzione della configurazione hardware relativa alla ventilazione è riportata nella seguente tabella.

NOTA: Nella colonna più a destra è indicato con “X” se il componente è sempre presente.

| Componente (in caso di ventilatori non Modbus) | Configurazione hardware | DI | AI (NTC) | AI (UNIV) | DO | AO | Sempre presente |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Ventole mandata | Allarme ventilatori: termico | 1 oppure 2 (se attivo ventilatore mandata di backup) | — | — | — | — | — |
|  | Allarme ventilatori: termico + flussostato | 2 oppure 4 (se attivo ventilatore mandata di backup) |  |  |  |  |  |
|  | Numero ventilatori: ventilatore mandata | — | — | — | 1 oppure 2 (se attivo ventilatore mandata di backup) | — | — |
|  | Tipologia ventilatori: modulanti | — | — | — | — | 1 | — |
| Ventola ripresa | Allarme ventilatori: termico | 1 oppure 2 (se attivo ventilatore ripresa di backup) | — | — | — | — | — |
|  | Allarme ventilatori: termico + flussostato | 2 oppure 4 (se attivo ventilatore mandata di backup) |  |  |  |  |  |
|  | Numero ventilatori: ventilatore mandata + ventilatore ripresa | — | — | — | 1 oppure 2 (se attivo ventilatore ripresa di backup) | — | — |
|  | Tipologia ventilatori: modulanti | — | — | — | — | 1 | — |

Tabella 13 – Mappa I/O e componenti – fans

Gli I/O richiesti in funzione della configurazione hardware relativa a sonde e altri segnali è riportata nella seguente tabella.

NOTA: Nella colonna più a destra è indicato con “X” se il componente è sempre presente.

| Componente | Configurazione hardware | DI | AI (NTC) | AI (UNIV) | DO | AO | Sempre presente |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sonda Temperatura ripresa |  | — | 1 | — | — | — | X |
| Sonda Umidità ripresa | Umidificatore o deumidificazione abilitati | — | — | 1 | — | — | — |
| Sonda Temperatura mandata |  | — | 1 | — | — | — | X |
| Sonda Umidità mandata | Umidificatore abilitato | — | — | 1 | — | — | — |
| Sonda esterna | — | — | 1 | — | — | — | — |
| Sonda espulsione | Tipologia recuperatore: a flussi incrociati con serranda di bypass; rotativo | — | 1 | — | — | — | — |
| Sonda preriscaldo | Tipologia batteria di preriscaldo: attiva (se nessuna, opera come riscaldamento primario) | — | 1 | — | — | — | — |
| Sonda saturazione | Tipologia deumidificazione: a punto di rugiada | — | 1 | — | — | — | — |
| Sonda qualità aria: sonda CO2 (1) | Regolazione ventilatori: qualità aria o Qualità aria abilitata con sonda CO2 o CO2 + VOC | — | — | 1 | — | — | — |
| Sonda qualità aria: sonda VOC (1) | Regolazione ventilatori: qualità aria o Qualità aria abilitata con sonda VOC o CO2 + VOC | — | — | 1 | — | — | — |
| Sonda di pressione 0-10 V (2) | Regolazione ventilatori: a portata costante; a pressione costante | — | — | 1 | — | — | — |
| Sonda antigelo per batteria a valvola modulante | Tipologia sonda antigelo: ON/OFF | 1 | — | — | — | — | — |
| Sonda antigelo per batteria a valvola modulante | Tipologia sonda antigelo: NTC | — | 1 | — | — | — | — |
| Pressostato filtri | — | Da 0 a 4 | — | — | — | — | — |
| Allarme ventilatori: flussostato ON/OFF | Allarme flussostato abilitato | Numero di ventole: 1…4 | — | — | — | — | — |
| Ingresso ON/OFF remoto | — | 1 | — | — | — | — | X |
| Ingresso allarme incendio | — | 1 | — | — | — | — | X |
| Ingresso microinterruttore porte | Ingresso porta abilitato | 1 | — | — | — | — | — |
| Ingresso cambio modo estate/inverno | Ingresso modo abilitato | 1 | — | — | — | — | — |
| Uscita per UTA stato ON/OFF | — | — | — | — | 1 | — | X |
| Uscita per modo estate/inverno | Uscita modo abilitato | — | — | — | 1 | — | — |
| Uscita allarme generico (contatto in cambio) | — | — | — | — | 1 | — | X |

Tabella 14 – Mappa I/O e componenti – sonde e altri segnali

NOTA: (1) Deve essere presente almeno una tra sonda CO2 o sonda VOC.

NOTA: (2) Possono essere presenti una o due sonde.

Funzioni

Nella seguente tabella è riportato l’elenco delle funzioni relative all’UTA gestite dal controllore.

| Funzioni | Riferimento nel presente Manuale |
| --- | --- |
| ON/OFF | 3.1 ON/OFF a pag. 25 |
| Cambio modo | 3.3 Modi di funzionamento a pag. 29 |
| Setpoint | 3.2 Setpoint a pag. 28 |
| Fasce orarie ed eventi | 3.4 Fasce orarie ed eventi a pag. 31 |
| Regolazione di temperatura | 3.5 Regolazione di temperatura a pag. 32 |
| Regolazione di umidità | 3.6 Regolazione di umidità a pag. 34 |
| Free-cooling e free-heating | 3.7 Free-cooling e free-heating a pag. 36 |
| Recupero di calore | 3.8 Recupero di calore a pag. 37 |
| Serrande esterne e serrande di ricircolo | 3.9 Serrande esterne e serrande di ricircolo a pag. 41 |
| Attuatori raffrescamento | 3.10 Attuatori per raffrescamento a pag. 42 |
| Attuatori riscaldamento | 3.11 Attuatori per riscaldamento a pag. 44 |
| Pompe | 3.12 Pompe a pag. 48 |
| Ventilatori | 3.13 Ventilatori a pag. 49 |
| Qualità aria: sonda CO2 e sonda VOC | 3.14 Qualità aria: sonda CO2 e sonda VOC a pag. 53 |
| Portata costante | 3.15 Regolazione a portata costante a pag. 54 |
| Pressione costante | 3.16 Regolazione a pressione costante a pag. 54 |
| Test output | 3.17 Test output a pag. 54 |

Tabella 15 – Funzioni relative all’UTA

NOTA: Per ulteriori informazioni sui parametri riportati nel prosieguo del capitolo fare riferimento a 2.2 Menu Display a pag. 10 e a 4 Menu Impostazioni Utente a pag. 55.

Convenzioni per grafici funzioni

Nel prosieguo del presente Manuale, per i grafici illustrativi di alcune funzioni si adottano le convenzioni riportate nella seguente tabella.

| Actuator Request | Richiesta all’attuatore (regolato) |
| --- | --- |
| Cooler | Attuatore freddo |
| Cooling | Raffreddamento |
| Heater | Attuatore caldo |
| Heating | Riscaldamento |
| Hysteresis | Isteresi |
| Main probe | Sonda principale, relativa al regolatore di temperatura principale |
| PI request | Richiesta del regolatore PI (che regola l’attuatore) |
| PI Input | Ingresso del regolatore PI |
| PI Output | Uscita del regolatore PI |
| Post-Heater | Batteria di postriscaldo |
| Recovery | Recuperatore |
| Return | Sonda ripresa |
| Summer mode | Modo estate |
| Supply | Sonda mandata |
| Text | Temperatura esterna |
| Tret | Temperatura di ripresa |
| Winter mode | Modo inverno |
| Electric heater | Resistenza elettrica |
| Damper | Serranda esterna |

Tabella 16 – Convenzioni per grafici funzioni

ON/OFF

Accensione

L’accensione dell’UTA avviene secondo una delle seguenti modalità:

standard;

con messa a regime, dove si mantengono inizialmente chiuse le serrande e gli attuatori per riscaldamento sono forzati alla massima potenza per ridurre il tempo di raggiungimento del setpoint desiderato.

Per maggiori dettagli relativi alla procedura di accensione standard vedi 3.1.1.1.

Per maggiori dettagli relativi alla procedura di accensione con messa a regime vedi 3.1.1.2.

L’accensione può essere gestita anche da BMS tramite protocollo Modbus o Bacnet (lo stato predefinito è ON).

L’UTA è in stato di ON se è richiesto contemporaneamente da:

ingresso digitale;

display;

BMS.

Accensione standard

In caso accensione standard (Fig 3 – a pag. 26), il controllore esegue nell’ordine le seguenti operazioni:

verifica l’assenza di allarmi;

porta le serrande esterne in apertura minima;

accende il ventilatore mandata e di ripresa;

attiva le regolazioni degli attuatori.

Fig 3 – Passaggio a stato ON senza messa a regime

Accensione con messa a regime

In caso accensione con messa a regime (Fig 4 – a pag. 26), il controllore esegue nell’ordine le seguenti operazioni:

- verifica l’assenza di allarmi;

accende il ventilatore mandata e di ripresa;

attiva gli attuatori per riscaldamento alla massima potenza.

al raggiungimento del setpoint o del time-out, le serrande esterne si portano ad apertura minima.

attiva le regolazioni degli attuatori

Fig 4 – Passaggio a stato ON con messa a regime

In caso di:

free-cooling,

free-heating

viene disattivata la messa a regime all’accensione.

Durante la messa a regime è forzata l’abilitazione dei limiti di mandata a prescindere dal relativo parametro di abilitazione.

Spegnimento

Lo spegnimento (Fig 5 – a pag. 27) consiste nel passaggio dell’UTA a stato OFF con il controllore che esegue nell’ordine le seguenti operazioni:

- disattiva le regolazioni agli attuatori;

eventualmente, avvia la postventilazione (se erano accese le resistenze elettriche o la motocondensante);

spegne il ventilatore mandata e il ventilatore ripresa;

chiude le serrande esterne.

Fig 5 – Spegnimento

NOTA: Lo stato di OFF da ingresso digitale ha massima priorità.

Lo stato di OFF/ON da porta seriale BMS ha priorità maggiore rispetto allo stato di OFF/ON:

da controllore;

mediante fasce orarie ed eventi (fare riferimento a 3.4 Fasce orarie ed eventi a pag. 31).

L’UTA è in stato di OFF se lo stato di OFF è verificato in almeno uno tra i seguenti casi:

su ingresso digitale;

su controllore;

su porta seriale BMS;

su fasce orarie.

Setpoint

È possibile definire tre setpoint, uno per ciascuno dei tre modi di funzionamento:

setpoint estate;

setpoint inverno;

setpoint auto.

NOTA: I tre setpoint corrispondono ai tre modi di funzionamento descritti in 3.3 Modi di funzionamento a pag. 29.

Ciascun setpoint può essere abbinato, sia in temperatura sia in umidità, a uno dei seguenti profili:

comfort,

economy,

night.

Il profilo night è caratterizzato da:

stesso setpoint del profilo economy;

velocità dei ventilatori ridotta al minimo.

Le caratteristiche dei profili economy e comfort in funzione dei setpoint sono descritte nella seguente tabella.

| Setpoint | Caratteristica dei profili economy e comfort |
| --- | --- |
| Estate | setpoint con profilo economy (parametro SP_T_CoolEco_E2) > setpoint con profilo comfort (parametro SP_T_Cool_E2) |
| Inverno | setpoint con profilo economy (parametro SP_T_HeatEco_E2) < setpoint con profilo comfort (parametro SP_T_Heat_E2) |
| Auto | setpoint con profilo economy = setpoint con profilo comfort ± offset (parametro DIFF_T_AutoEco) |

Tabella 17 – Caratteristiche dei profili economy e comfort in funzione dei setpoint

NOTA: Il parametro DIFF_T_AutoEco è definito anche come zona neutra.

NOTA: Il parametro SP_T_Auto_E2 è il setpoint auto da parametro, il parametro T_RegulationProbe è il setpoint corrente dovuto a economy/comfort, Bacnet, auto/estate/inverno.

Modi di funzionamento

Il controllore ammette tre modi di funzionamento per l’UTA:

inverno;

estate;

auto.

NOTA: In determinate configurazioni hardware dell’UTA (fare riferimento a 3.3.1 Configurazione hardware dell’UTA per realizzare il cambio modo a pag. 29), è ammesso il cambio modo estate/inverno, ovvero il passaggio da modo estate a modo inverno o viceversa. Per le modalità di esecuzione del cambio modo fare riferimento a 3.3.2 Modalità per eseguire il cambio modo a pag. 29.

In modo inverno sono attivati gli attuatori caldo per riscaldare l’aria ed eventualmente il recuperatore per limitare un eccessivo aumento della temperatura.

In modo estate sono attivati gli attuatori freddo per raffrescare l’aria ed eventualmente il recuperatore per limitare un’eccessiva diminuzione della temperatura.

NOTA: In modo estate non è possibile accendere le resistenze elettriche.

In modo auto (fare riferimento a 3.3.3 Funzionamento del modo auto a pag. 30) si ha passaggio automatico dell’UTA da raffrescamento a riscaldamento (e viceversa) in funzione della temperatura di regolazione e del setpoint di temperatura; è quindi possibile attivare sia gli attuatori caldo sia gli attuatori freddo.

Configurazione hardware dell’UTA per realizzare il cambio modo

Il cambio modo estate/inverno non è ammesso in assenza del recuperatore e con UTA configurato con componenti che realizzano solo caldo o solo freddo. Se è presente il solo recuperatore è possibile comunque realizzare il raffreddamento e il riscaldamento.

NOTA: Il cambio modo estate/inverno è forzato in modo auto in caso di configurazione dell’UTA dove:

sono attivi esclusivamente i ventilatori, oppure

è attivo esclusivamente il recuperatore.

Il passaggio da modo estate a modo inverno (heating):

è disattivo se presente una richiesta di deumidificazione in quanto la deumidificazione impedisce il riscaldamento;

è possibile se la richiesta di raffrescamento del regolatore di temperatura è conclusa.

Il passaggio da modo inverno a modo estate (cooling) è possibile se la richiesta di riscaldamento del regolatore di temperatura è conclusa.

Modalità per eseguire il cambio modo

Il cambio modo estate/inverno può essere eseguito da:

ingresso digitale;

tastiera, con cambio modo estate/inverno impostato automaticamente di default;

porta seriale BMS.

NOTA: Se abilitato, il cambio modo estate/inverno da ingresso digitale ha priorità rispetto alla selezione da tastiera; in questo caso il modo auto non è ammesso.

Funzionamento del modo auto

In modo auto, il passaggio da raffrescamento a riscaldamento (e viceversa) dipende:

dalla richiesta di caldo o di freddo del regolatore di temperatura principale;

dalla temperatura esterna:

in caso di temperatura esterna inferiore al parametro SP_T_FORCEWINTER, si ha forzatura a riscaldamento (1 – Fig 6 – a pag. 30);

in caso di temperatura esterna superiore al parametro SP_T_FORCESUMMER, si ha forzatura a raffreddamento (2 – Fig 6 – a pag. 30);

in caso di temperatura esterna compresa tra i due precedenti parametri, a seconda del tipo di regolazione di temperatura (fare riferimento a 3.5 Regolazione di temperatura a pag. 32) il passaggio da raffrescamento a riscaldamento (e viceversa) è gestito mediante sonda ripresa o sonda mandata (3 – Fig 6 – a pag. 30).

Fig 6 – Funzionamento del modo auto

In Fig 6 – a pag. 30 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per il funzionamento in modo auto. Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | SP_T_FORCEWINTER |
| B | SP_T_FORCESUMMER |
| C | DIFF_T_AutoChangeMode |
| D | SP_T_Auto_E2 (setpoint da parametro) T_CurrentSetpointByPar (setpoint corrente) |
| E | T_RegulationProbe |

Tabella 18 – Funzionamento del modo auto

Fasce orarie ed eventi

L’UTA può assumere stato ON (regolatori attivi) o stato OFF (regolatori disattivi) in funzione delle fasce orarie o eventi. L’occorrenza di un evento ha priorità sulle fasce orarie.

NOTA: È possibile forzare lo stato stand-by da tastiera.

NOTA: La funzione fasce orarie ed eventi supporta il cambio ora legale/solare.

Fasce orarie

Per ogni giorno della settimana è possibile scegliere tra quattro programmi:

P1,

P2,

P3,

P4

indipendentemente dal modo impostato (estate, inverno, auto).

Nel programma P1 e nel programma P2 è possibile definire quattro orari, dove a ogni orario si può associare uno dei seguenti stati-profili:

OFF,

ON con profilo comfort,

ON con profilo economy,

ON con profilo night.

Se attivo il programma P3 l’UTA è in stato ON tutto il giorno in profilo comfort.

Se attivo il programma P4 l’UTA è in stato OFF tutto il giorno.

Eventi

È possibile abilitare fino a 15 eventi. Ciascun evento è caratterizzato da:

un giorno di inizio;

un giorno di fine;

un stato-profilo associato.

Regolazione di temperatura

NOTA: Per i setpoint fare riferimento a 3.2 Setpoint a pag. 28.

Nella regolazione di temperatura vengono accesi in sequenza il recuperatore e i vari attuatori caldo e attuatori freddo.

Sono possibili tre tipologie di regolazione di temperatura:

regolazione di temperatura in mandata, con regolazione sulla sonda mandata;

regolazione di temperatura in ripresa, con regolazione sulla sonda ripresa e limite fornito dalla sonda mandata;

regolazione di temperatura in cascata, con regolazione sulla sonda mandata rispetto al regolatore di ripresa.

Nelle tre tipologie di regolazione di temperatura, la sonda di mandata è sempre presente.

NOTA: È possibile configurare la ripartizione richiesta ai vari regolatori degli attuatori.

La Fig 7 – a pag. 32 descrive il caso di regolazione di temperatura in mandata o in cascata; nel caso di regolazione di temperatura in ripresa, il regolatore del recuperatore non è presente in quanto il recuperatore è gestito da un regolatore indipendente.

Il regolatore di temperatura attiva alternativamente:

raffrescamento, la cui richiesta sugli attuatori è riportata in (1 – Fig 7 – a pag. 32);

riscaldamento, la cui richiesta sugli attuatori è riportata in (2 – Fig 7 – a pag. 32).

NOTA: A seconda della configurazione hardware dell’UTA, in Fig 7 – a pag. 32 i seguenti regolatori potrebbero non essere presenti:

regolatore del recuperatore;

regolatore della batteria di postriscaldo.

Fig 7 – Regolazione di temperatura

In Fig 7 – a pag. 32 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per la regolazione di temperatura. Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | RecoveryPower |
| B | PostPower |

Tabella 19 – Regolazione di temperatura

Boost

La funzionalità boost permette di eseguire da tastiera una messa a regime, simile a quella prevista all’accensione (fare riferimento a 3.1.1.2) in qualsiasi momento successivo allo stato stand-by.

Regolatore di preriscaldo

Se abilitato, il regolatore di preriscaldo è un regolatore PI operante esclusivamente in riscaldamento per mantenere la temperatura al setpoint di preriscaldo.

Il regolatore di preriscaldo è disabilitato durante la messa a regime all’accensione (fare riferimento a 3.1.1.2 Passaggio a stato ON con messa a regime a pag. 26) o il boost (fare riferimento a 3.5.1 Boost a pag. 33).

Limiti in mandata della temperatura

Se abilitati, i limiti in mandata di temperatura sono limitazioni alla regolazione di temperatura in ripresa:

in raffrescamento, è una limitazione inferiore alla diminuzione di temperatura dell’aria di mandata;

in riscaldamento, è una limitazione superiore all’aumento di temperatura dell’aria di mandata.

NOTA: In caso di regolazione in cascata la limitazione non è necessaria.

Con regolatore di preriscaldo (fare riferimento a 3.5.2 Regolatore di preriscaldo a pag. 33), la limitazione superiore dell’aumento di temperatura dell’aria di mandata durante il riscaldamento viene eseguita mediante la sonda preriscaldo (se presente).

Con richiesta di deumidificazione (fare riferimento a 3.6.2 Regolazione deumidificazione a pag. 34), si ha la limitazione inferiore della diminuzione di temperatura dell’aria di mandata durante il raffreddamento.

Regolazione di umidità

L’umidificazione dell’aria è realizzata mediante l’umidificatore, la deumidificazione dell’aria non è realizzata da uno specifico attuatore fisico ma è realizzata mediante l’azione combinata di due attuatori:

batteria freddo, come attuatore freddo;

batteria di postriscaldo, come attuatore caldo.

Regolazione umidificazione

Durante la regolazione dell’umidificazione dell’aria di mandata, la variazione della temperatura dell’aria di mandata stessa è trascurabile. Fino al raggiungimento del setpoint di umidità, il controllore:

abilita la produzione di vapore;

modula la quantità di vapore prodotto mediante segnale 0-10 V.

Il regolatore dell’umidificatore è proporzionale o ON/OFF, con:

sonda di umidità di ripresa dotata di isteresi;

sonda di umidità di mandata utilizzata come sonda limite.

Regolazione deumidificazione

Deumidificazione standard

La regolazione PI agisce sull’attuatore freddo per ottenere il setpoint di umidità richiesto. La regolazione viene eseguita sul valore di umidità acquisito dalla sonda di umidità di ripresa.

A una richiesta di deumidificazione, causata da un’umidità dell’aria di ripresa troppo elevata, si attiva la batteria freddo, che equivale a una regolazione di ripresa in raffrescamento.

Durante la deumidificazione la batteria di postriscaldo, necessariamente attivata, ha la funzione di compensare il raffreddamento. La batteria di postriscaldo regola la temperatura dell’aria di mandata con il setpoint di temperatura principale.

NOTA: La batteria freddo viene pilotata dalla più vincolante tra:

la richiesta di deumidificazione;

la richiesta di raffreddamento.

Il regolatore di postriscaldo viene:

attivato, in caso di diminuzione della temperatura di regolazione (mandata/ripresa) a un valore inferiore della differenza tra setpoint di postriscaldo e offset di postriscaldo;

disattivato, in caso di raggiungimento del setpoint di postriscaldo.

NOTA: La batteria di postriscaldo può operare:

sia come integrazione dell’azione della batteria di preriscaldo sia come compensazione della diminuzione di temperatura causata dalla deumidificazione (se presente).

Punto di rugiada

L’abilitazione del regolatore di deumidificazione a punto di rugiada è di tipo ON/OFF con differenziale impostabile mediante parametro Dehum_Req_Diff ed è funzione dalla sonda di umidità di ripresa.

Il regolatore utilizza la sonda di temperatura di saturazione posizionata a valle della batteria freddo.

Il controllore calcola il punto di rugiada a partire dal setpoint di temperatura di ripresa e dal setpoint di umidità di ripresa. Il punto di rugiada rappresenta il setpoint che la batteria freddo deve mantenere confrontandolo con il valore acquisito dalla sonda di temperatura di saturazione.

Deumidificazione con aria esterna (o invernale)

È una deumidificazione attiva in raffrescamento.

NOTA: In modo inverno gli attuatori caldo sono abilitati.

Per poter avviare la deumidificazione con aria esterna è necessario:

attivare la deumidificazione da Fabbricante e service;

attivare la sonda di umidità esterna;

attivare la sonda di temperatura esterna;

attivare le serrande esterne in configurazione ON/OFF + miscela 0-10V.

NOTA: La deumidificazione con aria esterna è attiva solo se abilitata dal Fabbricante mediante parametro cfgDeHumidifier. Una volta abilitata dal Fabbricante, tale deumidificazione può essere gestita dal service mediante parametro di abilitazione Dehum_WinterEn.

La regolazione è ON/OFF con differenziale impostabile. In caso il regolatore richieda la deumidificazione, se la somma tra umidità specifica esterna e il differenziale risulta inferiore dell’umidità specifica interna:

le serrande esterne vengono aperte completamente;

se necessario, la batteria di postriscaldo viene attivata.

Free-cooling e free-heating

Il free-cooling è:

disattivo in caso di temperatura esterna eccessivamente ridotta;

attivo in caso siano soddisfatte contemporaneamente le seguenti condizioni:

Treg – Text ≥ FreeCHDiff;

Treg > T_CurrentSetpointByPar;

Text > FreeCHMinExtTemp.

NOTA: Treg indica la temperatura della sonda di regolazione, Text indica la temperatura esterna.

NOTA: Il valore di default:

del parametro FreeCHDiff è pari a 5 °C;

del parametro FreeCHMinExtTemp è pari a 12 °C.

NOTA: Il parametro T_CurrentSetpointByPar è il setpoint corrente di free-cooling relativo alla regolazione di temperatura o, nel caso di regolazione di temperatura in cascata, il setpoint del regolatore di mandata.

Il free-heating è:

disattivo in caso di temperatura esterna eccessivamente elevata;

attivo in caso siano soddisfatte contemporaneamente le seguenti condizioni:

Text – Treg ≥ FreeCHDiff;

Treg < T_CurrentSetpointByPar.

NOTA: Il parametro T_CurrentSetpointByPar è il setpoint corrente di free-heating relativo alla regolazione di temperatura o, nel caso di regolazione di temperatura in cascata, il setpoint del regolatore di mandata.

In caso di attivazione del free-cooling o del free-heating, gli attuatori vengono arrestati per un tempo massimo impostabile per consentire all’UTA di raggiungere il setpoint (di free-cooling o free-heating) richiesto senza consumo di energia. In caso di mancato raggiungimento di tale setpoint entro tale tempo massimo, gli attuatori vengono ripristinati.

Il funzionamento delle serrande esterne in funzione del valore del parametro cfgFreeHeating e del parametro cfgFreeCooling è descritto nella seguente tabella.

| Valore del parametro | Regolatore delle serrande esterne | Serrande esterne |
| --- | --- | --- |
| cfgFreeHeating = 1 | Regolatore P | Le serrande esterne vengono aperte proporzionalmente alla differenza tra il relativo setpoint e la temperatura di regolazione |
| cfgFreeCooling = 1 | Regolatore P | Le serrande esterne vengono aperte proporzionalmente alla differenza tra la temperatura di regolazione e la temperatura esterna |
| cfgFreeHeating = 2 | Regolatore del recuperatore | Le serrande esterne sono regolate in parallelo al recuperatore |
| cfgFreeCooling = 2 | Regolatore del recuperatore | Le serrande esterne sono regolate in parallelo al recuperatore |

Tabella 20 – Funzionamento serrande esterne in funzione dei parametri cfgFreeHeating e cfgFreeCooling

In caso di recuperatore a flussi incrociati con serranda di bypass, la relativa serranda consente di prelevare aria dall’esterno e inviarla direttamente in ambiente, se presenti condizioni favorevoli (free-cooling o free-heating).

Recupero di calore

Se attivo, il recuperatore può risultare conveniente da un punto di vista energetico il recupero di calore. Il recupero di calore consiste in uno scambio termico, attuato dal recuperatore, tra l’aria di mandata e l’aria di espulsione:

per preriscaldare l’aria di mandata, se la temperatura esterna è eccessivamente ridotta;

per preraffreddare l’aria di mandata, se la temperatura esterna è eccessivamente elevata.

Le condizioni di avvio e arresto del recupero di calore sono descritte nella seguente tabella.

| Regolazione | Heating/Cooling | Condizione di avvio del recupero di calore | Condizione di arresto del recupero di calore |
| --- | --- | --- | --- |
| Ripresa/Cascata | Heating | Text ≤ Trip | Text > Trip + RecoveryDiff_Band |
| Ripresa/Cascata | Cooling | Text ≥ Trip | Text + RecoveryDiff_Band < Trip |
| Mandata | Heating | Text ≤ setpoint e se Trip presente: Text ≤ Trip | Text > setpoint + RecoveryDiff_Band e se Trip presente: Text > Trip + RecoveryDiff_Band |
| Mandata | Cooling | Text ≥ setpoint e se Trip presente Text ≥ Trip | Text + RecoveryDiff_Band < setpoint e se Trip presente: Text + RecoveryDiff_Band < Trip |

Tabella 21 – Condizioni di avvio e arresto del recupero di calore

NOTA: Il valore di default del parametro RecoveryDiff_Band è pari a 1,5 °C.

Sbrinamento (o antigelo) recuperatore

Lo sbrinamento (o antigelo) recuperatore è una funzione che previene la formazione di gelo sul recuperatore, che può verificarsi a seguito dello scambio di calore tra i flussi di aria.

Per eseguire lo sbrinamento recuperatore è possibile, alternativamente:

ridurre la velocità del ventilatore mandata con inverter;

attivare la batteria di preriscaldo e chiudere la serranda esterna modulante, se le seguenti condizioni sono contemporaneamente soddisfatte:

è attiva la batteria preriscaldo,

è abilitato il parametro cfgMixChamberBeforePreHeat.

NOTA: Lo sbrinamento recuperatore mediante riduzione della velocità del ventilatore mandata ha avvio dopo 240 secondi dall’accensione del ventilatore mandata.

A seconda della tipologia di recuperatore, durante lo sbrinamento il recuperatore ha il funzionamento descritto nella seguente tabella.

| Tipologia di recuperatore | Funzionamento del recuperatore durante lo sbrinamento recuperatore |
| --- | --- |
| A flussi incrociati con serranda di bypass | La serranda di bypass del recuperatore rimane chiusa |
| A batterie | La pompa del recuperatore continua a funzionare |
| Rotativo | La ruota del recuperatore continua a funzionare |

Tabella 22 – Funzionamento del recuperatore durante lo sbrinamento recuperatore

Recupero di calore con regolazione in ripresa

Il recuperatore opera indipendentemente dalla richiesta del regolatore principale di temperatura e la sonda di mandata è utilizzata come sonda limite.

NOTA: I grafici riportati in Fig 8 – a pag. 39 si riferiscono al recuperatore rotativo. In caso di recuperatore a flussi incrociati con serranda di bypass i relativi grafici sono speculari.

NOTA: In Fig 8 – a pag. 39, le seguenti disuguaglianze rappresentano l’ampiezza di isteresi relativa al recuperatore con regolazione in ripresa in caso di riscaldamento:

Text minore o uguale di Tret;

Text maggiore di Tret + RecoveryDiff_Band.

NOTA: In Fig 8 – a pag. 39, le seguenti disuguaglianze rappresentano l’ampiezza di isteresi relativa al recuperatore con regolazione in ripresa in caso di raffrescamento:

Text maggiore o uguale di Tret;

Text + RecoveryDiff_Band minore di Tret .

In Fig 8 – a pag. 39 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per il recupero di calore con regolazione in ripresa. Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | RecoveryDiff_Band |
| B | T_CurrentSetpointByPar + RecoveryDeadZone |
| C | T_CurrentSetpointByPar – RecoveryDeadZone |

Tabella 23 – Recupero di calore con regolazione in ripresa

Con riferimento a Fig 8 – a pag. 39, a titolo esemplificativo il funzionamento della regolazione in ripresa con raffrescamento e Text + RecoveryDiff_Band < Tret è descritto nella seguente tabella.

| Valore della temperatura di ripresa (Tret) | Modalità di raffrescamento |
| --- | --- |
| Molto elevato | Il recuperatore viene disattivato e l’aria dell’UTA viene raffrescata prelevando aria dall’esterno, in quanto a temperatura bassa |
| Inferiore al setpoint di raffrescamento | Il recuperatore viene attivato e non viene prelevata aria dall’esterno in quanto la temperatura è troppo bassa |

Tabella 24 – Funzionamento della regolazione in ripresa con raffrescamento e Text + RecoveryDiff_Band < Tret

Fig 8 – Recupero di calore con regolazione in ripresa

Recupero di calore con regolazione in mandata o in cascata

Il recuperatore di calore viene attivato dal regolatore di temperatura come riportato in Fig 7 – a pag. 32. In questo tipo di regolazione, il regolatore del recuperatore è sempre il primo regolatore a intervenire, successivamente vengono attivati anche gli altri attuatori caldo/freddo.

NOTA: Nel caso le condizioni di avvio del recupero di calore non siano soddisfatte, la richiesta di caldo/freddo del regolatore è soddisfatta dai soli attuatori caldo/freddo. Con riferimento a Fig 9 – a pag. 40, il regolatore del recuperatore è gestito mediante un’uscita analogica.

Fig 9 – Recupero di calore con regolazione in mandata o in cascata

In Fig 9 – a pag. 40 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per il recupero di calore con regolazione in mandata o in cascata. Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | RecoveryPower |

Tabella 25 – Recupero di calore con regolazione in mandata o in cascata

Serrande esterne e serrande di ricircolo

NOTA: In funzionamento normale le serrande esterne hanno un’apertura minima per garantire il ricambio di aria nell’UTA.

Le serrande esterne sono pilotate dalla medesima uscita del controllore. Esse vengono completamente chiuse se si verifica almeno una tra le seguenti condizioni:

UTA in stato OFF;

messa a regime in corso (per minimizzare il tempo di raggiungimento del setpoint);

allarme antigelo attivo (per riscaldare mediante avvio dell’antigelo, se presente batteria di preriscaldo);

sbrinamento recuperatore attivo (fare riferimento a 3.8 Recupero di calore a pag. 37).

| Uscita analogica relativa alle serrande | Serrande esterne | Serrande di ricircolo |
| --- | --- | --- |
| 0% | Chiuse | Aperte |
| 100% | Aperte | Chiuse |

Tabella 26 – Logica di funzionamento delle serrande esterne e delle serrande di ricircolo

La relazione tra condizione dell’UTA e apertura delle serrande esterne è descritta nella seguente tabella.

| Condizioni dell’UTA | Apertura delle serrande esterne |
| --- | --- |
| Normale | Apertura minima (default pari al 30%) |
| Modalità free-cooling/free-heating | Apertura delle serrande esterne proporzionale (parametro cfgFreeCooling o cfgFreeHeating pari a 1) |
| Regolazione CO2/VOC | Modulazione tra apertura minima (default pari al 30%) e apertura massima (100%) |
| Regolazione legata al recupero di calore in modalità free-cooling/free-heating | Apertura delle serrande esterne proporzionale (parametro cfgFreeCooling o cfgFreeHeating pari a 2) |

Tabella 27 – Condizione dell’UTA e apertura delle serrande esterne

La regolazione CO2 è realizzata sul valore acquisito dalla sonda CO2, la regolazione VOC è realizzata sul valore acquisito dalla sonda VOC. Da un punto di vista logico, la regolazione CO2 è identica alla regolazione VOC; se presenti entrambe, si considera attivo il regolatore che ha una richiesta maggiore.

In caso di:

recuperatore modulante, l’apertura delle serrande esterne è regolata in parallelo al recuperatore;

recuperatore ON/OFF, l’apertura delle serrande esterne inizia dopo che il recuperatore è in stato OFF.

NOTA: La regolazione CO2/VOC è prioritaria rispetto alla regolazione legata al recupero di calore.

La gestione serrande in configurazione ON/OFF consiste nell’aprire/chiudere le serrande esterne quando l’UTA è in stato ON/OFF.

La gestione serrande in configurazione esterne e miscela 0-10 V consiste nell’azionare le serrande esterne modulanti e la serranda di ricircolo, in opposizione rispetto alle serrande esterne modulanti: se le serrande esterne sono completamente aperte, la serranda di ricircolo è completamente chiusa, e viceversa. Solitamente in caso di serrande esterne modulanti:

si aprono le serrande esterne a una percentuale fissa,

si aprono ulteriormente le serrande esterne in caso di:

richiesta da sonda CO2/VOC (qualità aria);

free-cooling.

Attuatori per raffrescamento

Gli attuatori freddo gestiti sono descritti nella seguente tabella.

| Attuatori per raffrescamento | Modalità di gestione |
| --- | --- |
| Valvole (1 – Fig 10 - a pag. 43) | Uscita analogica 0-10 V |
| Motocondensante fino a 4 step (2 – Fig 10 - a pag. 43) | Comando a step |
| Motocondensanti modulanti, fino a 4 | Uscite analogiche 0-10 V |

Tabella 28 - Attuatori freddo gestiti e relative modalità di gestione

NOTA: In caso di resistenza elettrica 0-10 V + step o di resistenza elettrica PWM + step, uscita analogica e uscita digitale sono tra loro legate in quanto la modulante interpola step consecutivi. In caso di motocondensante, uscita analogica e uscita digitale intervengono nella regolazione in modo indipendente tra loro.

In Fig 10 - a pag. 43 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per gli attuatori freddo.

Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | CondUnitS1_Req |
| B | CondUnitS2_Req |
| C | CondUnitS3_Req |
| D | CondUnitS4_Req |

Tabella 29 - Attuatori freddo

In Fig 10 - a pag. 43 sono indicati, mediante i tag (lettere minuscole):

e, il passo dell’isteresi,

f, l’ampiezza dell’isteresi

legate tra loro dalla seguente relazione:

f = e · [CondUnitSx_Hysteresis]/100

La richiesta totale di raffreddamento viene suddivisa fra i vari attuatori in cascata, in base ai parametri, ed è dipendente dai limiti in mandata. In caso di motocondensante fino a 4 step, i parametri per la regolazione degli attuatori freddo sono:

percentuale di richiesta di regolazione alla motocondensante per ogni step;

isteresi, calcolata come percentuale dello step.

E’ possibile definire un tempo minimo di ON e di OFF per l’accensione della motocondensante e un offset della relativa uscita modulante che verrà applicato nel caso almeno un gradino sia attivo (l’uscite è 0V quando tutti i gradini sono OFF).

Nel caso vengano selezionate più unità motocondensanti queste vengono accese secondo una logica a step proporzionale alla richiesta del regolatore di temperatura e una potenza bilanciata su ciascuna delle unità attive.

Fig 10 - Attuatori freddo

Attuatori per riscaldamento

Gli attuatori per riscaldamento gestiti sono descritti nella seguente tabella.

| Attuatori caldo | Modalità di gestione |
| --- | --- |
| Valvole | Uscita analogica 0-10 V |
| Motocondensante fino a 4 step | Fino a 4 step ON/OFF |
| Motocondensanti modulanti, fino a 4 | Uscite analogiche 0-10 V |
| Resistenze | Fino a 6 step ON/OFF + eventuale modulazione con uscita PWM |

Tabella 30 - Attuatori per riscaldamento gestiti e relative modalità di gestione

Si tratta di una regolazione che ha due componenti:

analogica, per attuare la modulazione;

digitale, per attuare gli step.

La potenza della componente analogica (modulazione) deve essere maggiore o uguale alla potenza della componente digitale (step ON/OFF) per assicurare il raccordo tra due step consecutivi. La potenza della componente digitale è espressa in %/kW di ogni step.

L’isteresi di spegnimento degli step è definita in percentuale dello step.

Se presente la resistenza modulante, l'isteresi massima è limitata a 1/4 dello step di potenza minima.

NOTA: Gli step sono implementati per mezzo di una combinazione di relè attivati (fare riferimento a 3.11.1 Relè attivati e numero di step a pag. 46).

In Fig 11 - a pag. 45 sono illustrati i grafici di richiesta totale di riscaldamento del regolatore PI, con le relative componenti:

analogica, fornita da un'uscita analogica, indicata con AO;

digitale, fornita da uscite digitali, indicata con DO.

NOTA: Ogni step della componente digitale DO è caratterizzato da un'isteresi negativa.

NOTA: L'esempio riportato in Fig 11 - a pag. 45 si riferisce a due step digitali e un'uscita analogica di pari potenza con isteresi pari a (6/33)·100%.

Il funzionamento delle Motocondensanti è descritto al capitolo 3.10

Fig 11 - Attuatori caldo

Nella seguente tabella sono riportati i parametri di riferimento per Fig 11 - a pag. 45.

| Parametri relativi a Heater | Parametri relativi a Pre Heater | Parametri relativi a Post Heater | Descrizione |
| --- | --- | --- | --- |
| Heater_Power_Analog | PreHeater_Power_Analog | PostHeater_Power_Analog | Potenza relativa allo stadio analogico |
| Heater_Power_Step1 | PreHeater_Power_Step1 | PostHeater_Power_Step1 | Potenza relativa allo stadio digitale 1 |
| Heater_Power_Step2 | PreHeater_Power_Step2 | PostHeater_Power_Step2 | Potenza relativa allo stadio digitale 2 |
| Heater_Power_Step3 | PreHeater_Power_Step3 | PostHeater_Power_Step3 | Potenza relativa allo stadio digitale 3 |
| Heater_Power_Step4 | PreHeater_Power_Step4 | PostHeater_Power_Step4 | Potenza relativa allo stadio digitale 4 |
| Heater_Power_Step5 | PreHeater_Power_Step5 | PostHeater_Power_Step5 | Potenza relativa allo stadio digitale 5 |
| Heater_Power_Step6 | PreHeater_Power_Step6 | PostHeater_Power_Step6 | Potenza relativa allo stadio digitale 6 |
| Heater_Hysteresis | PreHeater_Hysteresis | PostHeater_Hysteresis | Isteresi % dello stadio attivo |

Tabella 31 - Attuatori caldo

Relè attivati e numero di step

I relè attivati per ottenere un dato numero di step sono descritti nelle seguenti tabelle.

| Relè | Step 1 | Step 2 |
| --- | --- | --- |
| 1 | X | X |
| 2 |  | X |
| Schema |  |  |

Tabella 32 - Connessione uscite digitali: 2 step, 2 relè

| Relè | Step 1 | Step 2 | Step 3 |
| --- | --- | --- | --- |
| 1 | X |  | X |
| 2 |  | X | X |
| Schema |  |  |  |

Tabella 33 - Connessione uscite digitali: 3 step, 2 relè

| Relè | Step 1 | Step 2 | Step 3 | Step 4 |
| --- | --- | --- | --- | --- |
| 1 | X |  | X | X |
| 2 |  | X | X | X |
| 3 |  |  |  | X |
| Schema |  |  |  |  |

Tabella 34 - Connessione uscite digitali: 4 step, 3 relè

| Relè | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 |
| --- | --- | --- | --- | --- | --- |
| 1 | X |  | X |  | X |
| 2 |  | X | X | X | X |
| 3 |  |  |  | X | X |
| Schema |  |  |  |  |  |

Tabella 35 - Connessione uscite digitali: 5 step, 3 relè

| Relè | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  | X |  | X |
| 2 |  | X |  |  | X | X |
| 3 |  |  | X | X | X | X |
| Schema |  |  |  |  |  |  |

Tabella 36 - Connessione uscite digitali: 6 step, 3 relè

Pompe

La gestione di una pompa può essere abilitata congiuntamente

ad una valvola con uscita analogica 0-10 V.

La gestione di una pompa con valvola caldo è descritta nella seguente tabella.

| Stato della pompa | Condizione |
| --- | --- |
| Accensione | Apertura della valvola |
| Spegnimento | - Dopo 5 minuti dalla chiusura della valvola (tempo di postfunzionamento), o - se UTA in stato OFF |

Tabella 37 - Gestione delle pompe

È possibile abilitare la funzione antisticking per evitare il blocco della pompa se essa rimane spenta per un lungo periodo: in caso di mancato utilizzo della pompa superiore a 7 giorni, la pompa viene avviata automaticamente (fare riferimento al parametro Pump_AntiStickingPeriod e al parametro Pump_AntiStickingRun).

Ventilatori

Se nella configurazione hardware dell'UTA:

è presente un unico ventilatore, se viene disattivato l'UTA passa in stato OFF;

sono presenti più ventilatori e ne viene disattivato un numero tale da non consentire un corretto funzionamento dell'UTA, viene generato un allarme.

Ciascun ventilatore può essere disattivato mediante parametro (fare riferimento a 4 Menu Impostazioni Utente a pag. 55).

I ventilatori hanno due ritardi di tempo:

in accensione/spegnimento dell'UTA, per permettere l'apertura e la chiusura delle serrande;

in postventilazione, dopo l'eventuale spegnimento delle resistenze e/o delle motocondensanti.

In riscaldamento, se attive le resistenze elettriche, l'avvio delle resistenze elettriche è ritardato rispetto all'avvio dei ventilatori, come illustrato in Fig 12 - a pag. 49: la regolazione delle resistenze ha avvio dopo che i ventilatori hanno raggiunto la massima velocità.

Fig 12 - Dinamica delle resistenze e dei ventilatori

In Fig 12 - a pag. 49 sono indicati, mediante dei tag (lettere maiuscole), i parametri di riferimento per resistenze e ventilatori. Fare riferimento alla seguente tabella per la corrispondenza tra tag e parametri.

| Tag | Parametri |
| --- | --- |
| A | Status_FanSupply Status_FanReturn |
| B | Fan_NominalSpeed |
| C | Fan_LowSpeed |
| D | Fan_PowerUp1_Time |
| E | Fan_PowerUp2_Time |

Tabella 38 - Dinamica delle resistenze e dei ventilatori

La funzione di pre-heating dei ventilatori viene attivata se sono contemporaneamente soddisfatte le seguenti condizioni:

attivazione del riscaldamento con valvola modulante;

temperatura esterna inferiore al parametro Fan_PreHeatOnSet;

disattivazione della messa a regime all'accensione.

NOTA: Se sono contemporaneamente soddisfatte le precedenti condizioni, i ventilatori vengono accesi con un ulteriore ritardo di Fan_PreHeating_Time rispetto all’apertura delle serrande esterne.

All’accensione dell'UTA i ventilatori vengono mantenuti spenti per un tempo pari al parametro Fan_PreHeating_Time per limitare di veicolare aria troppo fredda nella valvola.

Ventilatori ON/OFF

I ventilatori ON/OFF si accendono/spengono quando l'UTA si trova in stato ON/OFF. Dopo l'accensione, il ventilatore si porta a velocità costante.

L'accensione e lo spegnimento dei ventilatori sono attuati mediante un relè.

Ventilatori modulanti (con inverter)

Con ventilatori modulanti (con inverter) vengono utilizzate:

l'uscita digitale (relè), per il consenso inverter;

l'uscita analogica, per modulare la velocità.

NOTA: È possibile impostare una regolazione ventilatori a velocità costante anche per tipologia ventilatori modulanti mediante un'opportuna configurazione delle percentuali di ripresa e di mandata.

La gestione dei ventilatori modulanti è descritta nella seguente tabella.

| Gestione dei ventilatori modulanti | Modalità di gestione |
| --- | --- |
| Manuale (da controllore) | Mediante impostazione di una percentuale fissa per ciascun ventilatore |
| Automatica | Mediante richiesta dalla sonda CO2/sonda VOC |
| Automatica | Mediante sensori di pressione (fino a due) |

Tabella 39 - Gestione dei ventilatori modulanti

La gestione dei ventilatori modulanti tramite sensori di pressione può essere eseguita:

mediante regolazione in parallelo del sensore di pressione di mandata e del sensore di pressione di ripresa, con un offset di differenza tra i due sensori per bilanciare i flussi;

mediante una sonda di pressione dedicata per ciascun ventilatore.

In caso di sbrinamento recuperatore mediante riduzione della velocità del ventilatore mandata, la velocità del ventilatore mandata dipende anche dal regolatore che esegue lo sbrinamento recuperatore.

Ventilatori di backup

Ciascun ventilatore di backup ha il medesimo flusso di aria del corrispondente ventilatore principale.

La gestione dello swap (o inversione) tra ventilatori con backup è eseguita mediante il parametro Fan_SwapPolicy, in funzione del quale vengono selezionati i ventilatori mandata e i ventilatori ripresa da avviare, come descritto nella seguente tabella.

| Parametro Fan_SwapPolicy | Gestione dello swap tra ventilatori |
| --- | --- |
| 0 | Viene avviata la coppia di ventilatori principali (se entrambi attivi) |
| 1 | Viene avviata la coppia di ventilatori (principali o backup) che ha il minor numero di ore totali di funzionamento |
| 2 | Viene avviata la coppia di ventilatori (mandata o ripresa) che ha il minor numero di ore totali di funzionamento |
| 3 | Viene avviata la coppia di ventilatori (principali o backup) con la ventola che singolarmente ha il minor numero di ore di funzionamento |

Tabella 40 - Gestione dello swap tra ventilatori

In caso di allarmi attivi relativi alla coppia di:

ventilatori principali, all’avvio vengono selezionati i ventilatori di backup;

ventilatori di backup, all’avvio vengono selezionati i ventilatori principali.

In assenza di alcun allarme attivo relativo a ventilatori, viene eseguita periodicamente la rotazione dei ventilatori con periodicità pari al parametro Fan_Swap_Time ore (se diverso da 0) tra ventilatori principali e ventilatori di backup.

Ventilatori Modbus

I ventilatori Modbus sono pilotati da controllore mediante la porta seriale RS485-2 con la seguente configurazione: 19.2 E,8,1.

La tipologia di ventilatori Modbus supportata nell'UTA è:

EBM Papst;

ATV212;

Ziehl EC blue.

I relativi indirizzi slave Modbus per ciascun ventilatore nell'UTA sono riportati nella seguente tabella.

| Ventilatore | Indirizzo Modbus |
| --- | --- |
| Mandata principale | 2 |
| Ripresa principale | 3 |
| Mandata di backup | 4 |
| Ripresa di backup | 5 |
| Secondo Mandata (solo modello Ziehl) | 10 |
| Secondo Ripresa (solo modello Ziehl) | 11 |
| Secondo Mandata backup (solo modello Ziehl) | 12 |
| Secondo Ripresa backup (solo modello Ziehl) | 13 |
| Terzo Mandata (solo modello Ziehl) | 14 |
| Terzo Ripresa (solo modello Ziehl) | 15 |
| Terzo Mandata backup (solo modello Ziehl) | 16 |
| Terzo Ripresa backup (solo modello Ziehl) | 17 |

Tabella 41 - Ventilatori Modbus e relativi indirizzi

Per i ventilatori Modbus di tipologia EBM Papst fare riferimento a 3.13.4.1 Ventilatori Modbus di tipologia EBM Papst a pag. 52.

Per i ventilatori Modbus di tipologia Ziehl EC blue fare riferimento a 3.13.4.2 Ventilatori Modbus di tipologia Ziehl EC blue a pag. 52.

Per i ventilatori Modbus di tipologia ATV212 fare riferimento a 3.13.4.3 Ventilatori Modbus di tipologia ATV212 a pag. 52.

Ventilatori Modbus di tipologia EBM Papst

I valori dei registri relativi a ventilatore Modbus di tipologia EBM Papst sono riportati nella seguente tabella.

| Nome | Registro | Valore | Nota |
| --- | --- | --- | --- |
| Source set value | D101 | 1 | This parameter specifies the source from which the set value is taken: 1=RS485 (specified set value parameter D001) |
| Store Set Value | D103 | 0 | This parameter specifies whether or not an incoming specified set value (D001) is also stored in the EEPROM under set value (EEPROM) (D114 / D115): 0=Set value is not stored. The fan is stationary after a reset |
| Control Mode Day | D106-D017 | 2 | The external "Day/night" input and the "Day/night internal" parameter are used to select whether the value in "Control mode day" or "Control mode night" is applicable: 2=open loop PWM control. |
| Motor Stop Enable | D112 D113 | 1 | The external "Day/night" input and the "Day/night internal" parameter are used to select whether the value in "Motor stop enable day" or "Motor stop enable night" is applicable: 1=Motor stops if set value = 0 |

Tabella 42 - Valori dei registri relativi a ventilatore Modbus di tipologia EBM Papst

NOTA: Per ulteriori informazioni fare riferimento al manuale EBM Papst.

Ventilatori Modbus di tipologia Ziehl EC blue

I valori dei registri relativi a ventilatore Modbus di tipologia Ziehl EC blue sono riportati nella seguente tabella.

| Nome | Registro | Valore | Nota |
| --- | --- | --- | --- |
| Controlmode | 4 bit 0 | 2 | Speed control register h2 (fractional 0 - 32767 = 0 - 100 %) with possibility for switch over to Set Intern 2,3 |
| D1 Function (digital input) | 14 | 0 | Off |

Tabella 43 - Valori dei registri relativi a ventilatore Modbus di tipologia Ziehl EC blue

NOTA: Per ulteriori informazioni fare riferimento al manuale Ziehl EC blue.

Ventilatori Modbus di tipologia ATV212

I valori dei registri relativi a ventilatore Modbus di tipologia ATV212 sono riportati nella seguente tabella.

| Nome | Registro | Valore | Nota |
| --- | --- | --- | --- |
| CMOD | 3+1 | 2 | The setting of parameter CMOd determines the source of start, stop, forward, and reverse operation commands when the drive is in remote mode. The drive needs to be stopped to make changes to parameter CMOd. |
| FMOD | 4+1 | 4 | The setting of parameter FMOd determines the source of the drive’s speed reference when the drive is in remote mode. The drive needs to be stopped to make changes to parameter FMOd. |
| Timeout | 2051+1 | 10 | WARNING LOSS OF CONTROL - If F803 is set to 0, communication control will be inhibited. - For safety reasons, inhibiting the communication interruption detection should be restricted to the debug phase or to special applications. Failure to follow these instructions can result in death, serious injury, or equipment damage. 0= Communication error detection disabled 1 to 100=1 to 100 seconds |
| F732 | 1842+1 | 1 | Use parameter F732 to enable or disable the LOC/REM key on the drive embedded display terminal. If the LOC/REM key is disabled, switching between local and remote mode can be achieved with parameters [Frequency mode sel] (FMOd) and [Command mode sel] (CMOd). |

Tabella 44 - Valori dei registri relativi a ventilatore Modbus di tipologia ATV212

NOTA: Per ulteriori informazioni fare riferimento al manuale ATV212.

Qualità aria: sonda CO2 e sonda VOC

In caso di rilevazione di qualità dell'aria scarsa da parte di una sonda CO2 e/o di una sonda VOC, la regolazione aumenta la velocità dei ventilatori. In questo caso si ha un incremento della portata dell’aria in ingresso per aumentare la concentrazione di ossigeno.

È possibile abilitare la funzione di controllo qualità aria solo se una delle seguenti condizioni è verificata:

la serranda di miscela è presente;

il ventilatore è modulante.

La regolazione del controllo qualità aria può essere:

P, oppure

PI.

NOTA: In caso di attivazione sia della sonda CO2 sia della sonda VOC, la richiesta attiva risulta la maggiore tra le due.

Dopo aver definito la tipologia della sonda, è necessario definire i seguenti parametri relativi alla regolazione:

setpoint, in caso di regolatore P o PI;

differenziale, in caso di regolatore P o PI;

tempo integrale, in caso di regolatore PI.

Il regolatore della qualità aria è un regolatore in cascata; esso agisce nell'ordine, in funzione della richiesta:

- incrementando l'uscita delle serrande esterne modulanti (1 -Fig 13);

NOTA: È necessario impostare l'apertura minima delle serrande.

sui ventilatori modulanti (2 - -Fig 13), come descritto a seguire:

se i ventilatori sono regolati in pressione, incrementando il setpoint di pressione;

se i ventilatori sono a velocità fissa, incrementando la velocità (tra il valore minimo e il valore massimo ammesso per i ventilatori).

NOTA: La richiesta di regolazione sulla sonda VOC è prioritaria rispetto alla richiesta di regolazione sulle serrande esterne ON/OFF + miscela 0-10 V.

NOTA: In profilo night la velocità dei ventilatori è prioritaria.

Fig 13 - Regolatore della qualità aria

Regolazione a portata costante

Questa regolazione prevede un regolatore PID per limitare variazioni repentine nella reazione del ventilatore.

La regolazione a portata costante si ottiene mediante un sensore di pressione differenziale collegato alla parte aspirante del ventilatore.

In caso di diminuzione della portata dovuta a un aumento della resistenza aeraulica (filtro che progressivamente si intasa), la logica di funzionamento è la seguente:

- il controllore rileva una diminuzione della pressione mediante il sensore di pressione;

il controllore aumenta il valore dell'uscita collegata al ventilatore;

il controllore aumenta la velocità del ventilatore fino a raggiungere il setpoint impostato.

NOTA: Per le regolazioni a portata costante è richiesta una taratura della pressione o della portata mediante l'utilizzo di due ingressi opzionali.

Regolazione a pressione costante

Questa regolazione prevede un regolatore PID per limitare variazioni repentine nella reazione del ventilatore.

La regolazione a pressione costante si ottiene mediante un sensore di pressione differenziale collegato sul canale di mandata o sul canale di ripresa e rileva lo scostamento della pressione rispetto alla pressione atmosferica.

NOTA: La regolazione a pressione costante solitamente viene eseguita se il flusso di mandata è canalizzato su più ambienti caratterizzati dalla medesima esigenza di ventilazione ma non utilizzati contemporaneamenti.

La logica di regolazione è la seguente:

- il controllore stabilisce automaticamente il setpoint di pressione;

il controllore confronta il setpoint di pressione con il valore acquisito dal sensore di pressione differenziale;

tramite questa differenza la velocità del ventilatore viene aumentata o diminuita fino a raggiungere il setpoint di pressione.

Test output

Il test output è una funzione che consente di testare le uscite digitali e analogiche forzandole a un valore dato, con sicurezze sempre attive.

NOTA: Il test output è possibile sia da controllore sia da menu (fare riferimento al parametro EnableTestOutput).

Nella seguente tabella sono riportate le limitazioni in funzione del test output realizzato.

In caso di allarmi bloccanti, la modalità di test viene disabilitata automaticamente.

| Test output | Limitazione |
| --- | --- |
| Accensione ventilatori | Non ammessa in caso di serrande chiuse |
| Accensione resistenze | - Non ammessa in caso di ventilatori spenti - Non superiore a 5 minuti |

Tabella 45 - Limitazioni

Menu Impostazioni Utente

Le pagine del "Menu Impostazioni Utente" sono dinamiche e alcune di esse sono visibili solo se le relative funzionalità sono presenti.

Nella seguente tabella è riportato l'elenco dei menu a cui si può accedere dal “Menu Impostazioni Utente”.

| Menu | Utente | Installatore | Riferimento nel presente Manuale |
| --- | --- | --- | --- |
| A-Unit | SI | SI | 4.1 A-Unit a pag. 56 |
| B-Clock & Events | SI | SI | 4.2 B-Clock & Events a pag. 58 |
| C-Languages | SI | SI | 4.3 C-Languages a pag. 66 |
| D-Alarms | SI | SI | 4.4 D-Alarms a pag. 66 |
| E-User Settings | SI | SI | 4.5 E-User Settings a pag. 71 |
| F-I/O | SI | SI | 4.6 F-I/O a pag. 75 |
| G-Password | SI | SI | 4.7 G-Password a pag. 78 |
| H-System | NO | SI | 4.8 H-System a pag. 79 |

Tabella 46 - Menu a cui si può accedere dal “Menu Impostazioni Utente”

NOTA: A seguire sono riportate le pagine che vengono visualizzate a display:

in caso di valori fuori range;

come messaggio di conferma.

| Valori fuori range |  |  |
| --- | --- | --- |
| Messaggi di conferma |  |  |

A-Unit

A seguire viene riportata la navigazione del menu “A-Unit”, che consente la gestione dei parametri principali.

I parametri del menu "A-Unit" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| - - - | Status_PlantMode | 0=Cool; 1=Heat; | — | Unit Working Mode |
| - - - | T_CurrentSetpointByPar | Signed 16-bit | °C | Current Setpoint by parameter based on selected mode |
| - - - | T_RegulationProbe | Signed 16-bit | °C | Temperature Regulation Probe |
| - - - | T_CurrentSupplySetpoint | Signed 16-bit | °C | Current Supply Setpoint |
| - - - | AI_LogicIndex_0 | Signed 16-bit | °C | Supply Temperature |
| - - - | Status_OutPost | Signed 16-bit | % | Post Heating Output |
| - - - | Status_OutHeat | Signed 16-bit | % | Heating Output |
| - - - | Status_OutRec | Signed 16-bit | % | Recovery Output |
| - - - | Status_OutCool | Signed 16-bit | % | Cooling Output |
| - - - | Status_PID_TSupplyHeat | Signed 16-bit | % | Heating Regulator Request |
| - - - | Status_PID_TSupplyCool | Signed 16-bit | % | Cooling Regulator Request |
| - - - | Status_LowTempSupplyLimit | Signed 16-bit | % | Low Supply Limit Regulator Request |
| - - - | Status_HighTempSupplyLimit | Signed 16-bit | % | High Supply Limit Regulator Request |
| - - - | Status_HighTempPreHeatLimit | Signed 16-bit | % | High Preheater Limit Regulator Request |
| - - - | Pr_CurrentSupplySetpoint | Signed 32-bit | Pa-m3/h | Current Fan Supply Setpoint - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_CurrentReturnSetpoint | Signed 32-bit | Pa-m3/h | Current Fan Return Setpoint - Units depends on Fan_Return_Pressure_Flow |
| - - - | Pr_Flow_Supply | Signed 32-bit | Pa-m3/h | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_Flow_Return | Signed 32-bit | Pa-m3/h | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| - - - | Pr_Flow_Supply | Signed 32-bit | Pa-m3/h | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| - - - | Pr_Flow_Return | Signed 32-bit | Pa-m3/h | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| - - - | Status_PID_PrSupply | Signed 16-bit | % | Supply Fan Regulator Request |
| - - - | Status_PID_PrReturn | Signed 16-bit | % | Return Fan Regulator Request |
| - - - | Status_FanSupply | Signed 16-bit | % | Fan Supply Speed |
| - - - | Status_FanReturn | Signed 16-bit | % | Fan Return Speed |
| - - - | Status_DefrostFan | Boolean | — | Defrost with Fan Status |
| - - - | Status_DefrostFanRed | Signed 16-bit | % | Defrost Supply Fan Speed Reduction |
| - - - | RH_CurrentSetpoint | Signed 16-bit | %R.H. | Current Return Setpoint |
| - - - | T_DewPointSetPoint | Signed 16-bit | °C | Current Dewpoint Setpoint |
| - - - | AI_LogicIndex_5 | Signed 16-bit | °C | Saturation Temperature |
| - - - | RH_RegulationProbe | Signed 16-bit | %R.H. | Humdity Regulation Probe |
| - - - | Status_PID_Humid | Signed 16-bit | % | Hmidification Regulator Request |
| - - - | Status_PID_DeHumid | Signed 16-bit | % | Dehumidification Regulator Request |
| - - - | Status_OutHum | Signed 16-bit | % | Humidifier Output |
| - - - | Status_ExtSHum | Signed 16-bit | g/Kg | External Specific Humidity |
| - - - | Status_RetSHum | Signed 16-bit | g/Kg | Return Specific Humidity |
| - - - | Status_HighHumSupplyLimit | Signed 16-bit | % | High Humidity Limit Regulator Request |
| - - - | AirQ_RegulationProbe | Signed 16-bit | %/ppm | Air Quality Regulation Probe |
| - - - | AirQ_CurrentSetpointVOC | Signed 16-bit | % | Current Setpoint VOC |
| - - - | AirQ_CurrentSetpointCO2 | Signed 16-bit | ppm | Current Setpoint CO2 |
| - - - | Status_PID_AirQ | Signed 16-bit | % | Air Quality Regulator Request |
| - - - | AI_LogicIndex_2 | Signed 16-bit | °C | External Temperature |
| - - - | Status_ExtDamper | Signed 16-bit | % | External Damper Status |
| - - - | Status_RecoveryCooling | Boolean | — | Cooling Recovery Status |
| - - - | Status_RecoveryHeating | Boolean | — | Heating Recovery Status |
| - - - | Status_FreeCooling | Boolean | — | Free Cooling Status |
| - - - | Status_FreeHeating | Boolean | — | Free Heating Status |
| - - - | Status_ActuatorsOffbyFCH | Boolean | — | Actuators off by Free Cooling/Heating |
| - - - | Status_FCHreq | Signed 16-bit | % | Free Cooling/Heating Request |
| - - - | Status_DefrostDamper | Boolean | — | Defrost with Damper Status |
| - - - | PreHeaterSetpoint | Signed 16-bit | °C | Setpoint Pre Heating |
| - - - | AI_LogicIndex_4 | Signed 16-bit | °C | Preheating Temp, |
| - - - | Status_OutPre | Signed 16-bit | % | Preheating Output |
| - - - | RecoveryDefrost_SetMaxReq | Signed 16-bit | °C | Recovery Defrost: Setpoint Expulsion Temperature |
| - - - | AI_LogicIndex_3 | Signed 16-bit | °C | Expulsion Temperature |
| - - - | Status_DefrostPreHeat | Boolean | — | Defrost with Preheating Status |

Tabella 47 - A-Unit

B-Clock & Events

A seguire viene riportata la navigazione del menu "B-Clock & Events", che consente la gestione di fasce orarie ed eventi.

|  |  | Clock |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "B1-Clock" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | sysClock_seconds_WR | Unsigned 8-bit | 0 | 0 | 59 | Second value to update |
| - - - | sysClock_minutes_WR | Unsigned 8-bit | 0 | 0 | 59 | Minute value to update |
| - - - | sysClock_hours_WR | Unsigned 8-bit | 0 | 0 | 23 | Hour value to update |
| - - - | sysClock_dayweek_WR | Unsigned 8-bit | 0 | 0 | 6 | Day of the week value to update |
| - - - | sysClock_daymonth_WR | Unsigned 8-bit | 1 | 1 | 31 | Day of the month value to update |
| - - - | sysClock_month_WR | Unsigned 8-bit | 1 | 1 | 12 | Month value to update |
| - - - | sysClock_year_WR | Unsigned 8-bit | 10 | 10 | 99 | Year value to update |
| - - - | sysClock_update | 0=Current; 1=Update; 2=Modify | 0 | 0 | 2 | Confirm update |
| - - - | DayLight_Region | 0=Europe; 1=USA/Canada | 0 | 0 | 1 | Day Light Region |
| - - - | DayLight_Enable | Boolean | 1 | — | — | Day Light Enable |

Tabella 48 - B1-Clock

|  |  | Day Event |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Profile P1 |  |  |  |
|  |  |  |  | Profile P2 |  |  |  |
|  |  |  |  | Days |  |  |  |

Il parametro del menu "B2-Day Event" è riportati nella seguente tabella.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE00_TimeBandEnable | Boolean | 0 | — | — | Time events Enable |

I parametri del menu "B21-Profile P1" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE10_TimeProfile1Event1 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #1 of profile #1 |
| - - - | tE11_ModeProfile1Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #1 of profile #1 |
| - - - | tE12_TimeProfile1Event2 | Signed 16-bit | 12:00 | 00:00 | 23:59 | Time of event #2 of profile #1 |
| - - - | tE13_ModeProfile1Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #2 of profile #1 |
| - - - | tE14_TimeProfile1Event3 | Signed 16-bit | 14:00 | 00:00 | 23:59 | Time of event #3 of profile #1 |
| - - - | tE15_ModeProfile1Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #3 of profile #1 |
| - - - | tE16_TimeProfile1Event4 | Signed 16-bit | 18:00 | 00:00 | 23:59 | Time of event #4 of profile #1 |
| - - - | tE17_ModeProfile1Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #4 of profile #1 |

Tabella 49 - B21-Profile P1

I parametri del menu "B22-Profile P2" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | tE20_TimeProfile2Event1 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #1 of profile #2 |
| - - - | tE21_ModeProfile2Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #1 of profile #2 |
| - - - | tE22_TimeProfile2Event2 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #2 of profile #2 |
| - - - | tE23_ModeProfile2Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #2 of profile #2 |
| - - - | tE24_TimeProfile2Event3 | Signed 16-bit | 08:00 | 00:00 | 23:59 | Time of event #3 of profile #2 |
| - - - | tE25_ModeProfile2Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #3 of profile #2 |
| - - - | tE26_TimeProfile2Event4 | Signed 16-bit | 18:00 | 00:00 | 23:59 | Time of event #4 of profile #2 |
| - - - | tE27_ModeProfile2Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | Mode of event #4 of profile #2 |

Tabella 50 - B22-Profile P2

I parametri del menu "B23-Days" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/2 | tE01_TimeProfileMonday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Monday |
| 1/2 | tE02_TimeProfileTuesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Tuesday |
| 1/2 | tE03_TimeProfileWednesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Wednesday |
| 1/2 | tE04_TimeProfileThursday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Thursday |
| 2/2 | tE05_TimeProfileFriday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Friday |
| 2/2 | tE06_TimeProfileSaturday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Saturday |
| 2/2 | tE07_TimeProfileSunday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | Time events profile on Sunday |

Tabella 51 - B23-Days

|  |  | Year Event |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "B3-Year Event" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device Type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | TW00_EnableYearEvents | Boolean | 0 | — | — | — | Enable year events |
| 1/15 | TW01_EventProfile01 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 1 |
| 1/15 | TW16_EnEvent01 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 1 |
| 1/15 | TW31_EventDDStart01 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 1 |
| 1/15 | TW46_EventMMStart01 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 1 |
| 1/15 | TW61_EventDDStop01 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 1 |
| 1/15 | TW76_EventMMStop01 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 1 |
| 2/15 | TW02_EventProfile02 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 2 |
| 2/15 | TW17_EnEvent02 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 2 |
| 2/15 | TW32_EventDDStart02 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 2 |
| 2/15 | TW47_EventMMStart02 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 2 |
| 2/15 | TW62_EventDDStop02 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 2 |
| 2/15 | TW77_EventMMStop02 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 2 |
| 3/15 | TW03_EventProfile03 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 2 |
| 3/15 | TW18_EnEvent03 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 3 |
| 3/15 | TW33_EventDDStart03 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 3 |
| 3/15 | TW48_EventMMStart03 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 3 |
| 3/15 | TW63_EventDDStop03 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 3 |
| 3/15 | TW78_EventMMStop03 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 3 |
| 4/15 | TW04_EventProfile04 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 4 |
| 4/15 | TW19_EnEvent04 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 4 |
| 4/15 | TW34_EventDDStart04 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 4 |
| 4/15 | TW49_EventMMStart04 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 4 |
| 4/15 | TW64_EventDDStop04 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 4 |
| 4/15 | TW79_EventMMStop04 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 4 |
| 5/15 | TW05_EventProfile05 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 5 |
| 5/15 | TW20_EnEvent05 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 5 |
| 5/15 | TW35_EventDDStart05 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 5 |
| 5/15 | TW50_EventMMStart05 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 5 |
| 5/15 | TW65_EventDDStop05 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 5 |
| 5/15 | TW80_EventMMStop05 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 5 |
| 6/15 | TW06_EventProfile06 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 6 |
| 6/15 | TW21_EnEvent06 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 6 |
| 6/15 | TW36_EventDDStart06 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 6 |
| 6/15 | TW51_EventMMStart06 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 6 |
| 6/15 | TW66_EventDDStop06 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 6 |
| 6/15 | TW81_EventMMStop06 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 6 |
| 7/15 | TW07_EventProfile07 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 7 |
| 7/15 | TW22_EnEvent07 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 7 |
| 7/15 | TW37_EventDDStart07 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 7 |
| 7/15 | TW52_EventMMStart07 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 7 |
| 7/15 | TW67_EventDDStop07 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 7 |
| 7/15 | TW82_EventMMStop07 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 7 |
| 8/15 | TW08_EventProfile08 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 8 |
| 8/15 | TW23_EnEvent08 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 8 |
| 8/15 | TW38_EventDDStart08 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 8 |
| 8/15 | TW53_EventMMStart08 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 8 |
| 8/15 | TW68_EventDDStop08 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 8 |
| 8/15 | TW83_EventMMStop08 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 8 |
| 9/15 | TW09_EventProfile09 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 9 |
| 9/15 | TW24_EnEvent09 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 9 |
| 9/15 | TW39_EventDDStart09 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 9 |
| 9/15 | TW54_EventMMStart09 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 9 |
| 9/15 | TW69_EventDDStop09 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 9 |
| 9/15 | TW84_EventMMStop09 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 9 |
| 10/15 | TW10_EventProfile10 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 10 |
| 10/15 | TW25_EnEvent10 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 10 |
| 10/15 | TW40_EventDDStart10 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 10 |
| 10/15 | TW55_EventMMStart10 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 10 |
| 10/15 | TW70_EventDDStop10 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 10 |
| 10/15 | TW85_EventMMStop10 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 10 |
| 11/15 | TW11_EventProfile11 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 11 |
| 11/15 | TW26_EnEvent11 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 11 |
| 11/15 | TW41_EventDDStart11 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 11 |
| 11/15 | TW56_EventMMStart11 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 11 |
| 11/15 | TW71_EventDDStop11 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 11 |
| 11/15 | TW86_EventMMStop11 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 11 |
| 12/15 | TW12_EventProfile12 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 12 |
| 12/15 | TW27_EnEvent12 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 12 |
| 12/15 | TW42_EventDDStart12 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 12 |
| 12/15 | TW57_EventMMStart12 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 12 |
| 12/15 | TW72_EventDDStop12 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 12 |
| 12/15 | TW87_EventMMStop12 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 12 |
| 13/15 | TW13_EventProfile13 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 13 |
| 13/15 | TW28_EnEvent13 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 13 |
| 13/15 | TW43_EventDDStart13 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 13 |
| 13/15 | TW58_EventMMStart13 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 13 |
| 13/15 | TW73_EventDDStop13 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 13 |
| 13/15 | TW88_EventMMStop13 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 13 |
| 14/15 | TW14_EventProfile14 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 14 |
| 14/15 | TW29_EnEvent14 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 14 |
| 14/15 | TW44_EventDDStart14 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 14 |
| 14/15 | TW59_EventMMStart14 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 14 |
| 14/15 | TW74_EventDDStop14 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 14 |
| 14/15 | TW89_EventMMStop14 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 14 |
| 15/15 | TW15_EventProfile15 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | Year events profile 15 |
| 15/15 | TW30_EnEvent15 | 0 = Off; 1 = On | 0 | 0 | 1 | — | Enable Year events 15 |
| 15/15 | TW45_EventDDStart15 | Unsigned 8-bit | 1 | 1 | 31 | Day | Start Day Year events 15 |
| 15/15 | TW60_EventMMStart15 | Unsigned 8-bit | 1 | 1 | 12 | Month | Start Month Year events 15 |
| 15/15 | TW75_EventDDStop15 | Unsigned 8-bit | 1 | 1 | 31 | Day | Stop Day Year events 15 |
| 15/15 | TW90_EventMMStop15 | Unsigned 8-bit | 1 | 1 | 12 | Month | Stop Month Year events 15 |

Tabella 52 - B3-Year Event

C-Languages

A seguire viene riportata la navigazione del menu "C-Languages", che consente la selezione della lingua.

La lingua del display remoto è allineata all’accensione e periodicamente a quella del display locale.

Una modifica della lingua del display remoto è applicata automaticamente anche al display locale.

D-Alarms

A seguire viene riportata la navigazione del menu "D-Alarms", che consente la gestione degli allarmi.

|  |  | Active |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

Gli allarmi del menu "D1-Alarms" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Description |
| --- | --- | --- | --- |
| - - - | Alxx_Reset | Boolean | Alarm reset request command via Modbus |
| - - - | Al01_SupplyProbe | 0=Not Active; 1=Active; 2=Manual Reset | Al01-Supply Temperature Probe Error |
| - - - | Al02_ReturnProbe | See Al01_SupplyProbe | A02-Return Temperature Probe Error |
| - - - | Al03_ExternalProbe | See Al01_SupplyProbe | A03-External Temperature Probe Error |
| - - - | Al04_ExpulsionProbe | See Al01_SupplyProbe | A04-Expulsion Temperature Probe Error |
| - - - | Al05_PreHeatingProbe | See Al01_SupplyProbe | A05-Preheating Temperature Probe Error |
| - - - | Al06_SaturationProbe | See Al01_SupplyProbe | A06-Saturation Temperature Probe Error |
| - - - | Al07_AntifreezeProbe | See Al01_SupplyProbe | A07-Antifreeze Temperature Probe Error |
| - - - | Al08_AirQualityProbe_CO2 | See Al01_SupplyProbe | A08-CO2 Probe Error |
| - - - | Al09_SupplyPressureProbe | See Al01_SupplyProbe | A09-Supply Pressure Probe Error |
| - - - | Al10_ReturnPressureProbe | See Al01_SupplyProbe | A10-Return Pressure Probe Error |
| - - - | Al11_SupplyHumidityProbe | See Al01_SupplyProbe | A11-Hum. Supply Probe Error |
| - - - | Al12_ReturnHumidityProbe | See Al01_SupplyProbe | A12-Hum. Return Probe Error |
| - - - | Al13_AirQualityProbe_VOC | See Al01_SupplyProbe | A13-VOC Probe Error |
| - - - | Al14_ExternalHumidityProbe | See Al01_SupplyProbe | A14-Hum. External Probe Error |
| - - - | Al26_SensAirFlowSupply | See Al01_SupplyProbe | A26-Supply Airflow by Probe |
| - - - | Al27_SensAirFlowReturn | See Al01_SupplyProbe | A27-Return Airflow by Probe |
| - - - | Al28_SensAirFlowSupplyBck | See Al01_SupplyProbe | A28-Airflow Prb Sup.2 |
| - - - | Al29_SensAirFlowReturnBck | See Al01_SupplyProbe | A29-Airflow Prb Ret.2 |
| - - - | Al30_FanThermalSupply | See Al01_SupplyProbe | A30-Fan Supply |
| - - - | Al31_FanThermalReturn | See Al01_SupplyProbe | A31-Fan Return |
| - - - | Al32_Fire | See Al01_SupplyProbe | A32-Fire |
| - - - | Al33_Door | See Al01_SupplyProbe | A33-Door |
| - - - | Al34_Antifreeze | See Al01_SupplyProbe | A34-Antifreeze |
| - - - | Al35_AirFlowSupply | See Al01_SupplyProbe | A35-Airflow Supply |
| - - - | Al36_AirFlowReturn | See Al01_SupplyProbe | A36-Airflow Return |
| - - - | Al37_Humidifier | See Al01_SupplyProbe | A37-Humidifier |
| - - - | Al38_PreHeater | See Al01_SupplyProbe | A38-Preheater |
| - - - | Al39_Heater | See Al01_SupplyProbe | A39-Heater |
| - - - | Al40_PostHeater | See Al01_SupplyProbe | A40-Postheater |
| - - - | Al41_RotaryWheel | See Al01_SupplyProbe | A41-Recovery |
| - - - | Al42_Filter1 | See Al01_SupplyProbe | A42-Filter 1 |
| - - - | Al43_Filter2 | See Al01_SupplyProbe | A43-Filter 2 |
| - - - | Al44_Filter3 | See Al01_SupplyProbe | A44-Filter 3 |
| - - - | Al45_Filter4 | See Al01_SupplyProbe | A45-Filter 4 |
| - - - | Al46_FanThermalSupplyBck | See Al01_SupplyProbe | A46-Fan Supply 2 |
| - - - | Al47_FanThermalReturnBck | See Al01_SupplyProbe | A47-Fan Return 2 |
| - - - | Al48_AirFlowSupplyBck | See Al01_SupplyProbe | A48-Airflow Supply 2 |
| - - - | Al49_AirFlowReturnBck | See Al01_SupplyProbe | A49-Airflow Return 2 |
| - - - | Al50_CondUnit | See Al01_SupplyProbe | A50-Cond. Unit |
| - - - | Al51_RTC | See Al01_SupplyProbe | A51-Real Time Clock |
| - - - | Al52_FanMaintenance | See Al01_SupplyProbe | A52-Fan Maintenance |
| - - - | Al53_ModbusFanCfg | See Al01_SupplyProbe | A53-Modbus Fan Config. Timeout |
| - - - | Al54_FanSupplyCom | See Al01_SupplyProbe | A54-Modbus Fan Supply Communication |
| - - - | Al55_FanReturnCom | See Al01_SupplyProbe | A55-Modbus Fan Return Communication |
| - - - | Al56_FanSupplyBckCom | See Al01_SupplyProbe | A56-Modbus Fan Supply 2 Communication |
| - - - | Al57_FanReturnBckCom | See Al01_SupplyProbe | A57-Modbus Fan Return 2 Communication |
| - - - | Al58_Filter5 | See Al01_SupplyProbe | A58-Filter 5 |
| - - - | Al60_LogError | See Al01_SupplyProbe | A60-Log Error |
| - - - | Al61_Exp1 | See Al01_SupplyProbe | A61-Can Expansion 1 |
| - - - | Al62_Exp2 | See Al01_SupplyProbe | A62-Can Expansion 2 |
| - - - | Al66_CondUnit2 | See Al01_SupplyProbe | A66-Cond. Unit 2 |
| - - - | Al67_CondUnit3 | See Al01_SupplyProbe | A67-Cond. Unit 3 |
| - - - | Al68_CondUnit4 | See Al01_SupplyProbe | A68-Cond. Unit 4 |
| - - - | Al99_FanSupply_1b_Com | See Al01_SupplyProbe | Al99-Fan Supply 1b Com Alarm |
| - - - | Al100_FanSupply_1c_Com | See Al01_SupplyProbe | Al100-Fan Supply 1c Com Alarm |
| - - - | Al101_FanReturn_1b_Com | See Al01_SupplyProbe | Al101-Fan Return 1b Com Alarm |
| - - - | Al102_FanReturn_1c_Com | See Al01_SupplyProbe | Al102-Fan Return 1c Com Alarm |
| - - - | Al103_FanSupply_2b_Com | See Al01_SupplyProbe | Al103-Fan Supply 2b Com Alarm |
| - - - | Al104_FanSupply_2c_Com | See Al01_SupplyProbe | Al104-Fan Supply 2c Com Alarm |
| - - - | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | Al105-Fan Return 2b Com Alarm |
| - - - | Al106_FanReturn_2c_Com | See Al01_SupplyProbe | Al106-Fan Return 2c Com Alarm |

Tabella 53 - D1-Alarms

|  |  | Historical |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

La pagina “D2- Historical” permette la visualizzazione degli ultimi 50 eventi legati agli allarmi.

I parametri del menu "D2-Historical" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | Historical_Value_Code | 0 = ---; 1 = A01-Supply Pr.; 2 = A02-Return Pr.; 3 = A03-External Pr.; 4 = A04-Expulsion Pr.; 5 = A05-Preheating Pr.; 6 = A06-Saturation Pr.; 7 = A07-Antifreeze Pr.; 8 = A08-CO2 Pr.; 9 = A09-Supply Press. Pr.; 10 = A10-Return Press. Pr.; 11 = A11-Hum. Supply Pr.; 12 = A12-Hum. Return Pr.; 13 = A13-VOC Pr.; 14 = A14-Hum. External Pr.; 26 = A26-Airflow Prb Sup.; 27 = A27-Airflow Prb Ret.; 28 = A28-Airflow Prb Sup.2; 29 = A29-Airflow Prb Ret.2; 30 = A30-Fan Supply; 31 = A31-Fan Return; 32 = A32-Fire; 33 = A33-Door; 34 = A34-Antifreeze; 35 = A35-Airflow Supply; 36 = A36-Airflow Return; 37 = A37-Humidifier; 38 = A38-Preheater; 39 = A39-Heater; 40 = A40-Postheater; 41 = A41-Recovery; 42 = A42-Filter 1; 43 = A43-Filter 2; 44 = A44-Filter 3; 45 = A45-Filter 4; 46 = A46-Fan Supply 2; 47 = A47-Fan Return 2; 48 = A48-Airflow Supply 2; 49 = A49-Airflow Return 2; 50 = A50-Cond. Unit; 51 = A51-Real Time Clock; 52 = A52-Fan Maintenance; 58 = A58-Filter 5 60 = A60-Log Error; 61 = A61-Can Expansion 1; 62 = A62-Can Expansion 2; | — | 0 | 106 | Historical: Alarm Code |
| - - - | Historical_Value_Code | 66 = A66-Cond. Unit 2 67 = A67-Cond. Unit 3 68 = A68-Cond. Unit 4 99 = A99-Fan Sup.1b Com. 100 = A100-Fan Sup.1c Com. 101 = A101-Fan Ret.1b Com. 102 = A102-Fan Ret.1c Com. 103 = A103-Fan Sup.2b Com. 104 = A104-Fan Sup.2c Com. 105 = A105-Fan Ret.2b Com. 106 = A106-Fan Ret.2c Com. | — | 0 | 106 | Historical: Alarm Code |
| - - - | Historical_Value_Date | Signed 16-bit | — | — | — | Historical: Alarm Date |
| - - - | Historical_Value_Time | Signed 16-bit | — | — | — | Historical: Alarm Time |
| - - - | Historical_Value_SecStatus | Signed 16-bit | — | — | — | Historical: Alarm Seconds and Status: 100x+seconds (x=0 restored, x=1 active, x=2 wait for reset) |
| - - - | Historical_Number_alarms | Signed 16-bit | — | — | — | Historical: Number of stored alarms |
| - - - | Historical_Reset | Boolean | 0 | — | — | Historical: Reset Request |

Tabella 54 - D2-Historical

E-User Settings

A seguire viene riportata la navigazione del menu "E-User Settings", che consente la gestione dei parametri utente.

E1-Setpoints

A seguire viene riportata la navigazione del menu "E1-Setpoints", che consente la gestione dei setpoint.

I parametri del menu "E1-Setpoints" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6 | SP_T_Cool_E2 | Signed 16-bit | 26.0 | SP_T_MIN | SP_T_MAX | °C | Setpoint Cooling |
| 1/6 | SP_T_CoolEco_E2 | Signed 16-bit | 28.0 | SP_T_Cool_E2 | SP_T_MAX | °C | Setpoint Cooling Economy |
| 2/6 | SP_T_Heat_E2 | Signed 16-bit | 20.0 | SP_T_MIN | SP_T_MAX | °C | Setpoint Heating |
| 2/6 | SP_T_HeatEco_E2 | Signed 16-bit | 18.0 | SP_T_MIN | SP_T_Heat_E2 | °C | Setpoint Heating Economy |
| 3/6 | SP_T_Auto_E2 | Signed 16-bit | 240 | SP_T_MIN | SP_T_MAX | °C | Setpoint Auto |
| 3/6 | DIFF_T_AutoEco | Signed 16-bit | 20 | 0 | — | °C | Differential Economy Mode - Half Band (AUTO) |
| 4/6 | SP_RH_DehumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Dehumidication setpoint (comfort) |
| 4/6 | SP_RH_DehumidificationSetpointEco_E2 | Signed 16-bit | 55 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Dehumidication setpoint (eco) |
| 5/6 | SP_RH_HumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Humidification setpoint (comfort) |
| 5/6 | SP_RH_HumidificationSetpointEco_E2 | Signed 16-bit | 45 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | Humidification setpoint (eco) |
| 6/6 | SP_CO2_E2 | Signed 16-bit | 800 | 0 | 2000 | ppm | CO2 Air quality setpoint |
| 6/6 | SP_VOC_E2 | Signed 16-bit | 40 | 0 | 100 | % | VOC Air quality setpoint |
| 6/6 | SP_CO2_E2 | Signed 16-bit | 800 | 0 | 2000 | ppm | CO2 Air quality setpoint |

Tabella 55 - E1-Setpoints

E2-Work Hours

A seguire viene riportata la navigazione del menu "E2-Work Hours", che consente la gestione dei periodi di operatività dei ventilatori.

Gli stati del menu "E2-Work Hours" sono riportati nella seguente tabella, suddivisi per pagina (gli elementi sono visibili se definiti nella configurazione corrente dell’unità).

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| 1/5 |  | Unit_DD | Unsigned 16-bit |  | days |  | Unit Working Days |  |
| 1/5 |  | Unit_HH | Unsigned 16-bit |  | hours |  | Unit Working Hours |  |
| 1/5 |  | FanSupply_DD | Unsigned 16-bit |  | days |  | Supply Fan Working Days |  |
| 1/5 |  | FanSupply_HH | Unsigned 16-bit |  | hours |  | Supply Fan Working Hours |  |
| 2/5 |  | FanSupplyBck_DD | Unsigned 16-bit |  | days |  | Supply Fan 2 Working Days |  |
| 2/5 |  | FanSupplyBck_HH | Unsigned 16-bit |  | hours |  | Supply Fan 2 Working Hours |  |
| 2/5 |  | FanReturn_DD | Unsigned 16-bit |  | days |  | Return Fan Working Days |  |
| 2/5 |  | FanReturn_HH | Unsigned 16-bit |  | hours |  | Return Fan Working Hours |  |
| 3/5 |  | FanReturnBck_DD | Unsigned 16-bit |  | days |  | Return Fan 2 Working Days |  |
| 3/5 |  | FanReturnBck_HH | Unsigned 16-bit |  | hours |  | Return Fan 2 Working Hours |  |
| 3/5 | CondUnit1_DD | Unsigned 16-bit | days | Condensing Unit 1 Working Days |
| 3/5 | CondUnit1_HH | Unsigned 16-bit | hours | Condensing Unit 1 Working Hours |
| 4/5 | CondUnit2_DD | Unsigned 16-bit | days | Condensing Unit 2 Working Days |
| 4/5 | CondUnit2_HH | Unsigned 16-bit | hours | Condensing Unit 2 Working Hours |
| 4/5 | CondUnit3_DD | Unsigned 16-bit | days | Condensing Unit 3 Working Days |
| 4/5 | CondUnit3_HH | Unsigned 16-bit | hours | Condensing Unit 3 Working Hours |
| 5/5 | CondUnit4_DD | Unsigned 16-bit | days | Condensing Unit 4 Working Days |
| 5/5 | CondUnit4_HH | Unsigned 16-bit | hours | Condensing Unit 4 Working Hours |

Tabella 56 - E2-Work Hours

E3-Data Logger

A seguire viene riportata la navigazione del menu "E3-Data Logger", che consente la gestione del data logger.

|  |  | Ok |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "E3-Data Logger" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | LogEnable | Boolean | 0 | — | — | Logger Enable |
| - - - | StartMonth | Unsigned 8-bit | 1 | 1 | 12 | Start Month - Log Period Export to USB |
| - - - | EndMonth | Unsigned 8-bit | 1 | 1 | 12 | End Month - Log Period Export to USB |
| - - - | StartYear | Unsigned 8-bit | 16 | 0 | 99 | Start Year - Log Period Export to USB |
| - - - | EndYear | Unsigned 8-bit | 16 | 0 | 99 | End Year - Log Period Export to USB |

Tabella 57 - E3-Data Logger

|  |  | microSD |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "E31-microSD Options" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | microSdStatus | 0=Not present; 1=Unsafe Removed; 2=Not Mounted; 3=Mounted | — | 0 | 3 | microSd Status |
| - - - | microSdError | Boolean | — | — | — | microSD Error |
| - - - | microSdInfo | 0=...; 1=Release SD; 2=Ready to remove/mount; 3=Ready for log; 4=...; 5=insert SD..; 6=Release SD; 7=Retry command..; 8=Yet mounted | — | 0 | 8 | microSd Info |
| - - - | microSDPresCount | Unsigned 16-bit | 0 | — | — | microSD Presence Counter |

Tabella 58 - E31-microSD Options

E4-Web Server

A seguire viene riportata la navigazione del menu "E4-Web Server", che consente la gestione dei parametri di accesso relativi al web server.

I parametri del menu "E4-Web Server" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| - - - | WEB_User_E2 | String | administrator | Web User ID |
| - - - | WEB_PSW_E2 | String | password | Web Psw ID |

Tabella 59 - E4-Web Server

E5-Regulator

A seguire viene riportata la navigazione del menu "E5-Regulator", che consente la gestione dei regolatori.

I parametri del menu "E5-Regulator" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6 | cfgFreeCooling | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | FreeCooling Enable |
| 1/7 | cfgFreeHeating | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | FreeHeating Enable |
| 2/7 | FreeCHMinExtTemp | Signed 16-bit | 12.0 | -20.0 | 20.0 | °C | Free Cooling/Heating Minimum External Temperature |
| 2/7 | FreeCHBand | Signed 16-bit | 5.0 | 1.0 | 10.0 | °C | Free Cooling/Heating Proportional Band (direct return reg) |
| 3/7 | FreeCHTimeout | Unsigned 16-bit | 60 | 0 | 180 | min | Free Cooling/Heating Timeout |
| 3/7 | FreeCHDiff | Signed 16-bit | 5.0 | 1.0 | 10.0 | °C | Free Cooling/Heating Outside Regulation Differential |
| 4/7 | FreeCHHyst | Signed 16-bit | 1.0 | 0.2 | 5.0 | °C | Free Cooling/Heating Hysteresis |
| 4/7 | ---------------------- |  |  |  |  |  |  |
| 5/7 | FastHeatCoolEn | Boolean | 0 | — | — | — | Fast Heating/Cooling Enable |
| 5/7 | FastHCTimeout | Signed 16-bit | 10 | 1 | — | Min | Fast Heating/Cooling and StartUp timeout |
| 6/7 | FastCoolSet | Signed 16-bit | 20.0 | -50.0 | 50.0 | °C | Minimum outside temp for Power up Fast Cooling |
| 6/7 | FastCoolExitSet | Signed 16-bit | 26.0 | -50.0 | 50.0 | °C | Fast Cooling Return temperature exit set in case of supply Regulation |
| 7/7 | FastHeatSet | Signed 16-bit | 25.0 | -50.0 | 50.0 | °C | Maximum outside temp for Power up Fast Heating |
| 7/7 | FastHeatExitSet | Signed 16-bit | 18.0 | -50.0 | 50.0 | °C | Fast Heating Return temperature exit set in case of supply Regulation |

Tabella 60 - E5-Regulator

F-I/O

A seguire viene riportata la navigazione del menu "F-I/O", che consente la gestione di ingressi e uscite.

Gli stati del menu "F-I/O" sono riportati nella seguente tabella, suddivisi per pagina (gli elementi sono visibili se definiti nella configurazione corrente dell’unità).

| Pag | Name |  |  |  | Device type |  |  | Unit |  |  | Description |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | AI_LogicIndex_0 | Signed 16-bit |  |  |  | °C |  |  | Supply Temperature |  |
|  |  | AI_LogicIndex_1 | Signed 16-bit |  |  |  | °C |  |  | Return Temperature |  |
|  |  | AI_LogicIndex_2 | Signed 16-bit |  |  |  | °C |  |  | External Temperature |  |
|  |  | AI_LogicIndex_3 | Signed 16-bit |  |  |  | °C |  |  | Expulsion Temperature |  |
|  |  | AI_LogicIndex_4 | Signed 16-bit |  |  |  | °C |  |  | Preheating Temp, |  |
|  |  | AI_LogicIndex_5 | Signed 16-bit |  |  |  | °C |  |  | Saturation Temperature |  |
|  |  | AI_LogicIndex_6 | Signed 16-bit |  |  |  | °C |  |  | Antifreeze Temperature |  |
|  |  | AI_LogicIndex_7 | Signed 16-bit |  |  |  | % |  |  | Air Quality - VOC |  |
|  |  | AI_LogicIndex_8 | Signed 16-bit |  |  |  | ppm |  |  | Air Quality - CO2 |  |
|  |  | AI_LogicIndex_9 | Signed 16-bit |  |  |  | pa |  |  | Supply Pressure |  |
|  |  | AI_LogicIndex_10 | Signed 16-bit |  |  |  | pa |  |  | Return Pressure |  |
|  |  | AI_LogicIndex_11 | Signed 16-bit |  |  |  | % |  |  | Supply Humidity |  |
|  |  | AI_LogicIndex_12 | Signed 16-bit |  |  |  | % |  |  | Return Humidity |  |
|  |  | AI_LogicIndex_13 | Signed 16-bit |  |  |  | % |  |  | External Humidity |  |
|  |  | AI_LogicIndex_14 | Signed 32-bit |  |  |  | m3/h |  |  | Supply Flow Testing |  |
|  |  | AI_LogicIndex_15 | Signed 32-bit |  |  |  | m3/h |  |  | Return Flow Testing |  |
|  |  | DI_Voltage_LogicIndex_0 | 0 = 0V; 1 = 24V; 2 = Not Used |  |  |  | — |  |  | Supply Fan Thermal - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_1 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Return Fan Thermal - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_2 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | On/Off Input - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_3 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Fire Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_4 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Mode Input - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_5 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Door - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_6 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Antifreeze - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_7 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Supply Airflow - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_8 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Return Airflow - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_9 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Humidifier Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_10 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Preheater Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_11 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Postheater Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_12 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Rotary Wheel Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_13 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Filter 1 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_14 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Filter 2 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_15 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Filter 3 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_16 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Filter 4 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_30 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Filter 5 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_17 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Supply Fan 2 Th. - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_18 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Return Fan 2 Th. - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_19 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Supply Fan 2 Airflow - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_20 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Return Fan 2 Airflow - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_21 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_22 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | El. Heater Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_23 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 2 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_24 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 3 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_25 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 4 Alarm - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_26 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 1 Defrost - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_27 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 2 Defrost - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_28 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 3 Defrost - Physical Status |  |
|  |  | DI_Voltage_LogicIndex_29 | See DI_Voltage_LogicIndex_0 |  |  |  | — |  |  | Cond. Unit 4 Defrost - Physical Status |  |
|  |  | AO_LogicIndex_0 | Signed 16-bit |  |  |  | % |  |  | Supply Fan |  |
|  |  | AO_LogicIndex_1 | Signed 16-bit |  |  |  | % |  |  | Return Fan |  |
|  |  | AO_LogicIndex_2 | Signed 16-bit |  |  |  | % |  |  | Ext. Dampers |  |
|  |  | AO_LogicIndex_3 | Signed 16-bit |  |  |  | % |  |  | Bypass Damper |  |
|  |  | AO_LogicIndex_4 | Signed 16-bit |  |  |  | % |  |  | Modulating Cool - C/H |  |
|  |  | AO_LogicIndex_5 | Signed 16-bit |  |  |  | % |  |  | Modulating Heat |  |
|  |  | AO_LogicIndex_6 | Signed 16-bit |  |  |  | % |  |  | Pre Heater |  |
|  |  | AO_LogicIndex_7 | Signed 16-bit |  |  |  | % |  |  | Post Heater |  |
|  |  | AO_LogicIndex_8 | Signed 16-bit |  |  |  | % |  |  | Rotary Wheel / Exchanger |  |
|  |  | AO_LogicIndex_9 | Signed 16-bit |  |  |  | % |  |  | Humidifier |  |
|  |  | AO_LogicIndex_10 | Signed 16-bit |  |  |  | % |  |  | Condensing Unit 1 |  |
|  |  | AO_LogicIndex_11 | Signed 16-bit |  |  |  | % |  |  | Condensing Unit 2 |  |
|  |  | AO_LogicIndex_12 | Signed 16-bit |  |  |  | % |  |  | Condensing Unit 3 |  |
|  |  | AO_LogicIndex_13 | Signed 16-bit |  |  |  | % |  |  | Condensing Unit 4 |  |
|  |  | DO_LogicIndex_0 | 0 = Off; 1 = On; 2 = Not Used |  |  |  | — |  |  | Supply Fan - Logic Status |  |
|  |  | DO_LogicIndex_1 | See DO_LogicIndex_0 |  |  |  | — |  |  | Return Fan - Logic Status |  |
|  |  | DO_LogicIndex_2 | See DO_LogicIndex_0 |  |  |  | — |  |  | On Off - Logic Status |  |
|  |  | DO_LogicIndex_3 | See DO_LogicIndex_0 |  |  |  | — |  |  | Alarm - Logic Status |  |
|  |  | DO_LogicIndex_4 | See DO_LogicIndex_0 |  |  |  | — |  |  | Mode - Logic Status |  |
|  |  | DO_LogicIndex_5 | See DO_LogicIndex_0 |  |  |  | — |  |  | Ext. Dampers - Logic Status |  |
|  |  | DO_LogicIndex_6 | See DO_LogicIndex_0 |  |  |  | — |  |  | Bypass Damper - Logic Status |  |
|  |  | DO_LogicIndex_7 | See DO_LogicIndex_0 |  |  |  | — |  |  | Supply Damper - Logic Status |  |
|  |  | DO_LogicIndex_8 | See DO_LogicIndex_0 |  |  |  | — |  |  | Return Damper - Logic Status |  |
|  |  | DO_LogicIndex_9 | See DO_LogicIndex_0 |  |  |  | — |  |  | Pump Preheat - Logic Status |  |
|  |  | DO_LogicIndex_10 | See DO_LogicIndex_0 |  |  |  | — |  |  | Pump Postheat - Logic Status |  |
|  |  | DO_LogicIndex_11 | See DO_LogicIndex_0 |  |  |  | — |  |  | Cool/CH Pump - Logic Status |  |
|  |  | DO_LogicIndex_12 | See DO_LogicIndex_0 |  |  |  | — |  |  | Cool/CH Step 1 - Logic Status |  |
|  |  | DO_LogicIndex_13 | See DO_LogicIndex_0 |  |  |  | — |  |  | Cool/CH Step 2 - Logic Status |  |
|  |  | DO_LogicIndex_14 | See DO_LogicIndex_0 |  |  |  | — |  |  | Cool/CH Step 3 - Logic Status |  |
|  |  | DO_LogicIndex_15 | See DO_LogicIndex_0 |  |  |  | — |  |  | Cool/CH Step 4 - Logic Status |  |
|  |  | DO_LogicIndex_16 | See DO_LogicIndex_0 |  |  |  | — |  |  | Heat Pump - Logic Status |  |
|  |  | DO_LogicIndex_17 | See DO_LogicIndex_0 |  |  |  | — |  |  | Heater Step 1 - Logic Status |  |
|  |  | DO_LogicIndex_18 | See DO_LogicIndex_0 |  |  |  | — |  |  | Heater Step 2 - Logic Status |  |
|  |  | DO_LogicIndex_19 | See DO_LogicIndex_0 |  |  |  | — |  |  | Heater Step 3 - Logic Status |  |
|  |  | DO_LogicIndex_20 | See DO_LogicIndex_0 |  |  |  | — |  |  | Pre Heater Step 1 - Logic Status |  |
|  |  | DO_LogicIndex_21 | See DO_LogicIndex_0 |  |  |  | — |  |  | Pre Heater Step 2 - Logic Status |  |
|  |  | DO_LogicIndex_22 | See DO_LogicIndex_0 |  |  |  | — |  |  | Pre Heater Step 3 - Logic Status |  |
|  |  | DO_LogicIndex_23 | See DO_LogicIndex_0 |  |  |  | — |  |  | Post Heater Step 1 - Logic Status |  |
|  |  | DO_LogicIndex_24 | See DO_LogicIndex_0 |  |  |  | — |  |  | Post Heater Step 2 - Logic Status |  |
|  |  | DO_LogicIndex_25 | See DO_LogicIndex_0 |  |  |  | — |  |  | Post Heater Step 3 - Logic Status |  |
|  |  | DO_LogicIndex_26 | See DO_LogicIndex_0 |  |  |  | — |  |  | Humidifier - Logic Status |  |
|  |  | DO_LogicIndex_27 | See DO_LogicIndex_0 |  |  |  | — |  |  | Rotary Wheel / Exchanger - Logic Status |  |
|  |  | DO_LogicIndex_28 | See DO_LogicIndex_0 |  |  |  | — |  |  | Supply Fan 2 - Logic Status |  |
|  | DO_LogicIndex_29 |  |  | See DO_LogicIndex_0 |  | — |  |  | Return Fan 2 - Logic Status |  |  |  |
|  | DO_LogicIndex_30 |  |  | See DO_LogicIndex_0 |  | — |  |  | Supply Damper 2 - Logic Status |  |  |  |
|  | DO_LogicIndex_31 |  |  | See DO_LogicIndex_0 |  | — |  |  | Return Damper 2 - Logic Status |  |  |  |

Tabella 61 - F-I/O

G-Password

A seguire viene riportata la navigazione del menu "G-Password", che consente la gestione della password.

I parametri del menu "G-Password" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| - - - | PSWEntry | Unsigned 16-bit | 0 | Password Entry: |
| - - - | PSWLevel | Unsigned 8-bit | — | Current password level |
| - - - | PSWreset | Boolean | 0 | Password Level Reset Request |
| - - - | Unit_Version | Unsigned 16-bit | 0.00 | Unit Application Version |

Tabella 62 - G-Password

Sono previsti due livelli di password, la password Service di livello 1 e la password Costruttore di livello 2.

L’accesso al livello 2 è ammesso solo con unità in OFF. L’accesso ai sottomenu senza l’inserimento della password corretta è in sola lettura.

H-System

A seguire viene riportata la navigazione del menu "H-System", che consente la gestione dei parametri installatore.

S-Service

NOTA: Il tasto  è visibile solo su display del controllore.

S1-Fans

A seguire viene riportata la navigazione del menu "S1-Fans", che consente la gestione dei ventilatori.

|  |  | General |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "General" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/12 | Fan_MinimumSpeed | Signed 16-bit | 25.0 | 0.0 | 50.0 | % | Fan Minimum Speed (Pressure Regulation and limit for other speed) |
| 1/12 | Fan_LowSpeed | Signed 16-bit | 30.0 | Fan _MinimumSpeed | 80.0 | % | Fan Low Speed (Start Phase/Night/Min Air Q. and Defrost Speed) |
| 2/12 | Fan_NominalSpeed | Signed 16-bit | 90.0 | Fan_LowSpeed | 100.0 | % | Fan Nominal/Maximum Speed |
| 2/12 | Fan_ReturnSpeedCorrection | Signed 16-bit | 0.0 | -50.0 | 50.0 | % | Fan Return Output correction (not used with 2 pressure probes) |
| 3/12 | Fan_PowerUp1_Time | Unsigned 16-bit | 30 | 0 | 255 | sec | Fan Power Up Time at Min Speed (with Heaters) |
| 3/12 | Fan_PowerUp2_Time | Unsigned 16-bit | 10 | 0 | 255 | sec | Fan Power Up Time at Nom Speed (with Heaters) |
| 4/12 | Fan_SinglePressureReturn | Boolean | 0 | — | — | — | In case of a unique pressure probe mounted on return section and Supply+Return Fans |
| 4/12 | Fan_Post_Time | Unsigned 16-bit | 40 | 0 | 255 | sec | Fan Post Ventilation Time (with Heaters) |
| 5/12 | Fan_PreHeating_Time | Unsigned 16-bit | 180 | 0 | 600 | sec | Fan Preheating Time (with heating valves) |
| 5/12 | Fan_PreHeatOnSet | Signed 16-bit | -5.0 | -20.0 | 10.0 | °C | External Temperature Set forcing preheating time |
| 6/12 | Fan_Swap_Time | Unsigned 16-bit | 240 | 0 | 600 | hours | Fan swap time (0=Disabled) |
| 6/12 | Fan_SwapPolicy | 0 = If available Start always Fans 1; 1 = Start Section with less working hours (Supply + Return); 2 = Start Fans with less working hours; 3 = Start Fans with less working hours keeping parallel sections | 0 | 0 | 3 | — | Fan swap policy |
| 7/12 | Fan_Maintenance_Supply | Boolean | 0 | — | — | — | Fan Main Supply Forced Off for maintenance |
| 7/12 | Fan_Maintenance_Return | Boolean | 0 | — | — | — | Fan Main Return Forced Off for maintenance |
| 8/12 | Fan_Maintenance_SupplyBck | Boolean | 0 | — | — | — | Fan Supply 2 Forced Off for maintenance |
| 8/12 | Fan_Maintenance_ReturnBck | Boolean | 0 | — | — | — | Fan Return 2 Forced Off for maintenance |
| 9/12 | Fan_Maintenance_Supply1b | Boolean | 0 | — | — | — | Fan Main Supply b Forced Off for maintenance |
| 9/12 | Fan_Maintenance_Supply1c | Boolean | 0 | — | — | — | Fan Main Supply c Forced Off for maintenance |
| 10/12 | Fan_Maintenance_Return1b | Boolean | 0 | — | — | — | Fan Main Return b Forced Off for maintenance |
| 10/12 | Fan_Maintenance_Return1c | Boolean | 0 | — | — | — | Fan Main Return c Forced Off for maintenance |
| 11/12 | Fan_Maintenance_Supply2b | Boolean | 0 | — | — | — | Fan Supply 2b Forced Off for maintenance |
| 11/12 | Fan_Maintenance_Supply2c | Boolean | 0 | — | — | — | Fan Supply 2c Forced Off for maintenance |
| 12/12 | Fan_Maintenance_Return2b | Boolean | 0 | — | — | — | Fan Main Return 2b Forced Off for maintenance |
| 12/12 | Fan_Maintenance_Return2c | Boolean | 0 | — | — | — | Fan Main Return 2c Forced Off for maintenance |

Tabella 63 - General

I parametri del menu "Working Hours" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| 1/3 | Unit_DD | Unsigned 16-bit | days | Unit Working Days |
| 1/3 | --------------------- |  |  |  |
| 2/3 | FanSupply_DD | Unsigned 16-bit | days | Supply Fan Working Days |
| 2/3 | FanSupplyBck_DD | Unsigned 16-bit | days | Supply Fan 2 Working Days |
| 3/3 | FanReturn_DD | Unsigned 16-bit | days | Return Fan Working Days |
| 3/3 | FanReturnBck_DD | Unsigned 16-bit | days | Return Fan 2 Working Days |

Tabella 64 - Working Hours

I parametri del menu "Supply" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/7 | Fan_Supply_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | Fan Supply Regulation Unit |
| 1/7 | Fan_K_Supply | Unsigned 16-bit | 100 | 1 | 3000 | — | Fan K Supply |
| 2/7 | Fan_SetFlowSupply | Signed 32-bit | 100 | Fan_Supply_SetMinFlow | Fan_Supply_SetMaxFlow | m3/h | Fan Supply Flow Setpoint |
| 2/7 | Fan_SetPrSupply | Signed 16-bit | 100 | Fan_Supply_SetMinPr | Fan_Supply_SetMaxPr | Pa | Fan Supply Pressure Setpoint |
| 3/7 | AI_LogicIndex_14 | Signed 32-bit | — | — | — | m3/h | Supply Flow Testing |
| 3/7 | AI_LogicIndex_9 | Signed 16-bit | — | — | — | pa | Supply Pressure |
| 4/7 | Fan_Supply_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | Fan Supply Minimum/Night Flow Setpoint |
| 4/7 | Fan_Supply_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | Fan Supply Maximum Flow Setpoint |
| 5/7 | Fan_Supply_SetMinPr | Signed 16-bit | 50 | — | — | Pa | Fan Supply Minimum/Night Pressure Setpoint |
| 5/7 | Fan_Supply_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | Fan Supply Maximum Pressure Setpoint |
| 6/7 | FAN_Supply_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | Fan Supply Prop. Band Pressure |
| 6/7 | FAN_Supply_TiP | Unsigned 16-bit | 75 | — | — | sec | Fan Supply Integral Time Pressure |
| 7/7 | FAN_Supply_TdP | Unsigned 16-bit | 0 | — | — | sec | Fan Supply Derivative Time Pressure |

Tabella 65 - Supply

I parametri del menu "Return" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/7 | Fan_Return_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | Fan Return Regulation Unit |
| 1/7 | Fan_K_Return | Unsigned 16-bit | 100 | 1 | 3000 | — | Fan K Return |
| 2/7 | Fan_SetFlowReturn | Signed 32-bit | 100 | Fan_Return_SetMinFlow | Fan_Return_SetMaxFlow | m3/h | Fan Return Flow Setpoint |
| 2/7 | Fan_SetPrReturn | Signed 16-bit | 100 | Fan_Return_SetMinPr | Fan_Return_SetMaxPr | Pa | Fan Return Pressure Setpoint |
| 3/7 | AI_LogicIndex_15 | Signed 32-bit | — | — | — | m3/h | Return Flow Testing |
| 3/7 | AI_LogicIndex_10 | Signed 16-bit | — | — | — | pa | Return Pressure |
| 4/7 | Fan_Return_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | Fan Return Minimum/Night Flow Setpoint |
| 4/7 | Fan_Return_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | Fan Return Maximum Flow Setpoint |
| 5/7 | Fan_Return_SetMinPr | Signed 16-bit | 50 | — | — | Pa | Fan Return Minimum/Night Pressure Setpoint |
| 5/7 | Fan_Return_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | Fan Return Maximum Pressure Setpoint |
| 6/7 | FAN_Return_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | Fan Return Prop. Band Pressure |
| 6/7 | FAN_Return_TiP | Unsigned 16-bit | 75 | — | — | sec | Fan Return Integral Time Pressure |
| 7/7 | FAN_Return_TdP | Unsigned 16-bit | 0 | — | — | sec | Fan Return Derivative Time Pressure |

Tabella 66 - Return

Nel caso di ventole pilotate via Modbus ed in funzione del numero di ventole, i parametri del menu "i Supply" sono riportati nella seguente tabella.

|  |  | Modbus Fan Info |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| Model | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| Ziehl/EBM | Status_Supply1_FansActualSpeed | Signed 16-bit | Rpm | Supply Ziehl/EBM Speed |
| Ziehl/EBM | Status_Supply1_FansVoltage | Signed 16-bit | V | Supply Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Supply1_FansCurrent | Signed 16-bit | A | Supply Ziehl/EBM Current |
| Ziehl/EBM | Status_Supply2_FansActualSpeed | Signed 16-bit | Rpm | Supply Backup Ziehl/EBM Speed |
| Ziehl/EBM | Status_Supply2_FansVoltage | Signed 16-bit | V | Supply Backup Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Supply2_FansCurrent | Signed 16-bit | A | Supply Backup Ziehl/EBM Current |
| ATV | Status_Supply1_FansActualSpeedHz | Signed 16-bit | Hz | Supply ATV212 Speed |
| ATV | Supply1_ATV212_FreqMin | Unsigned 16-bit | Hz | Supply ATV 212 Minimum Frequency |
| ATV | Supply1_ATV212_FreqMax | Unsigned 16-bit | Hz | Supply ATV 212 Maximum Frequency |
| ATV | Status_Supply1_FansVoltagePerc | Signed 16-bit | % | Supply ATV212 DC Voltage |
| ATV | Status_Supply1_FansCurrentPerc | Signed 16-bit | % | Supply ATV212 DC Current |
| ATV | Status_Supply2_FansActualSpeedHz | Signed 16-bit | Hz | Supply Backup ATV212 Speed |
| ATV | Supply2_ATV212_FreqMin | Unsigned 16-bit | Hz | Supply Backup ATV 212 Minimum Frequency |
| ATV | Supply2_ATV212_FreqMax | Unsigned 16-bit | Hz | Supply Backup ATV 212 Minimum Frequency |
| ATV | Status_Supply2_FansVoltagePerc | Signed 16-bit | % | Supply Backup ATV212 DC Voltage |
| ATV | Status_Supply2_FansCurrentPerc | Signed 16-bit | % | Supply Backup ATV212 DC Current |

Tabella 67 - I Supply

Nel caso di ventole pilotate via Modbus ed in funzione del numero di ventole, i parametri del menu "i Return" sono riportati nella seguente tabella.

| Model | Name | Device type | Unit | Description |
| --- | --- | --- | --- | --- |
| Ziehl/EBM | Status_Return1_FansActualSpeed | Signed 16-bit | rpm | Return Ziehl/EBM Speed |
| Ziehl/EBM | Status_Return1_FansVoltage | Signed 16-bit | V | Return Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Return1_FansCurrent | Signed 16-bit | A | Return Ziehl/EBM Current |
| Ziehl/EBM | Status_Return2_FansActualSpeed | Signed 16-bit | rpm | Return Backup Ziehl/EBM Speed |
| Ziehl/EBM | Status_Return2_FansVoltage | Signed 16-bit | V | Return Backup Ziehl/EBM DC Voltage |
| Ziehl/EBM | Status_Return2_FansCurrent | Signed 16-bit | A | Return Backup Ziehl/EBM Current |
| ATV | Status_Return1_FansActualSpeedHz | Signed 16-bit | Hz | Return ATV212 Speed |
| ATV | Return1_ATV212_FreqMin | Unsigned 16-bit | Hz | Return ATV 212 Minimum Frequency |
| ATV | Return1_ATV212_FreqMax | Unsigned 16-bit | Hz | Return ATV 212 Maximum Frequency |
| ATV | Status_Return1_FansVoltagePerc | Signed 16-bit | % | Return ATV212 DC Voltage |
| ATV | Status_Return1_FansCurrentPerc | Signed 16-bit | % | Return ATV212 DC Current |
| ATV | Status_Return2_FansActualSpeedHz | Signed 16-bit | Hz | Return Backup ATV212 Speed |
| ATV | Return2_ATV212_FreqMin | Unsigned 16-bit | Hz | Return Backup ATV 212 Minimum Frequency |
| ATV | Return2_ATV212_FreqMax | Unsigned 16-bit | Hz | Return Backup ATV 212 Maximum Frequency |
| ATV | Status_Return2_FansVoltagePerc | Signed 16-bit | % | Return Backup ATV212 DC Voltage |
| ATV | Status_Return2_FansCurrentPerc | Signed 16-bit | % | Return Backup ATV212 DC Current |

Tabella 68 - I Return

|  |  | Alarm Info Supply |  |  | ATV212 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | EBM |  |  |
|  |  |  |  |  | ZIEHL |  |  |

I parametri del menu "Sup.Alarms" sono riportati nella seguente tabella, suddivisi per pagina.

| Name | Description |
| --- | --- |
| Supply1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply1_EBM_MotorStatus | EBM D011+1 : Motor status |
| Supply2_EBM_MotorStatus | EBM D011+1 : Motor status |
| Supply1_ATV212_Status | ATV212: 64769+1 Fd01 |
| Supply1_ATV212_Trip | ATV212: 64656+1 FC90 |
| Supply2_ATV212_Status | ATV212: 64769+1 Fd01 |
| Supply2_ATV212_Trip | ATV212: 64656+1 FC90 |
| Supply1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Supply2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |

Tabella 69 - Sup.Alarms

I parametri del menu "Ret.Alarms" sono riportati nella seguente tabella, suddivisi per pagina.

| Name | Description |
| --- | --- |
| Return1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return1_EBM_MotorStatus | EBM D011+1 : Motor status |
| Return2_EBM_MotorStatus | EBM D011+1 : Motor status |
| Return1_ATV212_Status | ATV212: 64769+1 Fd01 |
| Return1_ATV212_Trip | ATV212: 64656+1 FC90 |
| Return2_ATV212_Status | ATV212: 64769+1 Fd01 |
| Return2_ATV212_Trip | ATV212: 64656+1 FC90 |
| Return1_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |
| Return2_Ziehl_Basic_ErrorStatus | Ziehl MB Input Register 13 = error status |

Tabella 70 - Ret.Alarms

NOTA: Per i ventilatori Modbus il reset è possibile esclusivamente con password.

NOTA: Il tasto "I Supply" è visibile solo se attivo un ventilatore Modbus.

NOTA: Il tasto "Alarm Info Supply" è visibile solo se attivo un allarme relativo a un ventilatore Modbus.

S2-Actuators

A seguire viene riportata la navigazione del menu "S2-Actuators", che consente la gestione degli attuatori.

|  |  | Dampers |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "Dampers" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | ExtDamperOpenDelay | Unsigned 16-bit | 60 | — | — | sec | External/Fan Damper Open Time |
| 1/2 | ExtDamperCloseDelay | Unsigned 16-bit | 60 | — | — | sec | External/Fan Damper Close Time |
| 2/2 | ExtDamperMinOpen | Signed 16-bit | 50 | 0 | 100 | % | External Damper Minimum Open |
| 2/2 | ExtDamperMaxOpen | Signed 16-bit | 100 | ExtDamperMinOpen | 100 | % | External Damper Maximum Open |

Tabella 71 - Dampers

I parametri del menu "El.Heat." sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/15 | Heater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Analog Power |
| 1/15 | Heater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 1 Power |
| 2/15 | Heater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 2 Additional Power |
| 2/15 | Heater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 3 Additional Power |
| 3/15 | Heater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 4 Additional Power |
| 3/15 | Heater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 5 Additional Power |
| 4/15 | Heater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | Power | El. Heater Step 6 Additional Power |
| 4/15 | Heater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | El. Heater Hysteresis [% of current step] |
| 5/15 | Heater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | El. Heater PWM Period |
| 5/15 | ----------------------------- |  |  |  |  |  |  |
| 6/15 | PreHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Analog Power |
| 6/15 | PreHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 1 Power |
| 7/15 | PreHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 2 Power |
| 7/15 | PreHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 3 Power |
| 8/15 | PreHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 4 Power |
| 8/15 | PreHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 5 Power |
| 9/15 | PreHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | PreHeater Step 6 Power |
| 9/15 | PreHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | PreHeater Hysteresis [% of current step] |
| 10/15 | PreHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | PreHeater PWM Period |
| 10/15 | ----------------------------- |  |  |  |  |  |  |
| 11/15 | PostHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Analog Power |
| 11/15 | PostHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 1 Power |
| 12/15 | PostHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 2 Power |
| 12/15 | PostHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 3 Power |
| 13/15 | PostHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 4 Power |
| 13/15 | PostHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 5 Power |
| 14/15 | PostHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | PostHeater Step 6 Power |
| 14/15 | PostHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | PostHeater Hysteresis [% of current step] |
| 15/15 | PostHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | PreHeater PWM Period |

Tabella 72 - El.Heat.

I parametri del menu "Pumps" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | Pump_AntiStickingRun | Unsigned 16-bit | 20 | 0 | 255 | sec | Antisticking run time |
| 1/2 | Pump_AntiStickingPeriod | Unsigned 16-bit | 7 | 0 | 30 | days | Antisticking period (0=Disabled) |
| 2/2 | Pump_Post_Time | Unsigned 16-bit | 5 | 0 | 255 | min | Pump Post Running Time |

Tabella 73 - Pumps

I parametri del menu "Cond.Unit" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/11 | CondUnitS1_Req | Signed 16-bit | 20.0 | 0.0 | 100.0 | % | % CondUnit Step 1 |
| 1/11 | CondUnitS2_Req | Signed 16-bit | 40.0 | 0.0 | 100.0 | % | % CondUnit Step 2 |
| 2/11 | CondUnitS3_Req | Signed 16-bit | 60.0 | 0.0 | 100.0 | % | % CondUnit Step 3 |
| 2/11 | CondUnitS4_Req | Signed 16-bit | 80.0 | 0.0 | 100.0 | % | % CondUnit Step 4 |
| 3/11 | CondUnitSx_Hysteresis | Signed 16-bit | 50 | 10 | 100 | % | Cond. Unit Hysteresis % of current Step size |
| 3/11 | CondUnit_Offset | Signed 16-bit | 0.0 | 0.0 | 100.0 | % | Cond Unit AO Offset |
| 4/11 | CondUnit_Ton | Unsigned 16-bit | 0 | 0 | 600 | sec | Cond Unit Step Minimum On Time |
| 4/11 | CondUnit_Toff | Unsigned 16-bit | 0 | 0 | 600 | sec | Cond Unit Step Minimum Off Time |
| 5/11 | CondUnit_FanSpeedDefrost | 0=No Action 1=Low Speed 2=Fan Off |  |  |  |  | Condensing Unit: Fan Speed During Defrost |
| 6/11 | MultiCondUnit_CtrlMode | 0=Delay 1=Hysteresis |  |  |  |  | Multi Condensing Unit: Control |
| 6/11 | MultiCondUnit_RegHyst | Signed 16-bit | 5 | 2 | 30 | % | Multi Condensing Unit regulator hysteresis |
| 7/11 | MultiCondUnit_DelayOn | Unsigned 16-bit | 0 | 0 | 600 | Sec | Multi Cond Unit Delay On |
| 7/11 | MultiCondUnit_DelayOff | Unsigned 16-bit | 0 | 0 | 600 | Sec | Multi Cond Unit Delay Off |
| 8/11 | CU1_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 1 Forced Off for maintenance |
| 8/11 | CU2_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 2 Forced Off for maintenance |
| 9/11 | CU3_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 3 Forced Off for maintenance |
| 9/11 | CU4_Maintenance | Boolean | 0 |  |  |  | Condensing Unit 4 Forced Off for maintenance |
| 10/11 | CondUnit1_DD | Unsigned 16-bit |  |  |  | days | Condensing Unit 1 Working Days |
| 10/11 | CondUnit2_DD | Unsigned 16-bit |  |  |  | Days | Condensing Unit 2 Working Days |
| 11/11 | CondUnit3_DD | Unsigned 16-bit |  |  |  | Days | Condensing Unit 3 Working Days |
| 11/11 | CondUnit4_DD | Unsigned 16-bit |  |  |  | days | Condensing Unit 4 Working Days |

Tabella 74 - Cond.Unit

S3-Regulators

A seguire viene riportata la navigazione del menu "S3-Regulators", che consente la gestione dei regolatori.

|  |  | Temperat. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "Temperat." sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/17 | Unit_RegTempType | 0=Supply; 1=Return Direct; 2=Return Cascade | 1 | 0 | 2 | — | Temperature Regulation Probe |
| 1/17 | ---------------------- |  |  |  |  |  |  |
| 2/17 | SP_T_MIN | Signed 16-bit | 14.0 | — | SP_T_MAX | °C | Minimum Temperature Setpoint |
| 2/17 | SP_T_MAX | Signed 16-bit | 30.0 | SP_T_MIN | — | °C | Maximum Temperature Setpoint |
| 3/17 | SP_T_FORCESUMMER | Signed 16-bit | 24.0 | — | — | °C | Force Summer Mode (AUTO) |
| 3/17 | SP_T_FORCEWINTER | Signed 16-bit | 16.0 | — | — | °C | Force Winter Mode (AUTO) |
| 4/17 | DIFF_T_AutoChangeMode | Signed 16-bit | 2.0 | 0.5 | — | °C | Differential Change season (AUTO) |
| 4/17 | ---------------------- |  |  |  |  |  |  |
| 5/17 | Pb_Cooling | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Cooling Proportional Band |
| 5/17 | Ti_Cooling | Unsigned 16-bit | 0 | 0 | — | sec | Cooling Integral Time |
| 6/17 | Temp_LowSupplyEn | Boolean | 0 | — | — | — | Temperature Low Supply Limit Enable (Summer) |
| 6/17 | Temp_LowSupplySet | Signed 16-bit | 15.0 | 0.0 | 100.0 | °C | Temperature Low Supply Limit Setpoint (Summer) |
| 7/17 | Temp_LowSupplyBand | Signed 16-bit | 10.0 | 1.0 | 99.9 | °C | Temperature Low Supply Band (Summer) |
| 7/17 | ---------------------- |  |  |  |  |  |  |
| 8/17 | Pb_ReturnCooling | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Return Temp. Reg: Cooling Proportional Band (only Cascade) |
| 8/17 | Ti_ReturnCooling | Unsigned 16-bit | 0 | 0 | — | sec | Return Temp. Reg: Cooling Integral Time (only Cascade) |
| 9/17 | SupplyDeltaUpCooling | Signed 16-bit | 1.0 | 0.5 | 5.0 | °C | Cooling Max Supply =RegSet+SupplyDeltaUpCooling |
| 9/17 | SupplyDeltaDwCooling | Signed 16-bit | 12.0 | 0.5 | 15.0 | °C | Cooling Min Supply =RegSet-SupplyDeltaDwCooling |
| 10/17 | Pb_Heating | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Heating Proportional Band |
| 10/17 | Ti_Heating | Unsigned 16-bit | 0 | 0 | — | sec | Heating Integral Time |
| 11/17 | Temp_HighSupplyEn | Boolean | 0 | — | — | — | Temperature High Supply Limit Enable (Winter) |
| 11/17 | Temp_HighSupplySet | Signed 16-bit | 35.0 | 0.0 | 100.0 | °C | Temperature High Supply Limit Setpoint (Winter) |
| 12/17 | Temp_HighSupplyBand | Signed 16-bit | 10.0 | 1.0 | 99.9 | °C | Temperature High Supply Band (Winter) |
| 12/17 | ---------------------- |  |  |  |  |  |  |
| 13/17 | Pb_ReturnHeating | Signed 16-bit | 2.0 | 0.2 | 99.9 | °C | Return Temp. Reg: Heating Proportional Band (only Cascade) |
| 13/17 | Ti_ReturnHeating | Unsigned 16-bit | 0 | 0 | — | sec | Return Temp. Reg: Heating Integral Time (only Cascade) |
| 14/17 | SupplyDeltaUpHeating | Signed 16-bit | 16.0 | 0.5 | 40.0 | °C | Heating Max Supply =RegSet+SupplyDeltaUpHeating |
| 14/17 | SupplyDeltaDwHeating | Signed 16-bit | 2.0 | 0.0 | 5.0 | °C | Heating Min Supply =RegSet-SupplyDeltaDwHeating |
| 15/17 | PostHeating4Integration | Boolean | 1 | — | — | — | Use the post heating also in the heating phase |
| 15/17 | PostPower | Signed 16-bit | 30.0 | 0.1 | 100.0 | % | % of PI out sent to post (if enabled as heat integration) |
| 16/17 | PreHeaterSetpoint | Signed 16-bit | 5.0 | -10.0 | 20.0 | °C | Setpoint Pre Heating |
| 16/17 | Pb_PreHeating | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | PreHeating Proportional Band |
| 17/17 | Ti_PreHeating | Unsigned 16-bit | 300 | 0 | — | sec | PreHeating Integral Time |

Tabella 75 - Temperat.

I parametri del menu "Humidity" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/10 | SP_RH_MinSetpoint | Signed 16-bit | 30 | 20 | SP_RH _MaxSetpoint | %R.H. | Minimum relative humidity setpoint |
| 1/10 | SP_RH_MaxSetpoint | Signed 16-bit | 90 | SP_RH _MinSetpoint | 100 | %R.H. | Maximum relative humidity setpoint |
| 2/10 | Hum_Band | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | Humidification Band |
| 2/10 | Hum_HighSupplyEn | Boolean | 0 | — | — | — | Humidification High Supply Limit Enable |
| 3/10 | Hum_HighSupplySet | Signed 16-bit | 70.0 | 0.0 | 100.0 | %R.H. | Humidification High Supply Limit Setpoint |
| 3/10 | Hum_HighSupplyBand | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | Humidification High Supply Band |
| 4/10 | Pb_Dehum | Signed 16-bit | 10.0 | 0.2 | 20.0 | %R.H. | Dehum. Proportional Band |
| 4/10 | Ti_Dehum | Unsigned 16-bit | 0 | 0 | — | sec | Dehum. Integral Time |
| 5/10 | Pb_Dewpoint | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | Dewpoint Dehum. Proportional Band |
| 5/10 | Ti_Dewpoint | Unsigned 16-bit | 300 | 0 | — | sec | Dewpoint Dehum. Integral Time |
| 6/10 | Dehum_WinterEn | Boolean | 0 | — | — | — | Enable Winter Dehumidification |
| 6/10 | Dehum_WinterHumHyst | Signed 16-bit | 1.0 | 0.4 | 5.0 | g/Kg | Winter Dehumidification Hysteresis |
| 7/10 | Dehum_Req_Diff | Signed 16-bit | 5.0 | 0.1 | 15.0 | %R.H. | Dehumidification Request Differential on Return Humidity for Winter and Dewpoint mode |
| 7/10 | DeHum_LowSupplyEn | Boolean | 0 | — | — | %R.H. | DeHumidification Low Supply Limit Enable |
| 8/10 | DeHum_LowSupplySet | Signed 16-bit | 30.0 | 0.0 | 100.0 | %R.H. | DeHumidification Low Supply Limit Setpoint |
| 8/10 | DeHum_LowSupplyBand | Signed 16-bit | 20.0 | 1.0 | 40.0 | %R.H. | DeHumidification Low Supply Band |
| 9/10 | Pb_Post | Signed 16-bit | 10.0 | 0.2 | 99.9 | °C | PostHeating Dehum. Proportional Band |
| 9/10 | Ti_Post | Unsigned 16-bit | 300 | 0 | — | sec | PostHeating Dehum. Integral Time |
| 10/10 | Offset_Post | Signed 16-bit | 1.0 | 0.4 | 5.0 | °C | PostHeating Setpoint offset with respect to current set |

Tabella 76 - Humidity

I parametri del menu "Air Qual." sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/2 | VOC_Bp | Unsigned 16-bit | 30.0 | 0.1 | % | VOC Regulator: Prop. Band |
| 1/2 | VOC_Ti | Unsigned 16-bit | 0 | — | sec | VOC Regulator: Integral Time |
| 2/2 | CO2_Bp | Unsigned 16-bit | 400 | 1 | ppm | CO2 Regulator: Prop. Band |
| 2/2 | CO2_Ti | Unsigned 16-bit | 0 | — | sec | CO2 Regulator: Integral Time |

Tabella 77 - Air Qual.

I parametri del menu "Recovery" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | RecoveryDiff_Band | Signed 16-bit | 1.5 | 0.1 | 10.0 | °C | Recovery Diff (On/Off Case) Recovery Band (Mod Case with Direct Return control); |
| 1/2 | RecoveryDeadZone | Signed 16-bit | 1.0 | 0.0 | 10.0 | °C | Recovery Dead Zone |
| 2/2 | RecoveryPower | Signed 16-bit | 25.0 | 0.0 | 100.0 | % | % of PI out sent to recovery (Only for Cascade or Supply control) |
| 2/2 | RecoveryReqDuringFastHC | Signed 16-bit | 0 | 0 | 100.0 | % | Recovery request during Fast Heating/Cooling |

Tabella 78 - Recovery

I parametri del menu "Defrost" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | RecoveryDefrost_SetMaxReq | Signed 16-bit | -4.0 | -15.0 | 10.0 | °C | Recovery Defrost: Setpoint Expulsion Temperature |
| 1/2 | RecoveryDefrost_Band | Signed 16-bit | 4.0 | 0.1 | 10.0 | °C | Recovery Defrost: Band Mix Chamber/PreHeater/Supply Fan |
| 2/2 | RecoveryDefrost_Cutoff | Signed 16-bit | 0.0 | 0.0 | 10.0 | °C | Recovery Defrost: CutOff Modulating Fan |

Tabella 79 - Defrost

I parametri del menu "Other" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Description |
| --- | --- | --- | --- | --- |
| 1/1 | Unit_ForceOffAfterReboot | Boolean | 0 | Force Off keyboard after reboot |

Tabella 80 – Other

S4-Conf.Alarms

A seguire viene riportata la navigazione del menu "S4-Conf.Alarms", che consente la gestione degli allarmi.

I parametri del menu "Conf.Alarms" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/8 | AFset | Signed 16-bit | 5.0 | -5.0 | 15.0 |  |  | °C |  | Antifreeze Setpoint |
| 1/8 | AFdiff | Signed 16-bit | 2.0 | 0.1 | 5.0 |  |  | °C |  | Antifreeze Differential |
| 2/8 | AFphtime | Unsigned 16-bit | 5 | 0 | 255 |  |  | min |  | Antifreeze Preheater time |
| 2/8 | ---------------------- |  |  |  |  |  |  |  |  |  |
| 3/8 | cfgFireAlarm | 0=Off All; 1=All Fans-Damper On; 2=ReturnFan-Damper On | 0 | 0 | 2 |  |  | — |  | Fire Alarm Configuration |
| 3/8 | FireTempSet | Signed 16-bit | 95.0 | 90.0 | — |  |  | °C |  | Setpoint Temperature for Fire Alarm |
| 4/8 | Fan_SupplyAirflowAlrmByAi | Boolean | 0 | — | — |  |  | — |  | Enable supply flow alarm by probe (pressure probe must be already enabled) |
| 4/8 | Fan_ReturnAirflowAlrmByAi | Boolean | 0 | — |  | — |  | — |  | Enable return flow alarm by probe (pressure probe must be already enabled) |
| 5/8 | Fan_SetMinAirflow | Signed 16-bit | 50 | — | — |  |  | Pa |  | Fan Airflow Alarm setpoint |
| 5/8 | Fan_AlrmPressBypass | Unsigned 16-bit | 30 | 1 | 600 |  |  | Sec |  | Flow Bypass |
| 6/8 | Alm_MinHumiditySens | Signed 16-bit | 2.0 | 0.0 | 100.0 |  |  | %R.H. |  | Minimum Valid Humidity Value |
| 6/8 | Alm_MinCO2Sens | Signed 16-bit | 40 | 0 | — |  |  | ppm |  | Minimum Valid CO2 Value |
| 7/8 | Alm_MinVOCSens | Signed 16-bit | 2.0 | 0.0 | 100.0 |  |  | % |  | Minimum Valid VOC Value |
| 7/8 | Alm_MinPrSens | Signed 16-bit | 40 | 0 |  | — |  | pa |  | Minimum Valid Pr Value (Fans on) |
| 8/8 | Alm_ActiveProbeBypass | Unsigned 16-bit | 30 | 0 | 600 |  |  | sec |  | Active Probe alarm bypass |

Tabella 81 - Conf.Alarms

S5-Data Logger

A seguire viene riportata la navigazione del menu "S5-Data Logger", che consente la gestione del data logger.

I parametri del menu "Data Logger" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2 | LogEnable | Boolean | 0 | — | — | — | Logger Enable |
| 1/2 | LogCycle | Unsigned 16-bit | 00:01 | MinLogCycle | 23:59 | Min | Logger Period |
| 2/2 | FileDimension | Unsigned 32-bit | — | — | — | — | Size of the current log file- Log Export to USB |
| 2/2 | MinLogCycle | Signed 16-bit | 00:01 | 0 | 23:59 | Min | Minimum Log Cycle |

Tabella 82 - Data Logger

S6-Restore Factory

A seguire viene riportata la navigazione del menu "S6-Restore Factory", che consente la gestione del ripristino dei parametri di fabbrica.

I parametri del menu "Restore Factory" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | RestoreFactoryStatus | 0=Completed; 1=Running; 248=Open in write failed; 249=Write failed; 250=Some parameters failed; 251=File not compatible; 252=Usb not connected; 253=File too long; 254=File not present; 255=Command Failed | — | 0 | 255 | Restore Factory Settings Status |
| - - - | RestoreFactoryCommand | Boolean | 0 | — | — | Restore Factory Settings Request |

Tabella 83 - Restore Factory

S7-Modbus Scan

A seguire viene riportata la navigazione del menu "S7-Modbus Scan", che consente la configurazione di holding register per slave con indirizzo (1…10 o 247) 19.2 E,8,1 collegati alla porta RS485-2.

NOTA: Il tasto Preset si riferisce ai ventilatori Modbus.

|  |  | Preset |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O-I/O

NOTA: Il sottomenu è editabile solo dopo inserimento password.

O1-Polarity

A seguire viene riportata la navigazione del menu "O1-Polarity", che consente la gestione delle polarità di ingressi e uscite digitali.

|  |  | Polarity |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri della pagina "O1-Polarity" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/29 | DI_Polarity_LogicIndex_0 | 0V = Off, 24V = On/Alarm; 0V = On/Alarm, 24V = Off | 1 | 0 | 1 | Polarity - Supply Fan Thermal |
| 1/29 | DI_Polarity_LogicIndex_1 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return Fan Thermal |
| 2/29 | DI_Polarity_LogicIndex_2 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - On/Off Input |
| 2/29 | DI_Polarity_LogicIndex_3 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Fire Alarm |
| 3/29 | DI_Polarity_LogicIndex_4 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Mode Input |
| 3/29 | DI_Polarity_LogicIndex_5 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Door |
| 4/29 | DI_Polarity_LogicIndex_6 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Antifreeze |
| 4/29 | DI_Polarity_LogicIndex_7 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply Airflow |
| 5/29 | DI_Polarity_LogicIndex_8 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return Airflow |
| 5/29 | DI_Polarity_LogicIndex_9 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Humidifier Alarm |
| 6/29 | DI_Polarity_LogicIndex_10 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Preheater Alarm |
| 6/29 | DI_Polarity_LogicIndex_11 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Postheater Alarm |
| 7/29 | DI_Polarity_LogicIndex_12 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Rotary Wheel Alarm |
| 7/29 | DI_Polarity_LogicIndex_13 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 1 Alarm |
| 8/29 | DI_Polarity_LogicIndex_14 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 2 Alarm |
| 8/29 | DI_Polarity_LogicIndex_15 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 3 Alarm |
| 9/29 | DI_Polarity_LogicIndex_16 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 4 Alarm |
| 9/29 | DI_Polarity_LogicIndex_30 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | Polarity - Filter 5 Alarm |
| 10/29 | DI_Polarity_LogicIndex_17 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply 2 Fan Th. |
| 10/29 | DI_Polarity_LogicIndex_18 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return 2 Fan Th. |
| 11/29 | DI_Polarity_LogicIndex_19 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Supply 2 Airflow |
| 11/29 | DI_Polarity_LogicIndex_20 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Return 2 Airflow |
| 12/29 | DI_Polarity_LogicIndex_21 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Cond. Unit Alarm |
| 12/29 | DI_Polarity_LogicIndex_22 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - El. Heater Alarm |
| 13/29 | DI_Polarity_LogicIndex_26_29 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | Polarity - Cond. Unit Defrost |
| 13/29 | DO_Polarity_LogicIndex_0 | 0=NO; 1=NC | 0 | 0 | 1 | Supply Fan - DO Polarity |
| 14/29 | DO_Polarity_LogicIndex_1 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Fan - DO Polarity |
| 14/29 | DO_Polarity_LogicIndex_2 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | On Off - DO Polarity |
| 15/29 | DO_Polarity_LogicIndex_3 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Alarm - DO Polarity |
| 15/29 | DO_Polarity_LogicIndex_4 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Mode - DO Polarity |
| 16/29 | DO_Polarity_LogicIndex_5 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Ext. Dampers - DO Polarity |
| 16/29 | DO_Polarity_LogicIndex_6 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Bypass Damper - DO Polarity |
| 17/29 | DO_Polarity_LogicIndex_7 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Damper - DO Polarity |
| 17/29 | DO_Polarity_LogicIndex_8 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Damper - DO Polarity |
| 18/29 | DO_Polarity_LogicIndex_9 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump Preheat - DO Polarity |
| 18/29 | DO_Polarity_LogicIndex_10 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump Postheat - DO Polarity |
| 19/29 | DO_Polarity_LogicIndex_11 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Pump - DO Polarity |
| 19/29 | DO_Polarity_LogicIndex_12 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 1 - DO Polarity |
| 20/29 | DO_Polarity_LogicIndex_13 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 2 - DO Polarity |
| 20/29 | DO_Polarity_LogicIndex_14 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 3 - DO Polarity |
| 21/29 | DO_Polarity_LogicIndex_15 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Cool/CH Step 4 - DO Polarity |
| 21/29 | DO_Polarity_LogicIndex_16 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pump heat - DO Polarity |
| 22/29 | DO_Polarity_LogicIndex_17 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 1 - DO Polarity |
| 22/29 | DO_Polarity_LogicIndex_18 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 2 - DO Polarity |
| 23/29 | DO_Polarity_LogicIndex_19 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | El. Heater Step 3 - DO Polarity |
| 23/29 | DO_Polarity_LogicIndex_20 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 1 - DO Polarity |
| 24/29 | DO_Polarity_LogicIndex_21 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 2 - DO Polarity |
| 24/29 | DO_Polarity_LogicIndex_22 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Pre Heater Step 3 - DO Polarity |
| 25/29 | DO_Polarity_LogicIndex_23 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 1 - DO Polarity |
| 25/29 | DO_Polarity_LogicIndex_24 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 2 - DO Polarity |
| 26/29 | DO_Polarity_LogicIndex_25 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Post Heater Step 3 - DO Polarity |
| 26/29 | DO_Polarity_LogicIndex_27 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Humidifier - DO Polarity |
| 27/29 | DO_Polarity_LogicIndex_26 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Recovery - DO Polarity |
| 27/29 | DO_Polarity_LogicIndex_28 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Fan 2 - DO Polarity |
| 28/29 | DO_Polarity_LogicIndex_29 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Fan 2 - DO Polarity |
| 28/29 | DO_Polarity_LogicIndex_30 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Supply Damper 2 - DO Polarity |
| 29/29 | DO_Polarity_LogicIndex_31 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | Return Damper 2 - DO Polarity |

Tabella 84 - O1-Polarity

O2-Test Out

A seguire viene riportata la navigazione del menu "O2-Test Out", che consente la gestione dei test delle uscite analogiche e digitali.

|  |  | Test Out |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

I parametri del menu "O2-Test Out" dipendono dagli I/O allocati con la configurazione in uso.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | doTst_LogicIndex_0 | Boolean | 0 | — | — | — | Test DO - Supply Fan |
| - - - | aoTst_LogicIndex_0 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Supply Fan |
| - - - | doTst_LogicIndex_28 | Boolean | 0 | — | — | — | Test DO - Supply Fan 2 |
| - - - | doTst_LogicIndex_1 | Boolean | 0 | — | — | — | Test DO - Return Fan |
| - - - | aoTst_LogicIndex_1 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Return Fan |
| - - - | doTst_LogicIndex_29 | Boolean | 0 | — | — | — | Test DO - Return Fan 2 |
| - - - | doTst_LogicIndex_2 | Boolean | 0 | — | — | — | Test DO - On Off |
| - - - | doTst_LogicIndex_3 | Boolean | 0 | — | — | — | Test DO - Alarm |
| - - - | doTst_LogicIndex_4 | Boolean | 0 | — | — | — | Test DO - Mode |
| - - - | doTst_LogicIndex_5 | Boolean | 0 | — | — | — | Test DO - Ext. Dampers |
| - - - | aoTst_LogicIndex_2 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Ext. Dampers |
| - - - | doTst_LogicIndex_6 | Boolean | 0 | — | — | — | Test DO - Bypass Damper |
| - - - | aoTst_LogicIndex_3 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Bypass Damper |
| - - - | doTst_LogicIndex_7 | Boolean | 0 | — | — | — | Test DO - Supply Damper |
| - - - | doTst_LogicIndex_30 | Boolean | 0 | — | — | — | Test DO - Supply Damper 2 |
| - - - | doTst_LogicIndex_8 | Boolean | 0 | — | — | — | Test DO - Return Damper |
| - - - | doTst_LogicIndex_31 | Boolean | 0 | — | — | — | Test DO - Return Damper 2 |
| - - - | doTst_LogicIndex_9 | Boolean | 0 | — | — | — | Test DO - Pump Preheat |
| - - - | doTst_LogicIndex_10 | Boolean | 0 | — | — | — | Test DO - Pump Postheat |
| - - - | doTst_LogicIndex_11 | Boolean | 0 | — | — | — | Test DO - Cool/CH Pump |
| - - - | doTst_LogicIndex_12 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 1 |
| - - - | doTst_LogicIndex_13 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 2 |
| - - - | doTst_LogicIndex_14 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 3 |
| - - - | doTst_LogicIndex_15 | Boolean | 0 | — | — | — | Test DO - Cool/CH Step 4 |
| - - - | doTst_LogicIndex_16 | Boolean | 0 | — | — | — | Test DO - Heat Pump |
| - - - | doTst_LogicIndex_17 | Boolean | 0 | — | — | — | Test DO - Heater Step 1 |
| - - - | doTst_LogicIndex_18 | Boolean | 0 | — | — | — | Test DO - Heater Step 2 |
| - - - | doTst_LogicIndex_19 | Boolean | 0 | — | — | — | Test DO - Heater Step 3 |
| - - - | doTst_LogicIndex_20 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 1 |
| - - - | doTst_LogicIndex_21 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 2 |
| - - - | doTst_LogicIndex_22 | Boolean | 0 | — | — | — | Test DO - Pre Heater Step 3 |
| - - - | doTst_LogicIndex_23 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 1 |
| - - - | doTst_LogicIndex_24 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 2 |
| - - - | doTst_LogicIndex_25 | Boolean | 0 | — | — | — | Test DO - Post Heater Step 3 |
| - - - | doTst_LogicIndex_26 | Boolean | 0 | — | — | — | Test DO - Humidifier |
| - - - | doTst_LogicIndex_27 | Boolean | 0 | — | — | — | Test DO - Rotary Wheel / Exchanger |
| - - - | aoTst_LogicIndex_9 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Humidifier |
| - - - | aoTst_LogicIndex_8 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Rotary Wheel / Exchanger |
| - - - | aoTst_LogicIndex_4 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Cool - C/H Valve |
| - - - | aoTst_LogicIndex_5 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Heat Valve |
| - - - | aoTst_LogicIndex_6 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Pre Heater |
| - - - | aoTst_LogicIndex_7 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO - Post Heater |
| - - - | aoTst_LogicIndex_10 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 1 |
| - - - | aoTst_LogicIndex_11 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 2 |
| - - - | aoTst_LogicIndex_12 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 3 |
| - - - | aoTst_LogicIndex_13 | Signed 16-bit | 0 | 0 | 1000 | % | Test AO – Cond Unit 4 |

Tabella 85 - O2-Test Out

O3-I/O Allocation

A seguire viene riportata la navigazione del menu "O3-I/O Allocation", che consente la gestione delle allocazioni di ingressi e uscite.

|  |  | Allocate |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

NOTA (1): Il parametro AllocationCmdSet corrisponde alla pagina del menu "O3-IO Allocation" sopra riportata e consente la gestione delle allocazioni di ingressi e uscite analogiche e digitali, come descritto nella seguente tabella.

| Tasto | Descrizione |
| --- | --- |
| AI | Tasto di accesso al sottomenu "AI" |
| DI | Tasto di accesso al sottomenu "DI" |
| AO | Tasto di accesso al sottomenu "AO" |
| DO | Tasto di accesso al sottomenu "DO" |
| Auto | Comando di allocazione automatica |
| Save | Comando di salvataggio su EEProm dell'allocazione impostata |
| Clear | Comando di cancellazione dell'allocazione impostata |
| Reload | Comando di reload dell'allocazione |

Tabella 86 - Descrizione del menu "O3-IO Allocation"

I parametri del menu "O3-I/O Allocation" relativi agli ingressi analogici sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | — | Allocation command |
| 1/35 | ioSV_base_AI_01 | -1 = -1=Not Used; 0=Supply Temp.; 1=Return Temp.; 2=External Temp.; 3=Expulsion Temp.; 4=Preheat Temp.; 5=Saturation Temp.; 6=Antifreeze; 7=Air Quality CO2; 8=Air Quality VOC; 9=Pressure 1; 10=Pressure 2; 11=Supply Hum.; 12=Return Hum.; 13=External Hum.; 14=Flow Tuning 1; 15=Flow Tuning 2 | -1 | -1 | 15 | — | Temporary: Logic Allocation of the physical input |
| 1/35 | ioSV_base_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | Save command required to be effective |
| 2/35 | ioSV_base_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 2/35 | ioSV_base_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 3/35 | ioSV_base_AI_05 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 3/35 | ioSV_base_AI_06 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 4/35 | ioSV_base_AI_07 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 4/35 | ioSV_base_AI_08 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 5/35 | ioSV_base_AI_09 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 5/35 | ioSV_base_AI_10 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 6/35 | ioSV_base_AI_11 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 6/35 | ioSV_base_AI_12 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 7/35 | ioSV_exp1_AI_01 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 7/35 | ioSV_exp1_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 8/35 | ioSV_exp1_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 8/35 | ioSV_exp1_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 9/35 | ioSV_exp2_AI_01 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 9/35 | ioSV_exp2_AI_02 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 10/35 | ioSV_exp2_AI_03 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 10/35 | ioSV_exp2_AI_04 | See ioSV_base_AI_01 | -1 | -1 | 15 | — | — |
| 11/35 | ioSV_base_AI_0102 | 0=NTC(NK103); 2=NTC(103AT); 3=4...20mA; 4=0-10V; 5=Ratiometric; 6=PT1000; 9=PTC; 10=0-5V; 11=0...20mA | 2 | 0 | 11 | — | Temporary: AI probe configuration |
| 11/35 | ioSV_base_AI_0304 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | Save command required to be effective |
| 12/35 | ioSV_base_AI_0506 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | — |
| 12/35 | ioSV_base_AI_0708 | See ioSV_base_AI_0102 | 4 | 0 | 11 | — | — |
| 13/35 | ioSV_base_AI_0910 | See ioSV_base_AI_0102 | 2 | 0 | 11 | — | — |
| 13/35 | ioSV_base_AI_1112 | See ioSV_base_AI_0102 | 4 | 0 | 11 | — | — |
| 14/35 | ioSV_exp1_AI_0102 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 14/35 | ioSV_exp1_AI_0304 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 15/35 | ioSV_exp2_AI_0102 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 15/35 | ioSV_exp2_AI_0304 | See ioSV_base_AI_0102 |  | 0 | 11 | — | — |
| 16/35 | ioSV_base_AI01_min | Signed 16-bit | 0 | — | — | digit | Temporary: AI ranges |
| 16/35 | ioSV_base_AI01_max | Unsigned 16-bit | 1000 | — | — | digit | Save command required to be effective |
| 17/35 | ioSV_base_AI02_min | Signed 16-bit | 0 | — | — | digit | — |
| 17/35 | ioSV_base_AI02_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 18/35 | ioSV_base_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 18/35 | ioSV_base_AI03_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 19/35 | ioSV_base_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 19/35 | ioSV_base_AI04_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 20/35 | ioSV_base_AI05_min | Signed 16-bit | 0 | — | — | digit | — |
| 20/35 | ioSV_base_AI05_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 21/35 | ioSV_base_AI06_min | Signed 16-bit | 0 | — | — | digit | — |
| 21/35 | ioSV_base_AI06_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 22/35 | ioSV_exp1_AI01_min | Signed 16-bit | -500 | — | — | digit | — |
| 22/35 | ioSV_exp1_AI01_max | Signed 16-bit | 1100 | — | — | digit | — |
| 23/35 | ioSV_exp1_AI02_max | Signed 16-bit | 1100 | — | — | digit | — |
| 23/35 | ioSV_exp1_AI02_min | Signed 16-bit | -500 | — | — | digit | — |
| 24/35 | ioSV_exp1_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 24/35 | ioSV_exp1_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 25/35 | ioSV_exp1_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 25/35 | ioSV_exp1_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |
| 26/35 | ioSV_base_AI07_min | Signed 16-bit | 0 | — | — | digit | — |
| 26/35 | ioSV_base_AI07_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 27/35 | ioSV_base_AI08_min | Signed 16-bit | 0 | — | — | digit | — |
| 27/35 | ioSV_base_AI08_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 28/35 | ioSV_base_AI09_min | Signed 16-bit | 0 | — | — | digit | — |
| 28/35 | ioSV_base_AI09_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 29/35 | ioSV_base_AI10_min | Signed 16-bit | 0 | — | — | digit | — |
| 29/35 | ioSV_base_AI10_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 30/35 | ioSV_base_AI11_min | Signed 16-bit | 0 | — | — | digit | — |
| 30/35 | ioSV_base_AI11_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 31/35 | ioSV_base_AI12_min | Signed 16-bit | 0 | — | — | digit | — |
| 31/35 | ioSV_base_AI12_max | Unsigned 16-bit | 1000 | — | — | digit | — |
| 32/35 | ioSV_exp1_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 32/35 | ioSV_exp1_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 33/35 | ioSV_exp1_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 33/35 | ioSV_exp1_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |
| 34/35 | ioSV_exp2_AI03_min | Signed 16-bit | 0 | — | — | digit | — |
| 34/35 | ioSV_exp2_AI03_max | Signed 16-bit | 1000 | — | — | digit | — |
| 35/35 | ioSV_exp2_AI04_min | Signed 16-bit | 0 | — | — | digit | — |
| 35/35 | ioSV_exp2_AI04_max | Signed 16-bit | 1000 | — | — | digit | — |

Tabella 87 - O3-I/O Allocation per ingressi analogici

I parametri del menu "O3-I/O Allocation" relativi agli ingressi digitali sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/10 | ioSV_base_DI_01 | -1 = -1=Not Used; 0=Supply Fan Th.Prot.; 1=Return Fan Th.Prot.; 2=On Off; 3=Fire Alarm; 4=Mode; 5=Door; 6=Antifreeze Alarm; 7=Airflow Alarm Supply; 8=Airflow Alarm Return; 9=Humidifier Alarm; 10=Pre Heater Alarm 11=Post Heater Alarm 12=Rotary Heat Exch. Alarm 13=Filter 1 Alarm 14=Filter 2 Alarm 15=Filter 3 Alarm 16=Filter 4 Alarm 17=Supply Fan 2 Th.Prot. 18=Return Fan 2 Th.Prot. 19=Supply Fan 2 Airflow Alarm 20=Return Fan 2 Airflow Alarm 21=Cond. Unit Alarm 22=Heater Alarm 23=Cond. Unit 2 Alarm 24=Cond. Unit 3 Alarm 25=Cond. Unit 4 Alarm 26=Cond. Unit 1 Defrost 27=Cond. Unit 2 Defrost 28=Cond. Unit 3 Defrost 29=Cond. Unit 4 Defrost 30=Filter 5 Alarm | -1 | -1 | 10 | — |
| 1/10 | ioSV_base_DI_02 | See ioSV_base_DI_01 | -1 | -1 | 10 | — |
| 2/10 | ioSV_base_DI_03 |  | -1 | -1 | 10 | — |
| 2/10 | ioSV_base_DI_04 |  | -1 | -1 | 10 | — |
| 3/10 | ioSV_base_DI_05 |  | -1 | -1 | 10 | — |
| 3/10 | ioSV_base_DI_06 |  | -1 | -1 | 10 | — |
| 4/10 | ioSV_base_DI_07 |  | -1 | -1 | 10 | — |
| 4/10 | ioSV_base_DI_08 |  | -1 | -1 | 10 | — |
| 5/10 | ioSV_base_DI_09 |  | -1 | -1 | 10 | — |
| 5/10 | ioSV_base_DI_10 |  | -1 | -1 | 10 | — |
| 6/10 | ioSV_base_DI_11 |  | -1 | -1 | 10 | — |
| 6/10 | ioSV_base_DI_12 |  | -1 | -1 | 10 | — |
| 7/10 | ioSV_exp1_DI_01 |  | -1 | -1 | 10 | — |
| 7/10 | ioSV_exp1_DI_02 |  | -1 | -1 | 10 | — |
| 8/10 | ioSV_exp1_DI_03 |  | -1 | -1 | 10 | — |
| 8/10 | ioSV_exp1_DI_04 |  | -1 | -1 | 10 | — |
| 9/10 | ioSV_exp2_DI_01 |  | -1 | -1 | 10 | — |
| 9/10 | ioSV_exp2_DI_02 |  | -1 | -1 | 10 | — |
| 10/10 | ioSV_exp2_DI_03 |  | -1 | -1 | 10 | — |
| 10/10 | ioSV_exp2_DI_04 |  | -1 | -1 | 10 | — |

Tabella 88 - O3-I/O Allocation per ingressi digitali

I parametri del menu "O3-I/O Allocation" relativi alle uscite digitali sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/10 | ioSV_base_DO_01 | -1 =Not Used; 0=Supply Fan; 1=Return Fan; 2=On Off; 3=Alarm; 4=Mode; 5=Ext. Dampers; 6=Bypass Damper; 7=Supply Damper; 8=Return Damper; 9=Pump Preheat; 10=Pump Postheat; 11=Cool / Cool-Heat Pump; 12=Cool / Cool-Heat Step 1 or Cond.Unit 1; 13=Cool / Cool-Heat Step 2 or Cond.Unit 2; 14=Cool / Cool-Heat Step 3 or Cond.Unit 3; 15=Cool / Cool-Heat Step 4 or Cond.Unit 4; 16=Heat Pump; 17=Heater Step 1; 18=Heater Step 2; 19=Heater Step 3; 20=Pre Heater Step 1; 21=Pre Heater Step 2; 22=Pre Heater Step 3; 23=Post Heater Step 1; 24=Post Heater Step 2; 25=Post Heater Step 3; 26=Humidifier; 27=Recovery; 28=Supply Fan 2; 29=Return Fan 2; 30=Supply Damper 2; 31=Return Damper 2 | -1 | -1 | 31 | Temporary: Logic Allocation of the physical output |
| 1/10 | ioSV_base_DO_02 | See ioSV_base_DO_01 | -1 | -1 | 31 | Save command required to be effective |
| 2/10 | ioSV_base_DO_03 |  | -1 | -1 | 31 | — |
| 2/10 | ioSV_base_DO_04 |  | -1 | -1 | 31 | — |
| 3/10 | ioSV_base_DO_05 |  | -1 | -1 | 31 | — |
| 3/10 | ioSV_base_DO_06 |  | -1 | -1 | 31 | — |
| 4/10 | ioSV_base_DO_07 |  | -1 | -1 | 31 | — |
| 4/10 | ioSV_base_DO_08 |  | -1 | -1 | 31 | — |
| 5/10 | ioSV_base_DO_09 |  | -1 | -1 | 31 | — |
| 5/10 | ioSV_base_DO_10 |  | -1 | -1 | 31 | — |
| 6/10 | ioSV_base_DO_11 |  | -1 | -1 | 31 | — |
| 6/10 | ioSV_base_DO_12 |  | -1 | -1 | 31 | — |
| 7/10 | ioSV_exp1_DO_02 |  | -1 | -1 | 31 | — |
| 7/10 | ioSV_exp1_DO_01 |  | -1 | -1 | 31 | — |
| 8/10 | ioSV_exp1_DO_03 |  | -1 | -1 | 31 | — |
| 8/10 | ioSV_exp1_DO_04 |  | -1 | -1 | 31 | — |
| 9/10 | ioSV_exp2_DO_01 |  | -1 | -1 | 31 | — |
| 9/10 | ioSV_exp2_DO_02 |  | -1 | -1 | 31 | — |
| 10/10 | ioSV_exp2_DO_03 |  | -1 | -1 | 31 | — |
| 10/10 | ioSV_exp2_DO_04 |  | -1 | -1 | 31 | — |

Tabella 89 - "O3-I/O Allocation" relativi alle uscite digitali

I parametri del menu "O3-I/O Allocation" relativi alle uscite analogiche sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | AllocationCmdSet (1) | 0=Idle; 1=Load Stored; 2=Auto Allocation; 3=Save into Stored; 4=Clear All; 18 = 18=Auto Allocation AI; 19 = 19=Save Allocation AI; 20 = 20=Clear AI; 34 = 34=Auto Allocation DI; 35 = 35=Save Allocation DI; 36 = 36=Clear DI; 50 = 50=Auto Allocation DO; 51 = 51=Save Allocation DO; 52 = 52=Clear DO; 66 = 66=Auto Allocation AO; 67 = 67=Save Allocation AO; 68 = 68=Clear AO | 0 | 0 | 68 | Allocation command |
| 1/5 | ioSV_base_AO_01 | -1 = Not Used; 0=Supply Fan; 1=Return Fan; 2=Ext. Dampers; 3=Byp. Damper; 4=Cool / Cool-Heat; 5=Heat; 6=Pre Heater; 7=Post Heater; 8=Recovery; 9=Humidifier 10=Cond.Unit 1 11=Cond.Unit 2 12=Cond.Unit 3 13=Cond.Unit 4 | -1 | -1 | 9 | — |
| 1/5 | ioSV_base_AO_02 | See ioSV_base_AO_01 | -1 | -1 | 9 | — |
| 2/5 | ioSV_base_AO_03 |  | -1 | -1 | 9 | — |
| 2/5 | ioSV_base_AO_04 |  | -1 | -1 | 9 | — |
| 3/5 | ioSV_base_AO_05 |  | -1 | -1 | 9 | — |
| 3/5 | ioSV_base_AO_06 |  | -1 | -1 | 9 | — |
| 4/5 | ioSV_exp1_AO_01 |  | -1 | -1 | 9 | — |
| 4/5 | ioSV_exp1_AO_02 |  | -1 | -1 | 9 | — |
| 5/5 | ioSV_exp2_AO_01 |  | -1 | -1 | 9 | — |
| 5/5 | ioSV_exp2_AO_02 |  | -1 | -1 | 9 | — |

Tabella 90 - "O3-I/O Allocation" relativi alle uscite analogiche

O4-Base AI Cfg.

|  |  | Bios AI |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O5-AO Config.

|  |  | Bios AO |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

O6-Not Allocate

|  |  | I/O Not Fully Cfg |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

P-Serial ports

Il menu "P-Serial ports" consente la gestione delle porte di comunicazione mediante i relativi tasti, come riportato nella seguente tabella.

| Porta di comunicazione | Tasto del menu "P-Serial ports" | Significato |
| --- | --- | --- |
| P1 | 485-1 | Porta di comunicazione RS485 - 1 del controllore |
| P2 | 485-2 | Porta di comunicazione RS485 - 2 del controllore |
| P3 | ETH | Porta di comunicazione Ethernet del controllore |
| P5 | BACnet | Porta di comunicazione BACnet del controllore |
| P6 | RS485 | Porta di comunicazione RS485 del plug-in |
| P7 | RS232 | Porta di comunicazione RS232 del plug-in |
| P8 | CAN | Porta di comunicazione CAN del plug-in |

Tabella 91 - Gestione delle porte di comunicazione

|  |  | 485-1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 485-2 |  |  |  |  |  |
|  |  | ETH |  |  |  |  |  |
|  |  | BACnet |  |  |  |  |  |

I parametri del menu "P5-Bacnet" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- |
| - - - | BACNET_ENABLE | Boolean | 1 | — | — | Bacnet Protocol Enable |
| - - - | BACNET_ID | Unsigned 16-bit | 1 | 1 | — | Bacnet Device ID |
| - - - | BACNET_SUBNET | Unsigned 16-bit | 0 | 0 | 63 | Bacnet Device SUBNET |
| - - - | BACNET_BBMD_Ip1 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip2 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip3 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_Ip4 | Unsigned 8-bit | 0 | — | — | BBMD Service IP - Foreing Devices Handling |
| - - - | BACNET_BBMD_TMO | Unsigned 16-bit | 60 | — | sec | BBMD Timeout - Foreing Devices Handling |

Tabella 92 - P5-Bacnet

|  |  | RS485 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | RS232 |  |  |  |  |  |
|  |  | CAN |  |  |  |  |  |

NOTA: I parametri relativi alle porte di comunicazione P1, P2, P3, P6, P7, P8 sono parametri di BIOS del controllore. Per ulteriori informazioni fare riferimento al manuale User Guide FREE Advance.

Q-USB

U-Unit Configuration

A seguire viene riportata la navigazione del menu "Unit Configuration", che consente la gestione della configurazione hardware dell'UTA.

I parametri del menu "Unit Configuration" sono riportati nella seguente tabella, suddivisi per pagina.

| Pag | Name | Device type | Def | Min | Max | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 1/14 | cfgFans | 0=Supply; 1=Supply+Return | 0 | 0 | 1 | OEM: Fan Sections |
| 1/14 | cfgFanType | 0=On Off; 1=Modulating; 2=On Off Backup; 3=Modulating Backup; 4=ATV; 5=ATV Backup; 6=EBM; 7=EBM Backup; 8=Ziehl; 9=Ziehl Backup | 0 | 0 | 9 | OEM: Fan Type |
| 2/14 | cfgFanRegulation | 0=Fixed Speed; 1=Air Quality; 2=Pressure 1 Probe; 3=Pressure 2 Probes | 0 | 0 | 3 | OEM: Fan Regulator |
| 2/14 | cfgFanAlarm | 0=Thermal/Digital Protection; 1=Digital+Flowswitch | 0 | 0 | 1 | OEM: Fan Alarm Selection |
| 3/14 | cfgCoolHeatModules | 0=None; 1=Cool; 2=Heat; 3=Cool+Heat; 4=Cool/Heat Single out | 0 | 0 | 4 | OEM: Heating Cooling Enable |
| 5/14 | cfgPreHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Preheater Selection |
| 3/14 | cfgCooling | 0=Modulating Valve; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | OEM: Cooling Actuator Selection |
| 4/14 | cfgHeating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Heating Actuator Selection |
| 4/14 | cfgCooling_Heating | 0=Modulating Valve; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | OEM: Cooling+Heating Actuator Selection |
| 5/14 | cfgPostHeating | 0=None; 1=Modulating Valve; 2=Mod.Valve+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | OEM: Postheater Selection |
| 6/14 | cfgAntifreeze | 0=None; 1=On Off; 2=NTC | 0 | 0 | 2 | OEM: Antifreeze Selection |
| 6/14 | cfgHeatRecovery | 0=None; 1=Bypass On Off; 2=Bypass Mod; 3=Rotary On Off; 4=Rotary Mod; 5=Exchanger On Off; 6=Exchanger Mod | 0 | 0 | 6 | OEM: Heat Recovery Selection |
| 7/14 | cfgDefrostHeatRec | 0=None; 1=Supply Fans; 2=Preheating | 0 | 0 | 2 | OEM: Defrost Regulation Selection |
| 7/14 | cfgDampers | 0=None; 1=External On Off; 2=External + Mix Mod | 1 | 0 | 2 | OEM: External Dampers Selection |
| 8/14 | cfgHumidifier | 0=None; 1=On Off; 2=Modulating | 0 | 0 | 2 | OEM: Humidifier Selection |
| 8/14 | cfgDeHumidifier | 0=None; 1=Standard; 2=Dew Point; 3=Standard+Winter; 4=Dew Point+Winter | 0 | 0 | 4 | OEM: Dehumification Regulator |
| 9/14 | cfgDampersForFans | 0=None; 1=Supply; 2=Return; 3=Supply+Return | 0 | 0 | 3 | OEM: Dampers for fam Selection |
| 9/14 | cfgAirQuality | 0=None; 1=CO2; 2=VOC; 3=CO2+VOC | 0 | 0 | 3 | OEM: Air Quality Probe Selection |
| 10/14 | cfgFilterPressostat | Unsigned 8-bit | 0 | 0 | 5 | OEM: Number of filter pressostat |
| 10/14 | cfgDoorDI | Boolean | 0 | — | — | OEM: Door Input Enable |
| 11/14 | cfgModeDI | Boolean | 0 | — | — | OEM: Unit Mode Input Enable |
| 11/14 | cfgModeDO | Boolean | 0 | — | — | OEM: Unit Mode Output Enable |
| 12/14 | cfgCoolHeat_NumSteps | 0=1 Cond Unit – AO 1=1 Cond Unit - 1 Step+AO 2=1 Cond Unit - 2 Steps 3=1 Cond Unit - 3 Steps 4=1 Cond Unit - 4 Steps 16=2 Cond Units 32=3 Cond Units 64=4 Cond Units | 0 | 0 | 48 | OEM: Condensing Unit Steps |
| 12/14 | cfgHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Heater Steps |
| 13/14 | cfgPreHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Pre Heater Steps |
| 13/14 | cfgPostHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | OEM: Electric Post Heater Steps |
| 14/14 | cfgMixChamberBeforePreHeat | Boolean | 0 | — | — | OEM: If enabled dampers closed with PreAntifreeze and Defrost with PreHeating |
|  | CfgParallelFans | Unsigned 8-bit | 1 | 1 | 3 | OEM: Number of parallel fans (Ziehl only) |

Tabella 93 - Unit Configuration

W-Password

Datalogger

Il controllore permette il salvataggio dei dati su MicroSD.

A seguire sono riportate alcune indicazioni per il corretto uso della MicroSD sul controllore.

È vietato rimuovere la MicroSD senza averla precedentemente smontata (fare riferimento a 4 Menu Impostazioni Utente a pag. 55) e aver precedentemente disabilitato il data-logging per evitare una segnalazione di errore.

È obbligatorio montare la MicroSD in caso venga inserita nel controllore già acceso (fare riferimento a 4 Menu Impostazioni Utente a pag. 55).

È vietato utilizzare MicroSD con più di 500 file memorizzati.

La MicroSD deve essere formattata FAT32.

Se abilitato, il salvataggio dei dati su MicroSD inizia 1 minuto dopo il boot. I dati salvati su MicroSD sono:

lo stato degli allarmi;

i dati riportati nella seguente tabella:

| Dato salvato su MicroSD | Descrizione |
| --- | --- |
| On/Off | Stato UTA |
| Set T. | Setpoint di temperatura |
| Set RH | Setpoint di umidità |
| Set CO2 | Setpoint di qualità aria per sonda CO2 |
| Set VOC | Setpoint di qualità aria per sonda VOC |
| Supply T. | Temperatura della sonda mandata |
| Return T. | Temperatura della sonda ripresa |
| Ext.T. | Temperatura della sonda esterna |
| Exp.T. | Temperatura della sonda espulsione |
| Preheat T. | Temperatura della sonda preriscaldo |
| Sat. T. | Temperatura della sonda saturazione |
| Af T. | Temperatura della sonda antigelo |
| CO2 | Sonda CO2 |
| VOC | Sonda VOC |
| Supply Pr. | Sonda mandata |
| Return Pr. | Sonda ripresa |
| Supply Hum. | Umidità della sonda mandata |
| Return Hum. | Umidità della sonda ripresa |
| Ext.Hum. | Umidità della sonda esterna |
| Mode | Modo Corrente: 0=Cooling 1=Heating |
| Supply Fan | Velocità Ventola Mandata |
| Return Fan | Velocità Ventola Ripresa |
| Ext.Damper | Uscita Serranda Esterna |
| Recovery | Uscita Recuperatore |
| Free C. | Stato Free Cooling |
| Free H. | Stato Free Heating |
| Off by FC | Attuatori Off per Free Cooling/Heating |
| Heat | Uscita Attuatore Riscaldamento |
| Cool | Uscita Attuatore Raffrescamento |
| Pre Heat | Uscita Attuatore Preriscaldo |
| Post Heat | Uscita Attuatore Postriscaldo |
| Humidifier | Uscita Umidificatore |
| PID Cool | Richiesta PID Raffrescamento |
| PID Heat | Richiesta PID Riscaldamento |
| PID Air Q. | Richiesta PID Qualità dell’aria |
| Dehum. Req. | Richiesta Deumidificazione |
| Defrost Fan | Stato Sbrinamento con Ventilazione |

Tabella 94 - Dati salvati su MicroSD

Protocolli BMS

I protocolli BMS disponibili sono:

Modbus RTU;

Modbus TCP.

Bacnet;

Nel protocollo Modbus la modalità bridge è attiva verso tutti gli slave abilitati se il display non è nel menu S7-Modbus Scan per la gestione del Modbus master (fare riferimento a 4.8.1.7 S7-Modbus Scan a pag. 95).

Modbus RTU

NOTA: I parametri relativi al protocollo Modbus RTU sono parametri di BIOS del controllore. Per ulteriori informazioni fare riferimento al manuale User Guide FREE Advance e a 11 Tabelle Modbus a pag. 134, 8 Allarmi a pag. 125 per gli indirizzi dei registri Modbus che si possono leggere e scrivere.

Modbus TCP

NOTA: I parametri relativi al protocollo Modbus TCP sono parametri di BIOS del controllore. Per ulteriori informazioni fare riferimento al manuale User Guide FREE Advance e a 11 Tabelle Modbus a pag. 134, 8 Allarmi a pag. 125 per gli indirizzi dei registri Modbus che si possono leggere e scrivere.

Bacnet

Le caratteristiche relative al protocollo Bacnet sono riportate nella seguente tabella.

| Profilo | Controllore AAC |
| --- | --- |
| Porta | Su porta Ethernet o in alternativa esclusiva Bacnet MS/TP su porta RS485-1 (fare riferimento a 4.8.3 P-Serial Ports a pag. 109). |

Tabella 95 - Caratteristiche relative al protocollo Bacnet

Gli oggetti relativi al protocollo Bacnet sono riportati nella seguente tabella.

| Object name | Object type | Object instance | Description | Supports COV |
| --- | --- | --- | --- | --- |
| Supply Temperature | AI | 0 | Supply Temperature | Y |
| Return Temperature | AI | 1 | Return Temperature | Y |
| External Temperature | AI | 2 | External Temperature | Y |
| Expulsion Temperature | AI | 3 | Expulsion Temperature | Y |
| Preheating Temperature | AI | 4 | Preheating Temperature | Y |
| Saturation Temperature | AI | 5 | Saturation Temperature | Y |
| Antifreeze Temperature | AI | 6 | Antifreeze Temperature | Y |
| Air Quality CO2 | AI | 7 | Air Quality CO2 | Y |
| Air Quality VOC | AI | 8 | Air Quality VOC | Y |
| Supply Ventilation | AI | 9 | Supply Pressure or Flow | Y |
| Return Ventilation | AI | 10 | Return Pressure or Flow | Y |
| Supply Humidity | AI | 11 | Supply Humidity | Y |
| Return Humidity | AI | 12 | Return Humidity | Y |
| External Humidity | AI | 13 | External Humidity | Y |
| Supply Flow Tuning | AI | 14 | Supply Flow Tuning | Y |
| Return Flow Tuning | AI | 15 | Return Flow Tuning | Y |
| BAI16 | AI | 16 | Future Use | Y |
| Set Comfort Cool | AV | 17 | Set Comfort Cool | Y |
| Set Comfort Heat | AV | 18 | Set Comfort Heat | Y |
| Set Eco Cool | AV | 19 | Set Eco Cool | Y |
| Set Eco Heat | AV | 20 | Set Eco Heat | Y |
| Set Auto | AV | 21 | Set Auto | Y |
| Set Comfort Humidification | AV | 22 | Set Comfort Humidification | Y |
| Set Comfort DeHumidification | AV | 23 | Set Comfort DeHumidification | Y |
| Set Eco Humidification | AV | 24 | Set Eco Humidification | Y |
| Set Ecot DeHumidification | AV | 25 | Set Ecot DeHumidification | Y |
| Set CO2 | AV | 26 | Set CO2 | Y |
| Set VOC | AV | 27 | Set VOC | Y |
| Damper Position | AI | 28 | Damper Position | Y |
| Fan Supply Speed | AI | 29 | Fan Supply Speed | Y |
| Fan Return Speed | AI | 30 | Fan Return Speed | Y |
| Cooling Actuator | AI | 31 | Cooling Actuator | Y |
| Heating Actuator | AI | 32 | Heating Actuator | Y |
| PreHeating Actuator | AI | 33 | PreHeating Actuator | Y |
| PostHeating Actuator | AI | 34 | POstHeating Actuator | Y |
| Heat-Cool Recovery Request | AI | 35 | Heat-Cool Recovery Request | Y |
| Humidifier Actuator | AI | 36 | Humidifier Actuator | Y |
| On/Off Unit | BV | 0 | On Off Unit | N |
| Unit Alarm | BV | 1 | Unit Alarm | N |
| Unit Blocking Alarm | BV | 2 | Unit Blocking Alarm | N |
| Fire Alarm | BV | 3 | Unit Fire Alarm | N |
| Alarms Reset Request | BV | 4 | Alarms Reset Request |  |
| Unit Mode | MSV | 0 | Season Mode | N |
| Unit Set Mode | MSV | 2 | Setpoint Mode | N |
| Unit Current Mode | MSI | 1 | Season Mode | N |
| Unit Status | MSV | 3 | On Off Standby Unit | N |
| NC0 | NC | 0 | NC0 | N |
| NC1 | NC | 1 | NC1 | N |
| NC2 | NC | 2 | NC2 | N |
| NC3 | NC | 3 | NC3 | N |
| AHU_<subnet>_<id> | Device | 0 | — | N |

Tabella 96 - Oggetti relativi al protocollo Bacnet

Se un oggetto non è abilitato, l’applicativo ne forza lo stato a "out of service".

L’unità di misura degli AI Supply, Return Ventilation, Supply Flow Tuning e Return Flow Tuning è impostabile in Pascal (53) o m3/h (135).

Web Server

Il Web Server è un'applicazione software che consente di gestire l'UTA. È suddivisa nelle seguenti schermate:

- Home

  - Settings

  - Weekly Scheduler

  - Event Scheduler

- State

  - IOs

  - Alarms and Historical

- Log

  - Logged File

  - Trend.

La schermata Home permette di configurare dinamicamente il sinottico dell'UTA, gestire le principali funzioni, tra cui lo stato ON/OFF dell'UTA e il cambio modo estate/inverno, e visualizzare lo stato delle sonde e degli allarmi.

Fig 14 - Schermata Home

Fig 15 - Visualizzazione Mobile

La schermata Settings permette di configurare i setpoint.

Fig 16 - Schermata Settings

La schermata Weekly Scheduler permette la configurazione degli eventi settimanali.

Fig 17 – Weekly Scheduler

La schermata Event Scheduler permette di definire gli eventi annuali e associarli ad uno dei profili predefiniti.

Fig 18 – Event Scheduler

La schermata Alarms permette di visualizzare la lista relativa allo stato degli allarmi e lo storico allarmi.

Fig 19 - Schermata Alarms

Le pagine di Log permettono la visualizzazione lo scaricamento dei file memorizzati e la visualizzazione dei log mensili.

Fig 20 - Schermata Logged Files

Fig 21 - Schermata Trends

Allarmi

Nella seguente tabella sono descritti gli allarmi che possono verificarsi.

| Modbus Register | Descrizione | Effetto | Riarmo | Ritardo |
| --- | --- | --- | --- | --- |
| 9520 | Alarm reset request command via Modbus | — | — | — |
| 9521 | Al01-Supply Temperature Probe Error | Force Stop Unit | Auto | — |
| 9522 | A02-Return Temperature Probe Error | Force supply temperature regulation Disable Winter Dehumidification | Auto | — |
| 9523 | A03-External Temperature Probe Error | Disable FreeCooling FreeHeating Disable Recovery | Auto | — |
| 9524 | A04-Expulsion Temperature Probe Error | Disable Defrost Recovery | Auto | — |
| 9525 | A05-Preheating Temperature Probe Error | Disable Preheating Actuators | Auto | — |
| 9526 | A06-Saturation Temperature Probe Error | Disable Dewpoint Dehumidification | Auto | — |
| 9527 | A07-Antifreeze Temperature Probe Error | Disable Antifreeze alarm When unit is on, open all the valves | Auto | — |
| 9528 | A08-CO2 Probe Error | Disable Air quality regulator | Auto | Delayed |
| 9529 | A09-Supply Pressure Probe Error | If 2 pressure probes enabled, uses single pressure probe regulation Otherwise uses fixed speed regulation | Auto | Delayed |
| 9530 | A10-Return Pressure Probe Error | If 2 pressure probes enabled, uses single pressure probe regulation Otherwise uses fixed speed regulation | Auto | Delayed |
| 9531 | A11-Hum. Supply Probe Error | Disable Humidification | Auto | Delayed |
| 9532 | A12-Hum. Return Probe Error | Disable Humidification and Dehumidification | Auto | Delayed |
| 9533 | A13-VOC Probe Error | Disable Air quality regulator | Auto | Delayed |
| 9534 | A14-Hum. External Probe Error | Disable Winter Dehumidification | Auto | Delayed |
| 9546 | A26-Supply Airflow by Probe | Force stop unit if backup fans are not available | Manual | Delay at fan start |
| 9547 | A27-Return Airflow by Probe | Force stop unit if backup fans are not available | Manual | Delay at fan start |
| 9548 | A28-Airflow Prb Sup.2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9549 | A29-Airflow Prb Ret.2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9550 | A30-Fan Supply | Force stop unit if backup fans are not available | Manual | — |
| 9551 | A31-Fan Return | Force stop unit if backup fans are not available | Manual | — |
| 9552 | A32-Fire | Refer to 8.1 Allarme incendio a pag. 127 | Manual | — |
| 9553 | A33-Door | Force Stop Unit | Manual | — |
| 9554 | A34-Antifreeze | Force Off Unit Enabled only in heating mode | Auto | Delayed if preheating enabled |
| 9555 | A35-Airflow Supply | Force stop unit if backup fans are not available | Manual | — |
| 9556 | A36-Airflow Return | Force stop unit if backup fans are not available | Manual | — |
| 9557 | A37-Humidifier | Disable Humidification | Manual | — |
| 9558 | A38-Preheater | Disable Preheating Electric Heaters | Manual | — |
| 9559 | A39-Heater | Disable Electric Heaters | Manual | — |
| 9560 | A40-Postheater | Disable Post Electric Heaters | Manual | — |
| 9561 | A41-Recovery | Disable Heat Recovery | Manual | — |
| 9562 | A42-Filter 1 | --- | Manual | — |
| 9563 | A43-Filter 2 | --- | Manual | — |
| 9564 | A44-Filter 3 | --- | Manual | — |
| 9565 | A45-Filter 4 | --- | Manual | — |
| 9566 | A46-Fan Supply 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9567 | A47-Fan Return 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9568 | A48-Airflow Supply 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9569 | A49-Airflow Return 2 | Force stop unit if main fans are not available | Manual | Delay at fan start |
| 9570 | A50-Cond. Unit | Disable Condensing Unit | Manual | — |
| 9571 | A51-Real Time Clock | Disable Time and Events | Manual | — |
| 9572 | A52-Fan Maintenance | Force stop unit | Auto | — |
| 9573 | A53-Modbus Fan Config. Timeout | Force stop unit | Manual | — |
| 9574 | A54-Modbus Fan Supply Communication | Force stop unit if backup fans are not available | Manual | — |
| 9575 | A55-Modbus Fan Return Communication | Force stop unit if backup fans are not available | Manual | — |
| 9576 | A56-Modbus Fan Supply 2 Communication | Force stop unit if backup fans are not available | Manual | — |
| 9577 | A57-Modbus Fan Return 2 Communication | Force stop unit if backup fans are not available | Manual | — |
| 9578 | Al58_Filter5 | --- | Manual | — |
| 9580 | A60-Log Error | Disable Datalogging | Manual | — |
| 9581 | A61-Can Expansion 1 | Force Stop Unit | Manual | — |
| 9582 | A62-Can Expansion 2 | Force Stop Unit | Manual | — |
| 9586 | Al66_CondUnit2 | Disable Condensing Unit 2 | Manual | — |
| 9587 | Al67_CondUnit3 | Disable Condensing Unit 3 | Manual | — |
| 9588 | Al68_CondUnit4 | Disable Condensing Unit 4 | Manual | — |
| 9619 | Al99-Fan Supply 1b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9620 | Al100-Fan Supply 1c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9621 | Al101-Fan Return 1b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9622 | Al102-Fan Return 1c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9623 | Al103-Fan Supply 2b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9624 | Al104-Fan Supply 2c Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9625 | Al105-Fan Return 2b Com Alarm | Force stop unit if backup fans are not available | Manual |  |
| 9626 | Al106-Fan Return 2c Com Alarm | Force stop unit if backup fans are not available | Manual |  |

Tabella 97 - Allarmi

NOTA: I seguenti allarmi non hanno alcun effetto sull'UTA ma sono esclusivamente segnalati:

A42-Filter 1;

A43-Filter 2;

A44-Filter 3;

A45-Filter 4.

A58-Filter 5.

NOTA: Negli allarmi con ritardo di tipo "Delayed", l'allarme si attiva dopo un ritardo di tempo rispetto all'evento che lo ha generato.

NOTA: Negli allarmi con ritardo di tipo "Delay at fan start", l'allarme può attivarsi esclusivamente dopo l'accensione dei ventilatori.

Allarme incendio

L'allarme incendio è gestito mediante ingresso digitale.

In caso di incendio può essere configurata una delle seguenti azioni per l'UTA:

arresto;

apertura delle serrande e forzatura dei ventilatori a velocità massima;

apertura delle serrande e forzatura del solo ventilatore ripresa a velocità massima.

Allarme sonda qualità aria

La sonda qualità aria è gestita mediante ingresso analogico 0-10 V.

L'allarme sonda qualità aria si ha quando l'ingresso analogico acquisisce un segnale inferiore:

al parametro Alm_MinCO2Sens, in caso di sonda CO2,

al parametro Alm_MinVOCSens, in caso di sonda VOC

per un tempo superiore al timeout, dato dal parametro Alm_ActiveProbeBypass.

In caso di allarme sonda qualità aria, i ventilatori si portano a velocità massima.

Allarme sonda pressione

La sonda pressione è gestita mediante ingresso analogico 0-10 V.

L'allarme sonda pressione si ha se sono contemporaneamente soddisfatte le seguenti condizioni:

l'ingresso analogico acquisisce un segnale inferiore al parametro Fan_SupplyAirflowAlrmByAi per un tempo superiore al timeout dato dal parametro Alm_ActiveProbeBypass;

i ventilatori sono accesi.

In caso di allarme sonda pressione, i ventilatori si portano a velocità massima.

Allarme flusso aria

L’allarme flusso aria può essere abilitato in caso di presenza della sonda di pressione differenziale, l’allarme è disabilitato durante la procedura di spegnimento.

In caso di allarme flusso aria, viene arrestata l'UTA.

Allarme protezione ventilatori

L'allarme protezione ventilatori è relativo sia al ventilatore mandata sia al ventilatore ripresa.

In caso di ventilatori con ingressi fisici, l'allarme protezione ventilatori è gestito mediante ingresso digitale. L'allarme protezione ventilatori viene generato anche in caso di ventilatori Modbus.

Il riarmo dopo allarme protezione ventilatori è manuale.

Se i ventilatori di backup non sono presenti, al verificarsi dell'allarme protezione ventilatori l'UTA si arresta.

Se i ventilatori di backup sono presenti, al verificarsi dell'allarme protezione ventilatori:

entrambi i ventilatori principali vengono arrestati;

- la serranda ventilatori principali viene chiusa;

la serranda ventilatori di backup viene aperta, se presente;

entrambi i ventilatori di backup vengono avviati.

In caso l'allarme protezione ventilatori sia generato dal ventilatore ripresa, viene eseguita anche la postventilazione per raffreddare le resistenze.

Al rientro dell'allarme protezione ventilatori, vengono riavviati i ventilatori principali nel caso siano soddisfatte contemporaneamente le seguenti condizioni:

parametro Fan_SwapPolicy diverso da 2;

è attivo un ventilatore principale;

è attivo un ventilatore di backup.

Viene poi attivata la coppia di ventilatori principali o la coppia di ventilatori di backup a seconda del valore del parametro Fan_SwapPolicy e delle ore di funzionamento dei ventilatori stessi.

Allarme manutenzione ventilatori

Da controllore è possibile disattivare un singolo ventilatore per poterne eseguire la manutenzione. In caso di disattivazione di entrambi i ventilatori mandata o entrambi i ventilatori ripresa compare l'allarme manutenzione ventilatori in quanto non è possibile l’avviamento dell'UTA.

L'allarme manutenzione ventilatori è a riarmo automatico.

Allarme antigelo

L'allarme antigelo può essere attivato:

da termostato, mediante ingresso digitale;

da sonda antigelo, mediante ingresso analogico.

In caso di attivazione dell'allarme antigelo da termostato, la batteria di preriscaldo viene attivata al 100% della potenza.

La gestione dell'allarme antigelo da sonda antigelo è descritta nella seguente tabella.

| Temperatura misurata dalla sonda antigelo | Tempo (in minuti) | Segnalazione antigelo | Effetti |
| --- | --- | --- | --- |
| Inferiore a setpoint + differenziale | Inferiore al parametro AFphtime | Il controllo entra in modalità "prevenzione antigelo" | - La potenza viene incrementata gradualmente mediante regolatore P con banda proporzionale pari al differenziale tra temperatura sonda antigelo e setpoint antigelo - Chiusura serrrande esterne, se parametro cfgMixChamberBeforePreHeat è abilitato |
| Superiore a setpoint + differenziale | / | Il controllo esce dalla modalità "prevenzione antigelo" | Nessuno |
| Inferiore a setpoint + differenziale | Superiore al parametro AFphtime | Allarme antigelo | - UTA in stato OFF - Apertura valvole - Chiusura serrande esterne |

Tabella 98

Gestione dell'allarme antigelo da sonda antigelo

Se il controllore entra in modalità "prevenzione antigelo":

arresta i ventilatori;

chiude le serrande;

attiva le valvole al 100%;

attiva tutte le pompe.

Il controllore esce dalla modalità "prevenzione antigelo" se la sonda antigelo torna a una temperatura superiore a setpoint + differenziale.

L’antigelo è attivo con UTA in modalità riscaldamento e in stato OFF/Standby.

L'allarme antigelo è a riarmo automatico.

Smaltimento

|  | Il prodotto deve essere smaltito separatamente secondo le norme vigenti nel Paese di installazione in materia di smaltimento delle apparecchiature elettriche ed elettroniche. |
| --- | --- |

|  | È vietato disperdere il prodotto o parti di esso nell'ambiente. Un'errato smaltimento del prodotto potrebbe causare danni all'ambiente e/o alle persone. |
| --- | --- |

Informazioni di sicurezza

AVVISO

Leggere attentamente queste istruzioni e osservare l’apparecchiatura per familiarizzare con i suoi componenti prima di procedere ad attività di installazione, uso, assistenza o manutenzione. I seguenti messaggi speciali possono comparire in diverse parti della documentazione oppure sull'apparecchiatura per segnalare rischi o per richiamare l'attenzione su informazioni che chiariscono o semplificano una procedura.

NOTA

Le operazioni di manutenzione, riparazione, installazione e uso delle apparecchiature elettriche devono essere affidate solo a personale qualificato. Schneider Electric né Eliwell non si assume alcuna responsabilità per qualsiasi conseguenza derivante dall’uso di questo materiale.

Il personale qualificato è in possesso di capacità e conoscenze specifiche sulla costruzione, il funzionamento e l’installazione di apparecchiature elettriche ed è addestrato sui criteri di sicurezza da rispettare per poter riconoscere ed evitare le condizioni a rischio.

Qualifiche del personale

Solo personale con idonea formazione e con profonda conoscenza e comprensione del contenuto del presente manuale e di ogni altra documentazione sul prodotto pertinente è autorizzato a lavorare sul e con il presente prodotto.

L'addetto qualificato deve essere in grado di individuare eventuali pericoli che possono derivare dalla parametrizzazione, dalla modifica dei valori dei parametri e in generale dall'impiego di apparecchiature meccaniche, elettriche ed elettroniche. Inoltre, deve avere familiarità con le normative, le disposizioni e regolamenti antinfortunistici, che deve rispettare mentre progetta e implementa il sistema.

Utilizzo previsto

I prodotti descritti o interessati dal presente documento, oltre a software, accessori e opzioni, sono controller, previsti per macchine HVAC commerciali secondo le istruzioni, indicazioni, esempi e informazioni di sicurezza contenute nel presente documento e altra documentazione di supporto.

Il prodotto può essere utilizzato solo in conformità con tutte le normative e direttive di sicurezza applicabili, i requisiti specificati e i dati tecnici.

Prima di utilizzare il prodotto, è necessario eseguire una valutazione del rischio in vista dell'applicazione pianificata. In base ai risultati, occorre implementare le appropriate misure correlate alla sicurezza.

Poiché il prodotto è utilizzato come componente in un processo o macchina globale, è necessario garantire la sicurezza delle persone per mezzo del progetto di tale sistema globale.

Utilizzare il prodotto solo con cavi e accessori specificati. Utilizzare solo accessori e ricambi originali.

Impieghi diversi da quelli esplicitamente consentiti sono vietati e possono provocare pericoli imprevisti.

Uso vietato

Tutti gli usi diversi da quanto espresso sopra in Uso consentito sono assolutamente vietati.

I contatti dei relé forniti sono di tipo elettromeccanico e soggetti a usura. I dispositivi di protezione di sicurezza funzionale, specificati nelle norme internazionali o locali, devono essere installati esternamente a questo dispositivo.

Responsabilità e rischi residui

La responsabilità di Eliwell Controls srl e Schneider Electric è limitata all'uso corretto e professionale di questo prodotto secondo le linee guida contenute nel presente documento e in altri documenti di supporto e non si estende ai danni provocati da (ma non limitati a):

- Uso/installazione non specificato e, in particolare, contrario ai requisiti di sicurezza della regolamentazione in vigore o specificato su questo documento;

- Utilizzo su apparecchiatura che non fornisce adeguata protezione da scosse elettriche, acqua e polvere nelle condizioni di installazione effettive;

- Utilizzo su apparecchiatura in cui è possibile accedere a componenti pericolosi senza l'uso di utensili specifici;

- Installazione/uso su apparecchiatura non conforme con norme e regolamentazione in vigore.

Smaltimento

L'apparecchiatura (o il prodotto) deve essere smaltita separatamente in conformità con le normative locali in vigore relative allo smaltimento dei rifiuti.

Schema elettrico

Fig 22 - Schema elettrico

Tabelle Modbus

NOTA: Nelle seguenti tabelle:

in caso di format XXX.Y, dividere per 10 il valore contenuto nel relativo registro;

in caso di format XX.YY, dividere per 100 il valore contenuto nel relativo registro.

Tabella Modbus EEProm

Nella seguente tabella sono descritti i parametri EEProm.

| Modbus Register | Name | Device type | Def | Min | Max | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 16384 | PSW1 | Unsigned 16-bit | 10 | — | — | — | — | Level 1 Password |
| 16385 | PSW2 | Unsigned 16-bit | 65315 | — | — | — | %x | Level 2 Password |
| 16386 | cfgFans | 0=Supply; 1=Supply+Return | 0 | 0 | 1 | — | — | OEM: Fan Sections |
| 16387 | cfgFanType | 0=On Off; 1=Modulating; 2=On Off Backup; 3=Modulating Backup; 4=ATV; 5=ATV Backup; 6=EBM; 7=EBM Backup; 8=Ziehl; 9=Ziehl Backup | 0 | 0 | 9 | — | — | OEM: Fan Type |
| 16388 | cfgFanRegulation | 0=Fixed Speed; 1=Air Quality; 2=Pressure 1 Probe; 3=Pressure 2 Probes | 0 | 0 | 3 | — | — | OEM: Fan Regulator |
| 16389 | cfgFanAlarm | 0=Thermal/Digital Protection; 1=Digital+Flowswitch | 0 | 0 | 1 | — | — | OEM: Fan Alarm Selection |
| 16390 | cfgCoolHeatModules | 0=None; 1=Cool; 2=Heat; 3=Cool+Heat; 4=Cool/Heat Single out | 0 | 0 | 4 | — | — | OEM: Heating Cooling Enable |
| 16391 | cfgCooling | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | — | — | OEM: Cooling Actuator Selection |
| 16392 | cfgHeating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Heating Actuator Selection |
| 16393 | cfgCooling_Heating | 0=Modulating; 1=Mod+Pump; 2=Cond.Unit | 0 | 0 | 2 | — | — | OEM: Cooling+Heating Actuator Selection |
| 16394 | cfgPreHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Preheater Selection |
| 16395 | cfgPostHeating | 0=None; 1=Water; 2=Water+Pump; 3=On Off Heaters; 4=Mod Heaters; 5=PWM Heaters | 0 | 0 | 5 | — | — | OEM: Postheater Selection |
| 16396 | cfgAntifreeze | 0=None; 1=On Off; 2=NTC | 0 | 0 | 2 | — | — | OEM: Antifreeze Selection |
| 16397 | cfgHeatRecovery | 0=None/Not Regulated; 1=Bypass On Off; 2=Bypass Mod; 3=Rotary On Off; 4=Rotary Mod; 5=Exchanger On Off; 6=Exchanger Mod | 0 | 0 | 6 | — | — | OEM: Heat Recovery Selection |
| 16398 | cfgDefrostHeatRec | 0=None; 1=Supply Fans; 2=Preheating | 0 | 0 | 2 | — | — | OEM: Defrost Regulation Selection |
| 16399 | cfgDampers | 0=None; 1=External On Off; 2=External + Mix Mod | 1 | 0 | 2 | — | — | OEM: External Dampers Selection |
| 16400 | cfgHumidifier | 0=None; 1=On Off; 2=Modulating | 0 | 0 | 2 | — | — | OEM: Humidifier Selection |
| 16401 | cfgDeHumidifier | 0=None; 1=Standard; 2=Dew Point; 3=Standard+Winter; 4=Dew Point+Winter | 0 | 0 | 4 | — | — | OEM: Dehumification Regulator |
| 16402 | cfgDampersForFans | 0=None; 1=Supply; 2=Return; 3=Supply+Return | 0 | 0 | 3 | — | — | OEM: Dampers for fam Selection |
| 16403 | cfgAirQuality | 0=None; 1=CO2; 2=VOC; 3=CO2+VOC | 0 | 0 | 3 | — | — | OEM: Air Quality Probe Selection |
| 16404 | cfgFilterPressostat | Unsigned 8-bit | 0 | 0 | 4 | — | — | OEM: Number of filter pressostat |
| 16405 | cfgDoorDI | Boolean | 0 | — | — | — | — | OEM: Door Input Enable |
| 16406 | cfgModeDI | Boolean | 0 | — | — | — | — | OEM: Unit Mode Input Enable |
| 16407 | cfgModeDO | Boolean | 0 | — | — | — | — | OEM: Unit Mode Output Enable |
| 16408 | cfgCoolHeat_NumSteps | 0=1 Cond Unit – AO 1=1 Cond Unit - 1 Step+AO 2=1 Cond Unit - 2 Steps 3=1 Cond Unit - 3 Steps 4=1 Cond Unit - 4 Steps 16=2 Cond Units 32=3 Cond Units 64=4 Cond Units | 0 | 0 | 48 | — | — | OEM: Condensing Unit Steps |
| 16409 | cfgHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Heater Steps |
| 16410 | cfgPreHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Pre Heater Steps |
| 16411 | cfgPostHeat_NumSteps | Unsigned 8-bit | 1 | 0 | 6 | — | — | OEM: Electric Post Heater Steps |
| 16412 | cfgMixChamberBeforePreHeat | Boolean | 0 | — | — | — | — | OEM: If enabled dampers closed with PreAntifreeze and Defrost with PreHeating |
| 16413 | cfgEE_free2 | Signed 16-bit | 0 | — | — | — | — | — |
| 16414 | cfgEE_free3 | Signed 16-bit | 0 | — | — | — | — | — |
| 16415 | cfgEE_free4 | Signed 16-bit | 0 | — | — | — | — | — |
| 16416 | cfgEE_free5 | Signed 16-bit | 0 | — | — | — | — | — |
| 16417 | cfgEE_free6 | Signed 16-bit | 0 | — | — | — | — | — |
| 16418 | cfgEE_free7 | Signed 16-bit | 0 | — | — | — | — | — |
| 16419 | cfgEE_free8 | Signed 16-bit | 0 | — | — | — | — | — |
| 16420 | ioEE_base_AI_01 | -1 = -1=Not Used; 0=Supply Temp.; 1=Return Temp.; 2=External Temp.; 3=Expulsion Temp.; 4=Preheat Temp.; 5=Saturation Temp.; 6=Antifreeze; 7=Air Quality CO2; 8=Air Quality VOC; 9=Pressure 1; 10=Pressure 2; 11=Supply Hum.; 12=Return Hum.; 13=External Hum.; 14=Flow Tuning 1; 15=Flow Tuning 2 | 0 | -1 | 15 | — | — | Saved Logic Allocation of the physical input |
| 16421 | ioEE_base_AI_02 | See ioEE_base_AI_01 | 1 | -1 | 15 | — | — | — |
| 16422 | ioEE_base_AI_03 | See ioEE_base_AI_01 | 2 | -1 | 15 | — | — | — |
| 16423 | ioEE_base_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16424 | ioEE_base_AI_05 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16425 | ioEE_base_AI_06 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16426 | ioEE_base_AI_07 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16427 | ioEE_base_AI_08 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16428 | ioEE_base_AI_09 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16429 | ioEE_base_AI_10 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16430 | ioEE_base_AI_11 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16431 | ioEE_base_AI_12 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16432 | ioEE_exp1_AI_01 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16433 | ioEE_exp1_AI_02 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16434 | ioEE_exp1_AI_03 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16435 | ioEE_exp1_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16436 | ioEE_exp2_AI_01 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16437 | ioEE_exp2_AI_02 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16438 | ioEE_exp2_AI_03 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16439 | ioEE_exp2_AI_04 | See ioEE_base_AI_01 | -1 | -1 | 15 | — | — | — |
| 16440 | ioEE_free1 | Signed 16-bit | 0 | — | — | — | — | — |
| 16441 | ioEE_free2 | Signed 16-bit | 0 | — | — | — | — | — |
| 16442 | ioEE_free3 | Signed 16-bit | 0 | — | — | — | — | — |
| 16443 | ioEE_free4 | Signed 16-bit | 0 | — | — | — | — | — |
| 16444 | ioEE_free5 | Signed 16-bit | 0 | — | — | — | — | — |
| 16445 | ioEE_free6 | Signed 16-bit | 0 | — | — | — | — | — |
| 16446 | ioEE_free7 | Signed 16-bit | 0 | — | — | — | — | — |
| 16447 | ioEE_free8 | Signed 16-bit | 0 | — | — | — | — | — |
| 16448 | ioEE_base_DI_01 | -1 = Not Used; 0=Supply Fan Th.Prot.; 1=Return Fan Th.Prot.; 2=On Off; 3=Fire Alarm; 4=Mode; 5=Door; 6=Antifreeze Alarm; 7=Airflow Alarm Supply; 8=Airflow Alarm Return; 9=Humidifier Alarm; 10=Pre Heater A 11=Post Heater Alarm 12=Rotary Heat Exch. Alarm 13=Filter 1 Alarm 14=Filter 2 Alarm 15=Filter 3 Alarm 16=Filter 4 Alarm 17=Supply Fan 2 Th.Prot. 18=Return Fan 2 Th.Prot. 19=Supply Fan 2 Airflow Alarm 20=Return Fan 2 Airflow Alarm 21=Cond. Unit Alarm 22=Heater Alarm 23=Cond. Unit 2 Alarm 24=Cond. Unit 3 Alarm 25=Cond. Unit 4 Alarm 26=Cond. Unit 1 Defrost 27=Cond. Unit 2 Defrost 28=Cond. Unit 3 Defrost 29=Cond. Unit 4 Defrost 30=Filter 5 Alarm | 2 | -1 | 30 | — | — | — |
| 16449 | ioEE_base_DI_02 | See ioEE_base_DI_01 | 3 | -1 | 10 | — | — | — |
| 16450 | ioEE_base_DI_03 | See ioEE_base_DI_01 | 0 | -1 | 10 | — | — | — |
| 16451 | ioEE_base_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16452 | ioEE_base_DI_05 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16453 | ioEE_base_DI_06 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16454 | ioEE_base_DI_07 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16455 | ioEE_base_DI_08 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16456 | ioEE_base_DI_09 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16457 | ioEE_base_DI_10 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16458 | ioEE_base_DI_11 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16459 | ioEE_base_DI_12 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16460 | ioEE_exp1_DI_01 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16461 | ioEE_exp1_DI_02 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16462 | ioEE_exp1_DI_03 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16463 | ioEE_exp1_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16464 | ioEE_exp2_DI_01 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16465 | ioEE_exp2_DI_02 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16466 | ioEE_exp2_DI_03 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16467 | ioEE_exp2_DI_04 | See ioEE_base_DI_01 | -1 | -1 | 10 | — | — | — |
| 16468 | ioEE_free9 | Signed 16-bit | 0 | — | — | — | — | — |
| 16469 | ioEE_free10 | Signed 16-bit | 0 | — | — | — | — | — |
| 16470 | ioEE_free11 | Signed 16-bit | 0 | — | — | — | — | — |
| 16471 | ioEE_free12 | Signed 16-bit | 0 | — | — | — | — | — |
| 16472 | ioEE_free13 | Signed 16-bit | 0 | — | — | — | — | — |
| 16473 | ioEE_free14 | Signed 16-bit | 0 | — | — | — | — | — |
| 16474 | ioEE_free15 | Signed 16-bit | 0 | — | — | — | — | — |
| 16475 | ioEE_free16 | Signed 16-bit | 0 | — | — | — | — | — |
| 16476 | ioEE_base_DO_01 | -1 = -1=Not Used; 0=Supply Fan; 1=Return Fan; 2=On Off; 3=Alarm; 4=Mode; 5=Ext. Dampers; 6=Bypass Damper; 7=Supply Damper; 8=Return Damper; 9=Pump Preheat; 10=Pump Postheat; 11=Cool / Cool-Heat Pump; 12=Cool/Cool-Heat Step 1 or Cond.Unit 1; 13=Cool/Cool-Heat Step 2 or Cond.Unit 2; 14=Cool/Cool-Heat Step 3 or Cond.Unit 3; 15=Cool/Cool-Heat Step 4 or Cond.Unit 4; 16=Heat Pump; 17=Heater Step 1; 18=Heater Step 2; 19=Heater Step 3; 20=Pre Heater Step 1; 21=Pre Heater Step 2; 22=Pre Heater Step 3; 23=Post Heater Step 1; 24=Post Heater Step 2; 25=Post Heater Step 3; 26=Humidifier; 27=Recovery; 28=Supply Fan 2; 29=Return Fan 2; 30=Supply Damper 2; 31=Return Damper 2 | 2 | -1 | 31 | — | — | Saved Logic Allocation of the physical output |
| 16477 | ioEE_base_DO_02 | See ioEE_base_DO_01 | 3 | -1 | 31 | — | — | — |
| 16478 | ioEE_base_DO_03 | See ioEE_base_DO_01 | 0 | -1 | 31 | — | — | — |
| 16479 | ioEE_base_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16480 | ioEE_base_DO_05 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16481 | ioEE_base_DO_06 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16482 | ioEE_base_DO_07 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16483 | ioEE_base_DO_08 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16484 | ioEE_base_DO_09 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16485 | ioEE_base_DO_10 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16486 | ioEE_base_DO_11 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16487 | ioEE_base_DO_12 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16488 | ioEE_exp1_DO_01 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16489 | ioEE_exp1_DO_02 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16490 | ioEE_exp1_DO_03 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16491 | ioEE_exp1_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16492 | ioEE_exp2_DO_01 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16493 | ioEE_exp2_DO_02 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16494 | ioEE_exp2_DO_03 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16495 | ioEE_exp2_DO_04 | See ioEE_base_DO_01 | -1 | -1 | 31 | — | — | — |
| 16496 | ioEE_free17 | Signed 16-bit | 0 | — | — | — | — | — |
| 16497 | ioEE_free18 | Signed 16-bit | 0 | — | — | — | — | — |
| 16498 | ioEE_free19 | Signed 16-bit | 0 | — | — | — | — | — |
| 16499 | ioEE_free20 | Signed 16-bit | 0 | — | — | — | — | — |
| 16500 | ioEE_free21 | Signed 16-bit | 0 | — | — | — | — | — |
| 16501 | ioEE_free22 | Signed 16-bit | 0 | — | — | — | — | — |
| 16502 | ioEE_free23 | Signed 16-bit | 0 | — | — | — | — | — |
| 16503 | ioEE_free24 | Signed 16-bit | 0 | — | — | — | — | — |
| 16504 | ioEE_base_AO_01 | -1 = -1=Not Used; 0=Supply Fan; 1=Return Fan; 2=Ext. Dampers; 3=Byp. Damper; 4=Cool / Cool-Heat; 5=Heat; 6=Pre Heater; 7=Post Heater; 8=Recovery; 9=Humidifier | -1 | -1 | 9 | — | — | — |
| 16505 | ioEE_base_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16506 | ioEE_base_AO_03 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16507 | ioEE_base_AO_04 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16508 | ioEE_base_AO_05 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16509 | ioEE_base_AO_06 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16510 | ioEE_exp1_AO_01 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16511 | ioEE_exp1_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16512 | ioEE_exp2_AO_01 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16513 | ioEE_exp2_AO_02 | See ioEE_base_AO_01 | -1 | -1 | 9 | — | — | — |
| 16514 | ioEE_free25 | Signed 16-bit | 0 | — | — | — | — | — |
| 16515 | ioEE_free26 | Signed 16-bit | 0 | — | — | — | — | — |
| 16516 | ioEE_free27 | Signed 16-bit | 0 | — | — | — | — | — |
| 16517 | ioEE_free28 | Signed 16-bit | 0 | — | — | — | — | — |
| 16518 | ioEE_free29 | Signed 16-bit | 0 | — | — | — | — | — |
| 16519 | ioEE_free30 | Signed 16-bit | 0 | — | — | — | — | — |
| 16520 | ioEE_free31 | Signed 16-bit | 0 | — | — | — | — | — |
| 16521 | ioEE_free32 | Signed 16-bit | 0 | — | — | — | — | — |
| 16522 | Cfg_exp1_AI1 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16523 | Cfg_exp1_AI2 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16524 | Cfg_exp1_AI3 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16525 | Cfg_exp1_AI4 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16526 | Cfg_exp2_AI1 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16527 | Cfg_exp2_AI2 | Unsigned 16-bit | 2 | 2 | 2 | — | — | Static Configuration |
| 16528 | Cfg_exp2_AI3 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16529 | Cfg_exp2_AI4 | Unsigned 16-bit | 4 | 4 | 4 | — | — | Static Configuration |
| 16530 | ioEE_free33 | Signed 16-bit | 0 | — | — | — | — | — |
| 16531 | ioEE_free34 | Signed 16-bit | 0 | — | — | — | — | — |
| 16532 | ioEE_free35 | Signed 16-bit | 0 | — | — | — | — | — |
| 16533 | ioEE_free36 | Signed 16-bit | 0 | — | — | — | — | — |
| 16534 | ioEE_free37 | Signed 16-bit | 0 | — | — | — | — | — |
| 16535 | ioEE_free38 | Signed 16-bit | 0 | — | — | — | — | — |
| 16536 | ioEE_free39 | Signed 16-bit | 0 | — | — | — | — | — |
| 16537 | ioEE_free40 | Signed 16-bit | 0 | — | — | — | — | — |
| 16538 | FullScaleMin_exp1_AI1 | Signed 16-bit | -500 | -500 | -500 | — | — | Saved: AI probe configuration |
| 16539 | FullScaleMax_exp1_AI1 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16540 | FullScaleMin_exp1_AI2 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16541 | FullScaleMax_exp1_AI2 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16542 | FullScaleMin_exp1_AI3 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16543 | FullScaleMax_exp1_AI3 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16544 | FullScaleMin_exp1_AI4 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16545 | FullScaleMax_exp1_AI4 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16546 | FullScaleMin_exp2_AI1 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16547 | FullScaleMax_exp2_AI1 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16548 | FullScaleMin_exp2_AI2 | Signed 16-bit | -500 | -500 | -500 | — | — | — |
| 16549 | FullScaleMax_exp2_AI2 | Signed 16-bit | 1100 | 1100 | 1100 | — | — | — |
| 16550 | FullScaleMin_exp2_AI3 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16551 | FullScaleMax_exp2_AI3 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16552 | FullScaleMin_exp2_AI4 | Signed 16-bit | 0 | -9999 | 9999 | — | — | — |
| 16553 | FullScaleMax_exp2_AI4 | Signed 16-bit | 1000 | -9999 | 9999 | — | — | — |
| 16554 | ioEE_free41 | Signed 16-bit | 0 | — | — | — | — | — |
| 16555 | ioEE_free42 | Signed 16-bit | 0 | — | — | — | — | — |
| 16556 | ioEE_free43 | Signed 16-bit | 0 | — | — | — | — | — |
| 16557 | ioEE_free44 | Signed 16-bit | 0 | — | — | — | — | — |
| 16558 | ioEE_free45 | Signed 16-bit | 0 | — | — | — | — | — |
| 16559 | ioEE_free46 | Signed 16-bit | 0 | — | — | — | — | — |
| 16560 | ioEE_free47 | Signed 16-bit | 0 | — | — | — | — | — |
| 16561 | ioEE_free48 | Signed 16-bit | 0 | — | — | — | — | — |
| 16562 | ioEE_free57 | Signed 16-bit | 0 | — | — | — | — | — |
| 16563 | ioEE_free58 | Signed 16-bit | 0 | — | — | — | — | — |
| 16564 | ioEE_free59 | Signed 16-bit | 0 | — | — | — | — | — |
| 16565 | ioEE_free60 | Signed 16-bit | 0 | — | — | — | — | — |
| 16566 | ioEE_free61 | Signed 16-bit | 0 | — | — | — | — | — |
| 16567 | ioEE_free62 | Signed 16-bit | 0 | — | — | — | — | — |
| 16568 | ioEE_free63 | Signed 16-bit | 0 | — | — | — | — | — |
| 16569 | ioEE_free64 | Signed 16-bit | 0 | — | — | — | — | — |
| 16570 | Calibration_exp1_AI1 | Signed 16-bit | 0 | -1000 | 1000 | — | — | Offset of expansions AI |
| 16571 | Calibration_exp1_AI2 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16572 | Calibration_exp1_AI3 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16573 | Calibration_exp1_AI4 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16574 | Calibration_exp2_AI1 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16575 | Calibration_exp2_AI2 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16576 | Calibration_exp2_AI3 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16577 | Calibration_exp2_AI4 | Signed 16-bit | 0 | -1000 | 1000 | — | — | — |
| 16578 | ioEE_free49 | Signed 16-bit | 0 | — | — | — | — | — |
| 16579 | ioEE_free50 | Signed 16-bit | 0 | — | — | — | — | — |
| 16580 | ioEE_free51 | Signed 16-bit | 0 | — | — | — | — | — |
| 16581 | ioEE_free52 | Signed 16-bit | 0 | — | — | — | — | — |
| 16582 | ioEE_free53 | Signed 16-bit | 0 | — | — | — | — | — |
| 16583 | ioEE_free54 | Signed 16-bit | 0 | — | — | — | — | — |
| 16584 | ioEE_free55 | Signed 16-bit | 0 | — | — | — | — | — |
| 16585 | ioEE_free56 | Signed 16-bit | 0 | — | — | — | — | — |
| 16586 | DI_Polarity_LogicIndex_0 | 0 = 0V = Off, 24V = On/Alarm; 1 = 0V = On/Alarm, 24V = Off | 1 | 0 | 1 | — | — | Polarity - Supply Fan Thermal |
| 16587 | DI_Polarity_LogicIndex_1 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return Fan Thermal |
| 16588 | DI_Polarity_LogicIndex_2 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - On/Off Input |
| 16589 | DI_Polarity_LogicIndex_3 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Fire Alarm |
| 16590 | DI_Polarity_LogicIndex_4 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Mode Input |
| 16591 | DI_Polarity_LogicIndex_5 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Door |
| 16592 | DI_Polarity_LogicIndex_6 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Antifreeze |
| 16593 | DI_Polarity_LogicIndex_7 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply Airflow |
| 16594 | DI_Polarity_LogicIndex_8 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return Airflow |
| 16595 | DI_Polarity_LogicIndex_9 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Humidifier Alarm |
| 16596 | DI_Polarity_LogicIndex_10 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Preheater Alarm |
| 16597 | DI_Polarity_LogicIndex_11 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Postheater Alarm |
| 16598 | DI_Polarity_LogicIndex_12 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Rotary Wheel Alarm |
| 16599 | DI_Polarity_LogicIndex_13 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 1 Alarm |
| 16600 | DI_Polarity_LogicIndex_14 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 2 Alarm |
| 16601 | DI_Polarity_LogicIndex_15 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 3 Alarm |
| 16602 | DI_Polarity_LogicIndex_16 | See DI_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Polarity - Filter 4 Alarm |
| 16603 | DI_Polarity_LogicIndex_17 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply 2 Fan Th. |
| 16604 | DI_Polarity_LogicIndex_18 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return 2 Fan Th. |
| 16605 | DI_Polarity_LogicIndex_19 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Supply 2 Airflow |
| 16606 | DI_Polarity_LogicIndex_20 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Return 2 Airflow |
| 16607 | DI_Polarity_LogicIndex_21 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Cond. Unit Alarm |
| 16608 | DI_Polarity_LogicIndex_22 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - El. Heater Alarm |
| 16609 | DI_Polarity_LogicIndex_26_29 | See DI_Polarity_LogicIndex_0 | 1 | 0 | 1 | — | — | Polarity - Cond. Unit Defrost |
| 16610 | DI_Polarity_LogicIndex_30 | Signed 16-bit | 1 | 0 | 1 | — | — | Polarity - Filter 5 Alarm |
| 16611 | ioEE_free69 | Signed 16-bit | 0 | — | — | — | — | — |
| 16612 | ioEE_free70 | Signed 16-bit | 0 | — | — | — | — | — |
| 16613 | ioEE_free71 | Signed 16-bit | 0 | — | — | — | — | — |
| 16614 | ioEE_free72 | Signed 16-bit | 0 | — | — | — | — | — |
| 16615 | DO_Polarity_LogicIndex_0 | 0=NO; 1=NC | 0 | 0 | 1 | — | — | Supply Fan - DO Polarity |
| 16616 | DO_Polarity_LogicIndex_1 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Fan - DO Polarity |
| 16617 | DO_Polarity_LogicIndex_2 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | On Off - DO Polarity |
| 16618 | DO_Polarity_LogicIndex_3 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Alarm - DO Polarity |
| 16619 | DO_Polarity_LogicIndex_4 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Mode - DO Polarity |
| 16620 | DO_Polarity_LogicIndex_5 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Ext. Dampers - DO Polarity |
| 16621 | DO_Polarity_LogicIndex_6 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Bypass Damper - DO Polarity |
| 16622 | DO_Polarity_LogicIndex_7 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Damper - DO Polarity |
| 16623 | DO_Polarity_LogicIndex_8 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Damper - DO Polarity |
| 16624 | DO_Polarity_LogicIndex_9 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump Preheat - DO Polarity |
| 16625 | DO_Polarity_LogicIndex_10 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump Postheat - DO Polarity |
| 16626 | DO_Polarity_LogicIndex_11 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Pump - DO Polarity |
| 16627 | DO_Polarity_LogicIndex_12 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 1 - DO Polarity |
| 16628 | DO_Polarity_LogicIndex_13 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 2 - DO Polarity |
| 16629 | DO_Polarity_LogicIndex_14 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 3 - DO Polarity |
| 16630 | DO_Polarity_LogicIndex_15 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Cool/CH Step 4 - DO Polarity |
| 16631 | DO_Polarity_LogicIndex_16 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pump heat - DO Polarity |
| 16632 | DO_Polarity_LogicIndex_17 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 1 - DO Polarity |
| 16633 | DO_Polarity_LogicIndex_18 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 2 - DO Polarity |
| 16634 | DO_Polarity_LogicIndex_19 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | El. Heater Step 3 - DO Polarity |
| 16635 | DO_Polarity_LogicIndex_20 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 1 - DO Polarity |
| 16636 | DO_Polarity_LogicIndex_21 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 2 - DO Polarity |
| 16637 | DO_Polarity_LogicIndex_22 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Pre Heater Step 3 - DO Polarity |
| 16638 | DO_Polarity_LogicIndex_23 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 1 - DO Polarity |
| 16639 | DO_Polarity_LogicIndex_24 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 2 - DO Polarity |
| 16640 | DO_Polarity_LogicIndex_25 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Post Heater Step 3 - DO Polarity |
| 16641 | DO_Polarity_LogicIndex_27 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Humidifier - DO Polarity |
| 16642 | DO_Polarity_LogicIndex_26 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Recovery - DO Polarity |
| 16643 | DO_Polarity_LogicIndex_28 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Fan 2 - DO Polarity |
| 16644 | DO_Polarity_LogicIndex_29 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Fan 2 - DO Polarity |
| 16645 | DO_Polarity_LogicIndex_30 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Supply Damper 2 - DO Polarity |
| 16646 | DO_Polarity_LogicIndex_31 | See DO_Polarity_LogicIndex_0 | 0 | 0 | 1 | — | — | Return Damper 2 - DO Polarity |
| 16647 | ioEE_free73 | Signed 16-bit | 0 | — | — | — | — | — |
| 16648 | ioEE_free74 | Signed 16-bit | 0 | — | — | — | — | — |
| 16649 | ioEE_free75 | Signed 16-bit | 0 | — | — | — | — | — |
| 16650 | ioEE_free76 | Signed 16-bit | 0 | — | — | — | — | — |
| 16651 | ioEE_free77 | Signed 16-bit | 0 | — | — | — | — | — |
| 16652 | ioEE_free78 | Signed 16-bit | 0 | — | — | — | — | — |
| 16653 | ioEE_free79 | Signed 16-bit | 0 | — | — | — | — | — |
| 16654 | ioEE_free80 | Signed 16-bit | 0 | — | — | — | — | — |
| 16700 | BACNET_ENABLE | Boolean | 1 | — | — | — | — | Bacnet Protocol Enable |
| 16701 | BACNET_ID | Unsigned 16-bit | 1 | 1 |  | — | — | Bacnet Device ID |
| 16702 | BACNET_BBMD_Ip1 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16703 | BACNET_BBMD_Ip2 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16704 | BACNET_BBMD_Ip3 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16705 | BACNET_BBMD_Ip4 | Unsigned 8-bit | 0 | — | — | — | — | BBMD Service IP - Foreing Devices Handling |
| 16706 | BACNET_BBMD_TMO | Unsigned 16-bit | 60 | — | — | sec | — | BBMD Timeout - Foreing Devices Handling |
| 16707 | BACNET_BBMD_PORT | Unsigned 16-bit | 0 | — | — | — | — | BBMD Port - Foreing Devices Handling |
| 16708 | BACNET_SUBNET | Unsigned 8-bit | 0 | 0 | 63 |  |  | Bacnet Device Subnet |
| 16710 | WEB_User_E2 | String | administrator | — | — | — | — | Web User ID |
| 16719 | WEB_PSW_E2 | String | password | — | — | — | — | Web Psw ID |
| 16730 | DayLight_Region | 0=Europe; 1=USA/Canada | 0 | 0 | 1 | — | — | Day Light Region |
| 16731 | DayLight_Enable | Boolean | 1 | — | — | — | — | Day Light Enable |
| 16740 | Unit_ForceOffAfterReboot | Boolean | 0 | — | — | — | — | Force Off keyboard after reboot |
| 16741 | Unit_RegTempType | 0=Supply; 1=Return Direct; 2=Return Cascade | 1 | 0 | 2 | — | — | Temperature Regulation Probe |
| 16742 | SP_T_MIN | Signed 16-bit | 140 | — | SP_T_MAX | °C | XXX.Y | Minimum Temperature Setpoint |
| 16743 | SP_T_MAX | Signed 16-bit | 300 | SP_T_MIN | — | °C | XXX.Y | Maximum Temperature Setpoint |
| 16744 | SP_T_Auto_E2 | Signed 16-bit | 240 | SP_T_MIN | SP_T_MAX | °C | XXX.Y | Setpoint Auto |
| 16745 | DIFF_T_AutoChangeMode | Signed 16-bit | 20 | 5 | — | °C | XXX.Y | Differential Change season (AUTO) |
| 16746 | DIFF_T_AutoEco | Signed 16-bit | 20 | 0 | — | °C | XXX.Y | Differential Economy Mode - Half Band (AUTO) |
| 16747 | SP_T_FORCESUMMER | Signed 16-bit | 240 | — | — | °C | XXX.Y | Force Summer Mode (AUTO) |
| 16748 | SP_T_FORCEWINTER | Signed 16-bit | 160 | — | — | °C | XXX.Y | Force Winter Mode (AUTO) |
| 16749 | SP_T_Cool_E2 | Signed 16-bit | 260 | SP_T_Heat_E2 | SP_T_MAX | °C | XXX.Y | Setpoint Cooling |
| 16750 | SP_T_Heat_E2 | Signed 16-bit | 200 | SP_T_MIN | SP_T_Cool_E2 | °C | XXX.Y | Setpoint Heating |
| 16751 | SP_T_CoolEco_E2 | Signed 16-bit | 280 | SP_T_Cool_E2 | SP_T_MAX | °C | XXX.Y | Setpoint Cooling Economy |
| 16752 | SP_T_HeatEco_E2 | Signed 16-bit | 180 | SP_T_MIN | SP_T_Heat_E2 | °C | XXX.Y | Setpoint Heating Economy |
| 16753 | SP_RH_MinSetpoint | Signed 16-bit | 30 | 20 | SP_RH_MaxSetpoint | %R.H. | — | Minimum relative humidity setpoint |
| 16754 | SP_RH_MaxSetpoint | Signed 16-bit | 90 | SP_RH_MinSetpoint | 100 | %R.H. | — | Maximum relative humidity setpoint |
| 16755 | SP_RH_DehumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Dehumidication setpoint (comfort) |
| 16756 | SP_RH_DehumidificationSetpointEco_E2 | Signed 16-bit | 55 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Dehumidication setpoint (eco) |
| 16757 | SP_RH_HumidificationSetpoint_E2 | Signed 16-bit | 50 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Humidification setpoint (comfort) |
| 16758 | SP_RH_HumidificationSetpointEco_E2 | Signed 16-bit | 45 | SP_RH_MinSetpoint | SP_RH_MaxSetpoint | %R.H. | — | Humidification setpoint (eco) |
| 16759 | SP_VOC_E2 | Signed 16-bit | 40 | 0 | 100 | % | — | VOC Air quality setpoint |
| 16760 | SP_CO2_E2 | Signed 16-bit | 800 | 0 | 2000 | ppm | — | CO2 Air quality setpoint |
| 16770 | cfgFreeCooling | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | — | FreeCooling Enable |
| 16771 | cfgFreeHeating | 0=Disabled; 1=Prop.Reg.; 2=Recovery Reg. | 0 | 0 | 2 | — | — | FreeHeating Enable |
| 16772 | FreeCHMinExtTemp | Signed 16-bit | 120 | -200 | 200 | °C | XXX.Y | Free Cooling/Heating Minimum External Temperature |
| 16773 | FreeCHBand | Signed 16-bit | 50 | 10 | 100 | °C | XXX.Y | Free Cooling/Heating Proportional Band (direct return reg) |
| 16774 | FreeCHTimeout | Unsigned 16-bit | 60 | 0 | 180 | min | — | Free Cooling/Heating Timeout |
| 16775 | FreeCHDiff | Signed 16-bit | 50 | 10 | 100 | °C | XXX.Y | Free Cooling/Heating Outside Regulation Differential |
| 16776 | FreeCHHyst | Signed 16-bit | 10 | 2 | 50 | °C | XXX.Y | Free Cooling/Heating Hysteresis |
| 16780 | cfgFireAlarm | 0=Off All; 1=All Fans-Damper On; 2=ReturnFan-Damper On | 0 | 0 | 2 | — | — | Fire Alarm Configuration |
| 16781 | FireTempSet | Signed 16-bit | 950 | 900 | — | °C | XXX.Y | Setpoint Temperature for Fire Alarm |
| 16782 | Alm_MinHumiditySens | Signed 16-bit | 20 | 0 | 1000 | %R.H. | XXX.Y | Minimum Valid Humidity Value |
| 16783 | Alm_MinVOCSens | Signed 16-bit | 20 | 0 | 1000 | % | XXX.Y | Minimum Valid VOC Value |
| 16784 | Alm_MinCO2Sens | Signed 16-bit | 40 | 0 | — | ppm | — | Minimum Valid CO2 Value |
| 16785 | Alm_MinPrSens | Signed 16-bit | 40 | 0 | — | pa | — | Minimum Valid Pr Value (Fans on) |
| 16786 | Alm_ActiveProbeBypass | Unsigned 16-bit | 30 | 0 | 600 | sec | — | Active Probe alarm bypass |
| 16787 | AFset | Signed 16-bit | 50 | -50 | 150 | °C | XXX.Y | Antifreeze Setpoint |
| 16788 | AFdiff | Signed 16-bit | 20 | 1 | 50 | °C | XXX.Y | Antifreeze Differential |
| 16789 | AFphtime | Unsigned 16-bit | 5 | 0 | 255 | min | — | Antifreeze Preheater time |
| 16800 | ExtDamperOpenDelay | Unsigned 16-bit | 60 | — | — | sec | — | External/Fan Damper Open Time |
| 16801 | ExtDamperCloseDelay | Unsigned 16-bit | 60 | — | — | sec | — | External/Fan Damper Close Time |
| 16802 | ExtDamperMinOpen | Signed 16-bit | 50 | 0 | 100 | % | — | External Damper Minimum Open |
| 16803 | ExtDamperMaxOpen | Signed 16-bit | 100 | ExtDamperMinOpen | 100 | % | — | External Damper Maximum Open |
| 16820 | VOC_Bp | Unsigned 16-bit | 300 | 1 | — | % | XXX.Y | VOC Regulator: Prop. Band |
| 16821 | VOC_Ti | Unsigned 16-bit | 0 | — | — | sec | — | VOC Regulator: Integral Time |
| 16822 | CO2_Bp | Unsigned 16-bit | 400 | 1 | — | ppm | — | CO2 Regulator: Prop. Band |
| 16823 | CO2_Ti | Unsigned 16-bit | 0 | — | — | sec | — | CO2 Regulator: Integral Time |
| 16840 | Fan_MinimumSpeed | Signed 16-bit | 250 | 0 | 500 | % | XXX.Y | Fan Minimum Speed (Pressure Regulation and limit for other speed) |
| 16841 | Fan_LowSpeed | Signed 16-bit | 300 | Fan_MinimumSpeed | 800 | % | XXX.Y | Fan Low Speed (Start Phase/Night/Min Air Q. and Defrost Speed) |
| 16842 | Fan_NominalSpeed | Signed 16-bit | 900 | Fan_LowSpeed | 1000 | % | XXX.Y | Fan Nominal/Maximum Speed |
| 16843 | Fan_ReturnSpeedCorrection | Signed 16-bit | 0 | -500 | 500 | % | XXX.Y | Fan Return Output correction (not used with 2 pressure probes) |
| 16844 | Fan_PowerUp1_Time | Unsigned 16-bit | 30 | 0 | 255 | sec | — | Fan Power Up Time at Min Speed (with Heaters) |
| 16845 | Fan_PowerUp2_Time | Unsigned 16-bit | 10 | 0 | 255 | sec | — | Fan Power Up Time at Nom Speed (with Heaters) |
| 16846 | Fan_Post_Time | Unsigned 16-bit | 40 | 0 | 255 | sec | — | Fan Post Ventilation Time (with Heaters) |
| 16847 | Fan_PreHeating_Time | Unsigned 16-bit | 180 | 0 | 600 | sec | — | Fan Preheating Time (with heating valves) |
| 16848 | Fan_PreHeatOnSet | Signed 16-bit | -50 | -200 | 100 | °C | XXX.Y | External Temperature Set forcing preheating time |
| 16849 | Fan_Swap_Time | Unsigned 16-bit | 240 | 0 | 600 | hours | — | Fan swap time (0=Disabled) |
| 16850 | Fan_SwapPolicy | 0 = If available Start always Fans 1; 1 = Start Section with less working hours (Supply + Return); 2 = Start Fans with less working hours; 3 = Start Fans with less working hours keeping parallel sections | 0 | 0 | 3 | — | — | Fan swap policy |
| 16851 | Fan_SinglePressureReturn | Boolean | 0 | — | — | — | — | In case of a unique pressure probe mounted on return section and Supply+Return Fans |
| 16852 | Fan_AlrmPressBypass | Unsigned 16-bit | 30 | 1 | 600 | Sec | — | Flow Bypass |
| 16853 | Fan_SupplyAirflowAlrmByAi | Boolean | 0 | — | — | — | — | Enable supply flow alarm by probe (pressure probe must be already enabled) |
| 16854 | Fan_ReturnAirflowAlrmByAi | Boolean | 0 | — | — | — | — | Enable return flow alarm by probe (pressure probe must be already enabled) |
| 16855 | Fan_SetMinAirflow | Signed 16-bit | 50 | — | — | Pa | — | Fan Airflow Alarm setpoint |
| 16856 | FAN_Supply_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | — | Fan Supply Prop. Band Pressure |
| 16857 | FAN_Supply_TiP | Unsigned 16-bit | 75 | — | — | sec | — | Fan Supply Integral Time Pressure |
| 16858 | FAN_Supply_TdP | Unsigned 16-bit | 0 | — | — | sec | — | Fan Supply Derivative Time Pressure |
| 16859 | FAN_Return_BpP | Unsigned 16-bit | 400 | 1 | — | Pa | — | Fan Return Prop. Band Pressure |
| 16860 | FAN_Return_TiP | Unsigned 16-bit | 75 | — | — | sec | — | Fan Return Integral Time Pressure |
| 16861 | FAN_Return_TdP | Unsigned 16-bit | 0 | — | — | sec | — | Fan Return Derivative Time Pressure |
| 16862 | Fan_K_Supply | Unsigned 16-bit | 100 | 1 | 3000 | — | — | Fan K Supply |
| 16863 | Fan_K_Return | Unsigned 16-bit | 100 | 1 | 3000 | — | — | Fan K Return |
| 16880 | Fan_Supply_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | — | Fan Supply Regulation Unit |
| 16881 | Fan_Return_Pressure_Flow | 0=Pressure; 1=Flow | 0 | 0 | 1 | — | — | Fan Return Regulation Unit |
| 16882 | Fan_Supply_SetMinPr | Signed 16-bit | 50 | — | — | Pa | — | Fan Supply Minimum/Night Pressure Setpoint |
| 16883 | Fan_Return_SetMinPr | Signed 16-bit | 50 | — | — | Pa | — | Fan Return Minimum/Night Pressure Setpoint |
| 16884 | Fan_SetPrSupply | Signed 16-bit | 100 | Fan_Supply_SetMinPr | Fan_Supply_SetMaxPr | Pa | — | Fan Supply Pressure Setpoint |
| 16885 | Fan_SetPrReturn | Signed 16-bit | 100 | Fan_Return_SetMinPr | Fan_Return_SetMaxPr | Pa | — | Fan Return Pressure Setpoint |
| 16886 | Fan_Supply_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | — | Fan Supply Maximum Pressure Setpoint |
| 16887 | Fan_Return_SetMaxPr | Signed 16-bit | 5000 | — | — | Pa | — | Fan Return Maximum Pressure Setpoint |
| 16888 | Fan_Supply_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | — | Fan Supply Minimum/Night Flow Setpoint |
| 16890 | Fan_Return_SetMinFlow | Signed 32-bit | 50 | — | — | m3/h | — | Fan Return Minimum/Night Flow Setpoint |
| 16892 | Fan_SetFlowSupply | Signed 32-bit | 100 | Fan_Supply_SetMinFlow | Fan_Supply_SetMaxFlow | m3/h | — | Fan Supply Flow Setpoint |
| 16894 | Fan_SetFlowReturn | Signed 32-bit | 100 | Fan_Return_SetMinFlow | Fan_Return_SetMaxFlow | m3/h | — | Fan Return Flow Setpoint |
| 16896 | Fan_Supply_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | — | Fan Supply Maximum Flow Setpoint |
| 16898 | Fan_Return_SetMaxFlow | Signed 32-bit | 100000 | — | — | m3/h | — | Fan Return Maximum Flow Setpoint |
| 16910 | SupplyDeltaUpHeating | Signed 16-bit | 160 | 5 | 400 | °C | XXX.Y | Heating Max Supply =RegSet+SupplyDeltaUpHeating |
| 16911 | SupplyDeltaDwHeating | Signed 16-bit | 20 | 0 | 50 | °C | XXX.Y | Heating Min Supply =RegSet-SupplyDeltaDwHeating |
| 16912 | SupplyDeltaUpCooling | Signed 16-bit | 10 | 5 | 50 | °C | XXX.Y | Cooling Max Supply =RegSet+SupplyDeltaUpCooling |
| 16913 | SupplyDeltaDwCooling | Signed 16-bit | 120 | 5 | 150 | °C | XXX.Y | Cooling Min Supply =RegSet-SupplyDeltaDwCooling |
| 16914 | Pb_Cooling | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Cooling Proportional Band |
| 16915 | Pb_Heating | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Heating Proportional Band |
| 16916 | Ti_Cooling | Unsigned 16-bit | 0 | 0 | — | sec | — | Cooling Integral Time |
| 16917 | Ti_Heating | Unsigned 16-bit | 0 | 0 | — | sec | — | Heating Integral Time |
| 16918 | Pb_ReturnCooling | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Return Temp. Reg: Cooling Proportional Band (only Cascade) |
| 16919 | Pb_ReturnHeating | Signed 16-bit | 20 | 2 | 999 | °C | XXX.Y | Return Temp. Reg: Heating Proportional Band (only Cascade) |
| 16920 | Ti_ReturnCooling | Unsigned 16-bit | 0 | 0 | — | sec | — | Return Temp. Reg: Cooling Integral Time (only Cascade) |
| 16921 | Ti_ReturnHeating | Unsigned 16-bit | 0 | 0 | — | sec | — | Return Temp. Reg: Heating Integral Time (only Cascade) |
| 16930 | Temp_HighSupplyEn | Boolean | 0 | — | — | — | — | Temperature High Supply Limit Enable (Winter) |
| 16931 | Temp_HighSupplySet | Signed 16-bit | 350 | 0 | 1000 | °C | XXX.Y | Temperature High Supply Limit Setpoint (Winter) |
| 16932 | Temp_HighSupplyBand | Signed 16-bit | 100 | 10 | 999 | °C | XXX.Y | Temperature High Supply Band (Winter) |
| 16933 | Temp_LowSupplyEn | Boolean | 0 | — | — | — | — | Temperature Low Supply Limit Enable (Summer) |
| 16934 | Temp_LowSupplySet | Signed 16-bit | 150 | 0 | 1000 | °C | XXX.Y | Temperature Low Supply Limit Setpoint (Summer) |
| 16935 | Temp_LowSupplyBand | Signed 16-bit | 100 | 10 | 999 | °C | XXX.Y | Temperature Low Supply Band (Summer) |
| 16940 | FastHeatCoolEn | Boolean | 0 | — | — | — | — | Fast Heating/Cooling Enable |
| 16941 | FastHeatSet | Signed 16-bit | 200 | -500 | 500 | °C | XXX.Y | Maximum outside temp for Power up Fast Heating |
| 16942 | FastCoolSet | Signed 16-bit | 250 | -500 | 500 | °C | XXX.Y | Minimum outside temp for Power up Fast Cooling |
| 16943 | FastHCTimeout | Signed 16-bit | 10 | 1 | — | Min | — | Fast Heating/Cooling and StartUp timeout |
| 16950 | Pump_AntiStickingRun | Unsigned 16-bit | 20 | 0 | 255 | sec | — | Antisticking run time |
| 16951 | Pump_AntiStickingPeriod | Unsigned 16-bit | 7 | 0 | 30 | days | — | Antisticking period (0=Disabled) |
| 16952 | Pump_Post_Time | Unsigned 16-bit | 5 | 0 | 255 | min | — | Pump Post Running Time |
| 16953 | Heater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Analog Power |
| 16954 | Heater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 1 Power |
| 16955 | Heater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 2 Additional Power |
| 16956 | Heater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 3 Additional Power |
| 16957 | Heater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 4 Additional Power |
| 16958 | Heater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 5 Additional Power |
| 16959 | Heater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | Power | — | El. Heater Step 6 Additional Power |
| 16960 | Heater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | El. Heater Hysteresis [% of current step] |
| 16961 | Heater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | El. Heater PWM Period |
| 16962 | PreHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Analog Power |
| 16963 | PreHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 1 Power |
| 16964 | PreHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 2 Power |
| 16965 | PreHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 3 Power |
| 16966 | PreHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 4 Power |
| 16967 | PreHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 5 Power |
| 16968 | PreHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | — | PreHeater Step 6 Power |
| 16969 | PreHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | PreHeater Hysteresis [% of current step] |
| 16970 | PreHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | PreHeater PWM Period |
| 16971 | PostHeater_Power_Analog | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Analog Power |
| 16972 | PostHeater_Power_Step1 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 1 Power |
| 16973 | PostHeater_Power_Step2 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 2 Power |
| 16974 | PostHeater_Power_Step3 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 3 Power |
| 16975 | PostHeater_Power_Step4 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 4 Power |
| 16976 | PostHeater_Power_Step5 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 5 Power |
| 16977 | PostHeater_Power_Step6 | Unsigned 16-bit | 2 | 1 | — | — | — | PostHeater Step 6 Power |
| 16978 | PostHeater_Hysteresis | Unsigned 16-bit | 75 | 1 | 100 | % | — | PostHeater Hysteresis [% of current step] |
| 16979 | PostHeater_PWM_Period | Signed 16-bit | 30 | 10 | 3000 | sec | — | PreHeater PWM Period |
| 16980 | CondUnitS1_Req | Signed 16-bit | 200 | 0 | 1000 | % | XXX.Y | % CondUnit Step 1 |
| 16981 | CondUnitS2_Req | Signed 16-bit | 400 | 0 | 1000 | % | XXX.Y | % CondUnit Step 2 |
| 16982 | CondUnitS3_Req | Signed 16-bit | 600 | 0 | 1000 | % | XXX.Y | % CondUnit Step 3 |
| 16983 | CondUnitS4_Req | Signed 16-bit | 800 | 0 | 1000 | % | XXX.Y | % CondUnit Step 4 |
| 16984 | CondUnitSx_Hysteresis | Signed 16-bit | 50 | 10 | 100 | % | — | Cond. Unit Hysteresis % of current Step size |
| 16985 | CondUnit_Ton | Unsigned 16-bit | 0 | 0 | 600 | sec | — | Cond Unit Step Minimum On Time |
| 16986 | CondUnit_Toff | Unsigned 16-bit | 0 | 0 | 600 | sec | — | Cond Unit Step Minimum Off Time |
| 16987 | CondUnit_Offset | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | Cond Unit AO Offset |
| 16988 | CondUnit_FanSpeedDefrost | 0=No Action 1=Low Speed 2=Fan Off | 0 | 0 | 2 |  |  | Condensing Unit: Fan Speed During Defrost |
| 16989 | MultiCondUnit_CtrlMode | FALSE=Delay TRUE=Hysteresis | 1 | 0 | 1 |  |  | Multi Condensing Unit:Control |
| 16990 | MultiCondUnit_RegHyst | Signed 16-bit | 5 | 2 | 30 | sec |  | Multi Condensing Unit regulator hysteresis |
| 16991 | MultiCondUnit_DelayOn | Unsigned 16-bit | 0 | 0 | 600 | sec |  | Multi Cond Unit Delay On |
| 16992 | MultiCondUnit_DelayOff | Unsigned 16-bit | 0 | 0 | 600 | sec |  | Multi Cond Unit Delay Off |
| 17000 | PreHeaterSetpoint | Signed 16-bit | 50 | -100 | 200 | °C | XXX.Y | Setpoint Pre Heating |
| 17001 | Pb_PreHeating | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | PreHeating Proportional Band |
| 17002 | Ti_PreHeating | Unsigned 16-bit | 300 | 0 | — | sec | — | PreHeating Integral Time |
| 17010 | RecoveryDiff_Band | Signed 16-bit | 15 | 1 | 100 | °C | XXX.Y | Recovery Diff (On/Off Case) Recovery Band (Mod Case with Direct Return control); |
| 17011 | RecoveryDeadZone | Signed 16-bit | 10 | 0 | 100 | °C | XXX.Y | Recovery Dead Zone |
| 17012 | RecoveryPower | Signed 16-bit | 250 | 0 | 1000 | % | XXX.Y | % of PI out sent to recovery (Only for Cascade or Supply control) |
| 17013 | RecoveryDefrost_SetMaxReq | Signed 16-bit | -40 | -150 | 100 | °C | XXX.Y | Recovery Defrost: Setpoint Expulsion Temperature |
| 17014 | RecoveryDefrost_Band | Signed 16-bit | 40 | 1 | 100 | °C | XXX.Y | Recovery Defrost: Band Mix Chamber/PreHeater/Supply Fan |
| 17015 | RecoveryDefrost_Cutoff | Signed 16-bit | 0 | 0 | 100 | °C | XXX.Y | Recovery Defrost: CutOff Modulating Fan |
| 17016 | RecoveryReqDuringFastHC | Signed 16-bit | 0 | 0 | 1000 | % | XXX.Y | Recovery request during Fast Heating/Cooling |
| 17020 | Hum_Band | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | Humidification Band |
| 17021 | Pb_Dehum | Signed 16-bit | 100 | 2 | 200 | %R.H. | XXX.Y | Dehum. Proportional Band |
| 17022 | Ti_Dehum | Unsigned 16-bit | 0 | 0 | — | sec | — | Dehum. Integral Time |
| 17023 | Pb_Dewpoint | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | Dewpoint Dehum. Proportional Band |
| 17024 | Ti_Dewpoint | Unsigned 16-bit | 300 | 0 | — | sec | — | Dewpoint Dehum. Integral Time |
| 17025 | Offset_Post | Signed 16-bit | 10 | 4 | 50 | °C | XXX.Y | PostHeating Setpoint offset with respect to current set |
| 17026 | Dehum_WinterEn | Boolean | 0 | — | — | — | — | Enable Winter Dehumidification |
| 17027 | Dehum_WinterHumHyst | Signed 16-bit | 10 | 4 | 50 | g/Kg | XXX.Y | Winter Dehumidification Hysteresis |
| 17028 | Dehum_Req_Diff | Signed 16-bit | 50 | 1 | 150 | %R.H. | XXX.Y | Dehumidification Request Differential on Return Humidity for Winter and Dewpoint mode |
| 17029 | Hum_HighSupplyEn | Boolean | 0 | — | — | — | — | Humidification High Supply Limit Enable |
| 17030 | Hum_HighSupplySet | Signed 16-bit | 700 | 0 | 1000 | %R.H. | XXX.Y | Humidification High Supply Limit Setpoint |
| 17031 | Hum_HighSupplyBand | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | Humidification High Supply Band |
| 17032 | DeHum_LowSupplyEn | Boolean | 0 | — | — | %R.H. | — | DeHumidification Low Supply Limit Enable |
| 17033 | DeHum_LowSupplySet | Signed 16-bit | 300 | 0 | 1000 | %R.H. | XXX.Y | DeHumidification Low Supply Limit Setpoint |
| 17034 | DeHum_LowSupplyBand | Signed 16-bit | 200 | 10 | 400 | %R.H. | XXX.Y | DeHumidification Low Supply Band |
| 17040 | PostHeating4Integration | Boolean | 1 | — | — | — | — | Use the post heating also in the heating phase |
| 17041 | PostPower | Signed 16-bit | 300 | 1 | 1000 | % | XXX.Y | % of PI out sent to post (if enabled as heat integration) |
| 17042 | Pb_Post | Signed 16-bit | 100 | 2 | 999 | °C | XXX.Y | PostHeating Dehum. Proportional Band |
| 17043 | Ti_Post | Unsigned 16-bit | 300 | 0 | — | sec | — | PostHeating Dehum. Integral Time |
| 17900 | LogEnable | Boolean | 0 | — | — | — | — | Logger Enable |
| 17901 | LogCycle | Unsigned 16-bit | 1 | MinLogCycle | 1439 | Min | HH:MM | Logger Period |
| 17902 | LogErrorNumber | Unsigned 32-bit | 0 | — | — | — | — | Error while try to oper or save to a file |
| 17904 | LoggedRecord | Unsigned 32-bit | 0 | — | — | — | — | Number of logged record (Rounded by 100) |
| 17906 | MinLogCycle | Signed 16-bit | 1 | 0 | 1439 | Min | HH:MM | Minimum Log Cycle |
| 17907 | FirstDownload | Boolean | 1 | — | — | — | — | — |
| 17908 | microSDPresCount | Unsigned 16-bit | 0 | — | — | — | — | microSD Presence Counter |
| 18000 | tE00_TimeBandEnable | Boolean | 0 | — | — | — | — | Time events Enable |
| 18001 | tE01_TimeProfileMonday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Monday |
| 18002 | tE02_TimeProfileTuesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Tuesday |
| 18003 | tE03_TimeProfileWednesday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Wednesday |
| 18004 | tE04_TimeProfileThursday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Thursday |
| 18005 | tE05_TimeProfileFriday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Friday |
| 18006 | tE06_TimeProfileSaturday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Saturday |
| 18007 | tE07_TimeProfileSunday | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Time events profile on Sunday |
| 18008 | tE10_TimeProfile1Event1 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #1 of profile #1 |
| 18009 | tE11_ModeProfile1Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #1 of profile #1 |
| 18010 | tE12_TimeProfile1Event2 | Signed 16-bit | 720 | 0 | 1439 | — | HH:MM | Time of event #2 of profile #1 |
| 18011 | tE13_ModeProfile1Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #2 of profile #1 |
| 18012 | tE14_TimeProfile1Event3 | Signed 16-bit | 840 | 0 | 1439 | — | HH:MM | Time of event #3 of profile #1 |
| 18013 | tE15_ModeProfile1Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #3 of profile #1 |
| 18014 | tE16_TimeProfile1Event4 | Signed 16-bit | 1080 | 0 | 1439 | — | HH:MM | Time of event #4 of profile #1 |
| 18015 | tE17_ModeProfile1Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #4 of profile #1 |
| 18016 | tE20_TimeProfile2Event1 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #1 of profile #2 |
| 18017 | tE21_ModeProfile2Event1 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #1 of profile #2 |
| 18018 | tE22_TimeProfile2Event2 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #2 of profile #2 |
| 18019 | tE23_ModeProfile2Event2 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #2 of profile #2 |
| 18020 | tE24_TimeProfile2Event3 | Signed 16-bit | 480 | 0 | 1439 | — | HH:MM | Time of event #3 of profile #2 |
| 18021 | tE25_ModeProfile2Event3 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #3 of profile #2 |
| 18022 | tE26_TimeProfile2Event4 | Signed 16-bit | 1080 | 0 | 1439 | — | HH:MM | Time of event #4 of profile #2 |
| 18023 | tE27_ModeProfile2Event4 | 0=Off; 1=Eco; 2=Comfort; 3=Night | 0 | 0 | 3 | — | — | Mode of event #4 of profile #2 |
| 18200 | TW00_EnableYearEvents | Boolean | 0 | — | — | — | — | Enable year events |
| 18201 | TW01_EventProfile01 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 1 |
| 18202 | TW02_EventProfile02 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 2 |
| 18203 | TW03_EventProfile03 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 3 |
| 18204 | TW04_EventProfile04 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 4 |
| 18205 | TW05_EventProfile05 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 5 |
| 18206 | TW06_EventProfile06 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 6 |
| 18207 | TW07_EventProfile07 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 7 |
| 18208 | TW08_EventProfile08 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 8 |
| 18209 | TW09_EventProfile09 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 9 |
| 18210 | TW10_EventProfile10 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 10 |
| 18211 | TW11_EventProfile11 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 11 |
| 18212 | TW12_EventProfile12 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 12 |
| 18213 | TW13_EventProfile13 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 13 |
| 18214 | TW14_EventProfile14 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 14 |
| 18215 | TW15_EventProfile15 | 1=P1; 2=P2; 3=24h On; 4=24h Off | 1 | 1 | 4 | — | — | Year events profile 15 |
| 18216 | TW16_EnEvent01 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 1 |
| 18217 | TW17_EnEvent02 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 2 |
| 18218 | TW18_EnEvent03 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 3 |
| 18219 | TW19_EnEvent04 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 4 |
| 18220 | TW20_EnEvent05 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 5 |
| 18221 | TW21_EnEvent06 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 6 |
| 18222 | TW22_EnEvent07 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 7 |
| 18223 | TW23_EnEvent08 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 8 |
| 18224 | TW24_EnEvent09 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 9 |
| 18225 | TW25_EnEvent10 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 10 |
| 18226 | TW26_EnEvent11 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 11 |
| 18227 | TW27_EnEvent12 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 12 |
| 18228 | TW28_EnEvent13 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 13 |
| 18229 | TW29_EnEvent14 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 14 |
| 18230 | TW30_EnEvent15 | 0 = Off; 1 = On | 0 | 0 | 1 | — | — | Enable Year events 15 |
| 18231 | TW31_EventDDStart01 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 1 |
| 18232 | TW32_EventDDStart02 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 2 |
| 18233 | TW33_EventDDStart03 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 3 |
| 18234 | TW34_EventDDStart04 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 4 |
| 18235 | TW35_EventDDStart05 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 5 |
| 18236 | TW36_EventDDStart06 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 6 |
| 18237 | TW37_EventDDStart07 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 7 |
| 18238 | TW38_EventDDStart08 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 8 |
| 18239 | TW39_EventDDStart09 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 9 |
| 18240 | TW40_EventDDStart10 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 10 |
| 18241 | TW41_EventDDStart11 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 11 |
| 18242 | TW42_EventDDStart12 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 12 |
| 18243 | TW43_EventDDStart13 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 13 |
| 18244 | TW44_EventDDStart14 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 14 |
| 18245 | TW45_EventDDStart15 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Start Day Year events 15 |
| 18246 | TW46_EventMMStart01 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 1 |
| 18247 | TW47_EventMMStart02 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 2 |
| 18248 | TW48_EventMMStart03 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 3 |
| 18249 | TW49_EventMMStart04 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 4 |
| 18250 | TW50_EventMMStart05 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 5 |
| 18251 | TW51_EventMMStart06 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 6 |
| 18252 | TW52_EventMMStart07 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 7 |
| 18253 | TW53_EventMMStart08 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 8 |
| 18254 | TW54_EventMMStart09 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 9 |
| 18255 | TW55_EventMMStart10 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 10 |
| 18256 | TW56_EventMMStart11 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 11 |
| 18257 | TW57_EventMMStart12 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 12 |
| 18258 | TW58_EventMMStart13 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 13 |
| 18259 | TW59_EventMMStart14 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 14 |
| 18260 | TW60_EventMMStart15 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Month Year events 15 |
| 18261 | TW61_EventDDStop01 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 1 |
| 18262 | TW62_EventDDStop02 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 2 |
| 18263 | TW63_EventDDStop03 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 3 |
| 18264 | TW64_EventDDStop04 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 4 |
| 18265 | TW65_EventDDStop05 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 5 |
| 18266 | TW66_EventDDStop06 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 6 |
| 18267 | TW67_EventDDStop07 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 7 |
| 18268 | TW68_EventDDStop08 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 8 |
| 18269 | TW69_EventDDStop09 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 9 |
| 18270 | TW70_EventDDStop10 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 10 |
| 18271 | TW71_EventDDStop11 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 11 |
| 18272 | TW72_EventDDStop12 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 12 |
| 18273 | TW73_EventDDStop13 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 13 |
| 18274 | TW74_EventDDStop14 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 14 |
| 18275 | TW75_EventDDStop15 | Unsigned 8-bit | 1 | 1 | 31 | Day | — | Stop Day Year events 15 |
| 18276 | TW76_EventMMStop01 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18277 | TW77_EventMMStop02 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18278 | TW78_EventMMStop03 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18279 | TW79_EventMMStop04 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18280 | TW80_EventMMStop05 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18281 | TW81_EventMMStop06 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18282 | TW82_EventMMStop07 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18283 | TW83_EventMMStop08 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18284 | TW84_EventMMStop09 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18285 | TW85_EventMMStop10 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18286 | TW86_EventMMStop11 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18287 | TW87_EventMMStop12 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18288 | TW88_EventMMStop13 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18289 | TW89_EventMMStop14 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Stop Month Year events 1 |
| 18290 | TW90_EventMMStop15 | Unsigned 8-bit | 1 | 1 | 12 | Month | — | Start Day Year events 1 |
| 19810 | Fan_Maintenance_Supply | Boolean | 0 | — | — | — | — | Fan Main Supply Forced Off for maintenance |
| 19811 | Fan_Maintenance_Return | Boolean | 0 | — | — | — | — | Fan Main Return Forced Off for maintenance |
| 19812 | Fan_Maintenance_SupplyBck | Boolean | 0 | — | — | — | — | Fan Supply 2 Forced Off for maintenance |
| 19813 | Fan_Maintenance_ReturnBck | Boolean | 0 | — | — | — | — | Fan Return 2 Forced Off for maintenance |
| 19814 | Fan_Maintenance_Supply1b | Boolean | 0 | — | — | — | — | Fan Main Supply b Forced Off for maintenance |
| 19815 | Fan_Maintenance_Supply1c | Boolean | 0 | — | — | — | — | Fan Main Supply c Forced Off for maintenance |
| 19816 | Fan_Maintenance_Return1b | Boolean | 0 | — | — | — | — | Fan Main Return b Forced Off for maintenance |
| 19817 | Fan_Maintenance_Return1c | Boolean | 0 | — | — | — | — | Fan Main Return c Forced Off for maintenance |
| 19818 | Fan_Maintenance_Supply2b | Boolean | 0 | — | — | — | — | Fan Main Supply 2b Forced Off for maintenance |
| 19819 | Fan_Maintenance_Supply2c | Boolean | 0 | — | — | — | — | Fan Main Supply 2c Forced Off for maintenance |
| 19820 | Fan_Maintenance_Return2b | Boolean | 0 | — | — | — | — | Fan Main Return 2b Forced Off for maintenance |
| 19821 | Fan_Maintenance_Return2c | Boolean | 0 | — | — | — | — | Fan Main Return 2c Forced Off for maintenance |
| 19822 | Fan_Modbus_Configured_E2 | Boolean | 0 |  |  |  |  | Modbus Fan have been configured |
| 19823 | udhoursCU1E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 1 Running Hours |
| 19825 | udhoursCU2E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 2 Running Hours |
| 19827 | udhoursCU3E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 3 Running Hours |
| 19829 | udhoursCU4E2 | Unsigned 32-bit | 0 |  |  |  |  | Condensing Unit 4 Running Hours |
| 19831 | CU1_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 1 Forced Off for maintenance |
| 19832 | CU2_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 2 Forced Off for maintenance |
| 19833 | CU3_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 3 Forced Off for maintenance |
| 19834 | CU4_Maintenance | Boolean | 0 | — | — | — | — | Condensing Unit 4 Forced Off for maintenance |

Tabella 99 - Tabella Modbus EEProm

Tabella Modbus Stati

Nella seguente tabella sono descritti i parametri Stati.

| Modbus Register | Name | Device type | Def | Min | Max | Unit | Format | RW | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9213 | PSWEntry | Unsigned 16-bit | 0 | — | — | — | — | RW | Password Entry: |
| 9214 | PSWLevel | Unsigned 8-bit | — | — | — | — | — | R | Current password level |
| 9215 | PSWreset | Boolean | 0 | — | — | — | — | RW | Password Level Reset Request |
| 9216 | sysClock_seconds_WR | Unsigned 8-bit | 0 | 0 | 59 | — | — | RW | Second value to update |
| 9217 | sysClock_minutes_WR | Unsigned 8-bit | 0 | 0 | 59 | — | — | RW | Minute value to update |
| 9218 | sysClock_hours_WR | Unsigned 8-bit | 0 | 0 | 23 | — | — | RW | Hour value to update |
| 9219 | sysClock_dayweek_WR | Unsigned 8-bit | 0 | 0 | 6 | — | — | RW | Day of the week value to update |
| 9220 | sysClock_daymonth_WR | Unsigned 8-bit | 1 | 1 | 31 | — | — | RW | Day of the month value to update |
| 9221 | sysClock_month_WR | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | Month value to update |
| 9222 | sysClock_year_WR | Unsigned 8-bit | 10 | 10 | 99 | — | — | RW | Year value to update |
| 9223 | sysClock_update | 0=Current; 1=Update; 2=Modify | 0 | 0 | 2 | — | — | RW | Confirm update |
| 9224 | sv_sysUsbStatus | 0=Completed; 1=Running; 248 = 248=Open in write failed; 249 = 249=Write failed; 250 = 250=Some parameters failed; 251 = 251=File not compatible; 252 = 252=Usb not connected; 253 = 253=File too long; 254 = 254=File not present; 255 = 255=Command Failed | — | 0 | 255 | — | — | R | Usb status code |
| 9225 | sv_sysUsbCommand | Unsigned 16-bit | 0 | — | — | — | — | RW | Usb status code |
| 9226 | SaveFactoryStatus | 0=Running; 1=Done; 2=Error/Not Done | — | 0 | 2 | — | — | R | Save Factory Settings Status |
| 9227 | SaveFactoryCommand | Boolean | 0 | — | — | — | — | RW | Save Factory Settings Request |
| 9228 | RestoreFactoryStatus | 0=Completed; 1=Running; 248 = 248=Open in write failed; 249 = 249=Write failed; 250 = 250=Some parameters failed; 251 = 251=File not compatible; 252 = 252=Usb not connected; 253 = 253=File too long; 254 = 254=File not present; 255 = 255=Command Failed | — | 0 | 255 | — | — | R | Restore Factory Settings Status |
| 9229 | RestoreFactoryCommand | Boolean | 0 | — | — | — | — | RW | Restore Factory Settings Request |
| 9299 | Unit_ApplicationCode | Unsigned 16-bit | 1 |  |  |  |  | R | Unit Application Code |
| 9300 | Unit_Version | Unsigned 16-bit | 0 | — | — | — | XX.YY | RW | Unit Application Version |
| 9301 | Unit_BMS_OnOff | Boolean | 1 | — | — | — | — | RW | Unit On/Off via Modbus |
| 9302 | Unit_Status | 0=OFF; 1=STANDBY; 2=RUN | — | 0 | 2 | — | — | R | Unit Status |
| 9303 | Unit_Mode_Status | 0=Cool; 1=Heat; 2=Auto | — | 0 | 2 | — | — | R | Unit Mode |
| 9304 | Unit_EcoCmfNight_Status | 1=Economy; 2=Comfort; 3=Night | — | 1 | 3 | — | — | R | Unit Mode |
| 9305 | Unit_Alarm | Boolean | — | — | — | — | — | R | Unit Alarm |
| 9306 | T_RegulationProbe | Signed 16-bit | — | — | — | °C | XXX.Y | R | Temperature Regulation Probe |
| 9307 | T_CurrentSetpointByPar | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Setpoint by parameter based on selected mode |
| 9308 | T_CurrentSupplySetpoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Supply Setpoint |
| 9309 | T_CurrentReturnSetpoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Return Setpoint |
| 9310 | T_DewPointSetPoint | Signed 16-bit | — | — | — | °C | XXX.Y | R | Current Dewpoint Setpoint |
| 9311 | RH_CurrentSetpoint | Signed 16-bit | — | — | — | %R.H. | — | R | Current Return Setpoint |
| 9312 | AirQ_CurrentSetpointVOC | Signed 16-bit | — | — | — | % | — | R | Current Setpoint VOC |
| 9313 | AirQ_CurrentSetpointCO2 | Signed 16-bit | — | — | — | ppm | — | R | Current Setpoint CO2 |
| 9314 | Pr_CurrentSupplySetpoint | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Supply Setpoint - Units depends on Fan_Supply_Pressure_Flow |
| 9316 | Pr_CurrentReturnSetpoint | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Return Setpoint - Units depends on Fan_Return_Pressure_Flow |
| 9318 | RH_RegulationProbe | Signed 16-bit | — | — | — | %R.H. | — | R | Humdity Regulation Probe |
| 9319 | AirQ_RegulationProbe | Signed 16-bit | — | — | — | %/ppm | — | R | Air Quality Regulation Probe |
| 9320 | Pr_Flow_Supply | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Supply Sensor - Units depends on Fan_Supply_Pressure_Flow |
| 9322 | Pr_Flow_Return | Signed 32-bit | — | — | — | Pa-m3/h | — | R | Current Fan Return Sensor - Units depends on Fan_Return_Pressure_Flow |
| 9350 | OnOffRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit On/Off via request via Web/Modbus |
| 9351 | ChangeSeasonRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit Season Change request via Web/Modbus |
| 9352 | ComfortEcoNightRequestFromWeb | Boolean | 0 | — | — | — | — | RW | Unit Comfort/Eco/Night request via Web/Modbus |
| 9480 | History000 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9481 | History001 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9482 | History002 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9483 | History003 | Signed 16-bit | — | — | — | — | — | R | Most recent value |
| 9484 | HistoricalPosition | Unsigned 16-bit | 0 | — | — | — | — | RW | Historical Postion Required |
| 9485 | Historical_Value_Code | 0 = ---; 1 = A01-Supply Pr.; 2 = A02-Return Pr.; 3 = A03-External Pr.; 4 = A04-Expulsion Pr.; 5 = A05-Preheating Pr.; 6 = A06-Saturation Pr.; 7 = A07-Antifreeze Pr.; 8 = A08-CO2 Pr.; 9 = A09-Supply Press. Pr.; 10 = A10-Return Press. Pr.; 11 = A11-Hum. Supply Pr.; 12 = A12-Hum. Return Pr.; 13 = A13-VOC Pr.; 14 = A14-Hum. External Pr.; 15 = A15-; 16 = A16-; 17 = A17-; 18 = A18-; 19 = A19-; 20 = A20-; 21 = A21-; 22 = A22-; 23 = A23-; 24 = A24-; 25 = A25-; 26 = A26-Airflow Prb Sup.; 27 = A27-Airflow Prb Ret.; 28 = A28-Airflow Prb Sup.2; 29 = A29-Airflow Prb Ret.2; 30 = A30-Fan Supply; 31 = A31-Fan Return; 32 = A32-Fire; 33 = A33-Door; | — | 0 | 65 | — | — | R | Historical: Alarm Code |
| 9485 | Historical_Value_Code | 34 = A34-Antifreeze; 35 = A35-Airflow Supply; 36 = A36-Airflow Return; 37 = A37-Humidifier; 38 = A38-Preheater; 39 = A39-Heater; 40 = A40-Postheater; 41 = A41-Recovery; 42 = A42-Filter 1; 43 = A43-Filter 2; 44 = A44-Filter 3; 45 = A45-Filter 4; 46 = A46-Fan Supply 2; 47 = A47-Fan Return 2; 48 = A48-Airflow Supply 2; 49 = A49-Airflow Return 2; 50 = A50-Cond. Unit; 51 = A51-Real Time Clock; 52 = A52-Fan Maintenance; 53 = A53-Modbus Fan Config. Timeout 54 = A54-Modbus Fan Supply Communication; 55 = A55-Modbus Fan Return Communication; 56 = A56-Modbus Fan Supply 2 Communication; 57 = A57-Modbus Fan Return 2 Communication; 58 = A58-Filter 5; 59 = A59-; 60 = A60-Log Error; 61 = A61-Can Expansion 1; 62 = A62-Can Expansion 2; 63 = A63-Can Expansion 3; 64 = A64-Can Expansion 4; 65 = A65-Can Expansion 5 66 = A66-Cond. Unit 2 67 = A67-Cond. Unit 3 68 =A68-Cond. Unit 4 | — | 0 | 65 | — | — | R | Historical: Alarm Code |
| 9486 | Historical_Value_Date | Signed 16-bit | — | — | — | — | XX.YY | R | Historical: Alarm Date |
| 9487 | Historical_Value_Time | Signed 16-bit | — | — | — | — | HH:MM | R | Historical: Alarm Time |
| 9488 | Historical_Value_SecStatus | Signed 16-bit | — | — | — | — | XX.YY | R | Historical: Alarm Seconds and Status: 100x+seconds (x=0 restored, x=1 active, x=2 wait for reset) |
| 9489 | Historical_Number_alarms | Signed 16-bit | — | — | — | — | — | R | Historical: Number of stored alarms |
| 9490 | Historical_Reset | Boolean | 0 | — | — | — | — | RW | Historical: Reset Request |
| 9491 | Historical_Value_Sec | Signed 16-bit | — | — | — | — | — | R | Historical: Alarm Time Seconds |
| 9492 | Historical_Value_Status | AlarmEnum | — | — | — | — | — | R | Historical: Alarm Status |
| 9520 | Alxx_Reset | Boolean | — | — | — | — | — | RW | Alarm reset request command via Modbus |
| 9521 | Al01_SupplyProbe | 0=Not Active; 1=Active; 2=Manual Reset | — | 0 | 2 | — | — | R | Al01-Supply Temperature Probe Error |
| 9522 | Al02_ReturnProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A02-Return Temperature Probe Error |
| 9523 | Al03_ExternalProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A03-External Temperature Probe Error |
| 9524 | Al04_ExpulsionProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A04-Expulsion Temperature Probe Error |
| 9525 | Al05_PreHeatingProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A05-Preheating Temperature Probe Error |
| 9526 | Al06_SaturationProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A06-Saturation Temperature Probe Error |
| 9527 | Al07_AntifreezeProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A07-Antifreeze Temperature Probe Error |
| 9528 | Al08_AirQualityProbe_CO2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A08-CO2 Probe Error |
| 9529 | Al09_SupplyPressureProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A09-Supply Pressure Probe Error |
| 9530 | Al10_ReturnPressureProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A10-Return Pressure Probe Error |
| 9531 | Al11_SupplyHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A11-Hum. Supply Probe Error |
| 9532 | Al12_ReturnHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A12-Hum. Return Probe Error |
| 9533 | Al13_AirQualityProbe_VOC | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A13-VOC Probe Error |
| 9534 | Al14_ExternalHumidityProbe | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A14-Hum. External Probe Error |
| 9535… 9545 | Future use | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Future Usse |
| 9546 | Al26_SensAirFlowSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A26-Supply Airflow by Probe |
| 9547 | Al27_SensAirFlowReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A27-Return Airflow by Probe |
| 9548 | Al28_SensAirFlowSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A28-Airflow Prb Sup.2 |
| 9549 | Al29_SensAirFlowReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A29-Airflow Prb Ret.2 |
| 9550 | Al30_FanThermalSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A30-Fan Supply |
| 9551 | Al31_FanThermalReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A31-Fan Return |
| 9552 | Al32_Fire | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A32-Fire |
| 9553 | Al33_Door | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A33-Door |
| 9554 | Al34_Antifreeze | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A34-Antifreeze |
| 9555 | Al35_AirFlowSupply | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A35-Airflow Supply |
| 9556 | Al36_AirFlowReturn | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A36-Airflow Return |
| 9557 | Al37_Humidifier | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A37-Humidifier |
| 9558 | Al38_PreHeater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A38-Preheater |
| 9559 | Al39_Heater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A39-Heater |
| 9560 | Al40_PostHeater | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A40-Postheater |
| 9561 | Al41_RotaryWheel | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A41-Recovery |
| 9562 | Al42_Filter1 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A42-Filter 1 |
| 9563 | Al43_Filter2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A43-Filter 2 |
| 9564 | Al44_Filter3 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A44-Filter 3 |
| 9565 | Al45_Filter4 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A45-Filter 4 |
| 9566 | Al46_FanThermalSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A46-Fan Supply 2 |
| 9567 | Al47_FanThermalReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A47-Fan Return 2 |
| 9568 | Al48_AirFlowSupplyBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A48-Airflow Supply 2 |
| 9569 | Al49_AirFlowReturnBck | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A49-Airflow Return 2 |
| 9570 | Al50_CondUnit | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A50-Cond. Unit |
| 9571 | Al51_RTC | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A51-Real Time Clock |
| 9572 | Al52_FanMaintenance | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A52-Fan Maintenance |
| 9573 | Al53_ModbusFanCfg | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A53-Modbus Fan Config. Timeout |
| 9574 | Al54_FanSupplyCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A54-Modbus Fan Supply Communication |
| 9575 | Al55_FanReturnCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A55-Modbus Fan Return Communication |
| 9576 | Al56_FanSupplyBckCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A56-Modbus Fan Supply 2 Communication |
| 9577 | Al57_FanReturnBckCom | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A57-Modbus Fan Return 2 Communication |
| 9578 | Al58_Filter5 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A58-Filter 5 |
| 9579 | Al59_ | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | — |
| 9580 | Al60_LogError | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A60-Log Error |
| 9581 | Al61_Exp1 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A61-Can Expansion 1 |
| 9582 | Al62_Exp2 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A62-Can Expansion 2 |
| 9583 | Al63_Exp3 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A63-Can Expansion 3 |
| 9584 | Al64_Exp4 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A64-Can Expansion 4 |
| 9585 | Al65_Exp5 | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | A65-Can Expansion 5 |
| 9586… 9618 | Future use |  |  |  |  |  |  | R | Future use |
| 9619 | Al99_FanSupply_1b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al99-Fan Supply 1b Com Alarm |
| 9620 | Al100_FanSupply_1c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al100-Fan Supply 1c Com Alarm |
| 9621 | Al101_FanReturn_1b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al101-Fan Return 1b Com Alarm |
| 9622 | Al102_FanReturn_1c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al102-Fan Return 1c Com Alarm |
| 9623 | Al103_FanSupply_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al103-Fan Supply 2b Com Alarm |
| 9624 | Al104_FanSupply_2c_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al104-Fan Supply 2c Com Alarm |
| 9625 | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al105-Fan Return 2b Com Alarm |
| 9626 | Al105_FanReturn_2b_Com | See Al01_SupplyProbe | — | 0 | 2 | — | — | R | Al106-Fan Return 2c Com Alarm |
| 9670 | AI_Exp1_1 | Signed 16-bit | — | — | — | — | — | R | Physical Input 1 Exp1 |
| 9671 | AI_Exp1_2 | Signed 16-bit | — | — | — | — | — | R | Physical Input 2 Exp1 |
| 9672 | AI_Exp1_3 | Signed 16-bit | — | — | — | — | — | R | Physical Input 3 Exp1 |
| 9673 | AI_Exp1_4 | Signed 16-bit | — | — | — | — | — | R | Physical Input 4 Exp1 |
| 9674 | AI_Exp2_1 | Signed 16-bit | — | — | — | — | — | R | Physical Input 1 Exp2 |
| 9675 | AI_Exp2_2 | Signed 16-bit | — | — | — | — | — | R | Physical Input 2 Exp2 |
| 9676 | AI_Exp2_3 | Signed 16-bit | — | — | — | — | — | R | Physical Input 3 Exp2 |
| 9677 | AI_Exp2_4 | Signed 16-bit | — | — | — | — | — | R | Physical Input 4 Exp2 |
| 9720 | AI_LogicIndex_0 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Supply Temperature |
| 9721 | AI_LogicIndex_1 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Return Temperature |
| 9722 | AI_LogicIndex_2 | Signed 16-bit | — | — | — | °C | XXX.Y | R | External Temperature |
| 9723 | AI_LogicIndex_3 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Expulsion Temperature |
| 9724 | AI_LogicIndex_4 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Preheating Temp, |
| 9725 | AI_LogicIndex_5 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Saturation Temperature |
| 9726 | AI_LogicIndex_6 | Signed 16-bit | — | — | — | °C | XXX.Y | R | Antifreeze Temperature |
| 9727 | AI_LogicIndex_7 | Signed 16-bit | — | — | — | ppm | — | R | Air Quality - VOC |
| 9728 | AI_LogicIndex_8 | Signed 16-bit | — | — | — | % | XXX.Y | R | Air Quality - CO2 |
| 9729 | AI_LogicIndex_9 | Signed 16-bit | — | — | — | pa | — | R | Supply Pressure |
| 9730 | AI_LogicIndex_10 | Signed 16-bit | — | — | — | pa | — | R | Return Pressure |
| 9731 | AI_LogicIndex_11 | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Humidity |
| 9732 | AI_LogicIndex_12 | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Humidity |
| 9733 | AI_LogicIndex_13 | Signed 16-bit | — | — | — | % | XXX.Y | R | External Humidity |
| 9734 | AI_LogicIndex_14 | Signed 32-bit | — | — | — | m3/h | — | R | Supply Flow Testing |
| 9736 | AI_LogicIndex_15 | Signed 32-bit | — | — | — | m3/h | — | R | Return Flow Testing |
| 9738 | AI_free4 | Signed 16-bit | — | — | — | — | — | R | — |
| 9739 | AI_free5 | Signed 16-bit | — | — | — | — | — | R | — |
| 9740 | AI_free6 | Signed 16-bit | — | — | — | — | — | R | — |
| 9741 | AI_free7 | Signed 16-bit | — | — | — | — | — | R | — |
| 9742 | AI_free8 | Signed 16-bit | — | — | — | — | — | R | — |
| 9743 | AI_free9 | Signed 16-bit | — | — | — | — | — | R | — |
| 9744 | AI_free10 | Signed 16-bit | — | — | — | — | — | R | — |
| 9745 | DI_Voltage_LogicIndex_0 | 0 = 0V; 1 = 24V; 2 = Not Used | — | 0 | 2 | — | — | R | Supply Fan Thermal - Physical Status |
| 9746 | DI_Voltage_LogicIndex_1 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan Thermal - Physical Status |
| 9747 | DI_Voltage_LogicIndex_2 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | On/Off Input - Physical Status |
| 9748 | DI_Voltage_LogicIndex_3 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Fire Alarm - Physical Status |
| 9749 | DI_Voltage_LogicIndex_4 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Mode Input - Physical Status |
| 9750 | DI_Voltage_LogicIndex_5 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Door - Physical Status |
| 9751 | DI_Voltage_LogicIndex_6 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Antifreeze - Physical Status |
| 9752 | DI_Voltage_LogicIndex_7 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Airflow - Physical Status |
| 9753 | DI_Voltage_LogicIndex_8 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Airflow - Physical Status |
| 9754 | DI_Voltage_LogicIndex_9 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Humidifier Alarm - Physical Status |
| 9755 | DI_Voltage_LogicIndex_10 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Preheater Alarm - Physical Status |
| 9756 | DI_Voltage_LogicIndex_11 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Postheater Alarm - Physical Status |
| 9757 | DI_Voltage_LogicIndex_12 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Rotary Wheel Alarm - Physical Status |
| 9758 | DI_Voltage_LogicIndex_13 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 1 Alarm - Physical Status |
| 9759 | DI_Voltage_LogicIndex_14 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 2 Alarm - Physical Status |
| 9760 | DI_Voltage_LogicIndex_15 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 3 Alarm - Physical Status |
| 9761 | DI_Voltage_LogicIndex_16 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Filter 4 Alarm - Physical Status |
| 9762 | DI_Voltage_LogicIndex_17 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 Th. - Physical Status |
| 9763 | DI_Voltage_LogicIndex_18 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 Th. - Physical Status |
| 9764 | DI_Voltage_LogicIndex_19 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 Airflow - Physical Status |
| 9765 | DI_Voltage_LogicIndex_20 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 Airflow - Physical Status |
| 9766 | DI_Voltage_LogicIndex_21 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | Cond. Unit Alarm - Physical Status |
| 9767 | DI_Voltage_LogicIndex_22 | See DI_Voltage_LogicIndex_0 | — | 0 | 2 | — | — | R | El. Heater Alarm - Physical Status |
| 9768 | DI_Voltage_LogicIndex_23 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 2 Alarm - Physical Status |
| 9769 | DI_Voltage_LogicIndex_24 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 3 Alarm - Physical Status |
| 9770 | DI_Voltage_LogicIndex_25 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 4 Alarm - Physical Status |
| 9771 | DI_Voltage_LogicIndex_26 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 1 Defrost - Physical Status |
| 9772 | DI_Voltage_LogicIndex_27 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 2 Defrost - Physical Status |
| 9773 | DI_Voltage_LogicIndex_28 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 3 Defrost - Physical Status |
| 9774 | DI_Voltage_LogicIndex_29 | Signed 16-bit | — | — | — | — | — | R | Cond. Unit 4 Defrost - Physical Status |
| 9775 | DI_Voltage_LogicIndex_30 | Signed 16-bit | — | — | — | — | — | R | Filter 5 Alarm - Physical Status |
| 9776 | DI_free9 | Signed 16-bit | — | — | — | — | — | R | — |
| 9777 | DI_free10 | Signed 16-bit | — | — | — | — | — | R | — |
| 9778 | DO_LogicIndex_0 | 0 = Off; 1 = On; 2 = Not Used | — | 0 | 2 | — | — | R | Supply Fan - Logic Status |
| 9779 | DO_LogicIndex_1 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan - Logic Status |
| 9780 | DO_LogicIndex_2 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | On Off - Logic Status |
| 9781 | DO_LogicIndex_3 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Alarm - Logic Status |
| 9782 | DO_LogicIndex_4 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Mode - Logic Status |
| 9783 | DO_LogicIndex_5 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Ext. Dampers - Logic Status |
| 9784 | DO_LogicIndex_6 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Bypass Damper - Logic Status |
| 9785 | DO_LogicIndex_7 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Damper - Logic Status |
| 9786 | DO_LogicIndex_8 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Damper - Logic Status |
| 9787 | DO_LogicIndex_9 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pump Preheat - Logic Status |
| 9788 | DO_LogicIndex_10 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pump Postheat - Logic Status |
| 9789 | DO_LogicIndex_11 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Pump - Logic Status |
| 9790 | DO_LogicIndex_12 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 1 - Logic Status |
| 9791 | DO_LogicIndex_13 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 2 - Logic Status |
| 9792 | DO_LogicIndex_14 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 3 - Logic Status |
| 9793 | DO_LogicIndex_15 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Cool/CH Step 4 - Logic Status |
| 9794 | DO_LogicIndex_16 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heat Pump - Logic Status |
| 9795 | DO_LogicIndex_17 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 1 - Logic Status |
| 9796 | DO_LogicIndex_18 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 2 - Logic Status |
| 9797 | DO_LogicIndex_19 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Heater Step 3 - Logic Status |
| 9798 | DO_LogicIndex_20 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 1 - Logic Status |
| 9799 | DO_LogicIndex_21 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 2 - Logic Status |
| 9800 | DO_LogicIndex_22 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Pre Heater Step 3 - Logic Status |
| 9801 | DO_LogicIndex_23 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 1 - Logic Status |
| 9802 | DO_LogicIndex_24 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 2 - Logic Status |
| 9803 | DO_LogicIndex_25 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Post Heater Step 3 - Logic Status |
| 9804 | DO_LogicIndex_26 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Humidifier - Logic Status |
| 9805 | DO_LogicIndex_27 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Rotary Wheel / Exchanger - Logic Status |
| 9806 | DO_LogicIndex_28 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Fan 2 - Logic Status |
| 9807 | DO_LogicIndex_29 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Fan 2 - Logic Status |
| 9808 | DO_LogicIndex_30 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Supply Damper 2 - Logic Status |
| 9809 | DO_LogicIndex_31 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | Return Damper 2 - Logic Status |
| 9810 | DO_free1 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9811 | DO_free2 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9812 | DO_free3 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9813 | DO_free4 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9814 | DO_free5 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9815 | DO_free6 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9816 | DO_free7 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9817 | DO_free8 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9818 | DO_free9 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9819 | DO_free10 | See DO_LogicIndex_0 | — | 0 | 2 | — | — | R | — |
| 9820 | AO_LogicIndex_0 | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Fan |
| 9821 | AO_LogicIndex_1 | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Fan |
| 9822 | AO_LogicIndex_2 | Signed 16-bit | — | — | — | % | XXX.Y | R | Ext. Dampers |
| 9823 | AO_LogicIndex_3 | Signed 16-bit | — | — | — | % | XXX.Y | R | Bypass Damper |
| 9824 | AO_LogicIndex_4 | Signed 16-bit | — | — | — | % | XXX.Y | R | Cool - C/H Valve |
| 9825 | AO_LogicIndex_5 | Signed 16-bit | — | — | — | % | XXX.Y | R | Heat Valve |
| 9826 | AO_LogicIndex_6 | Signed 16-bit | — | — | — | % | XXX.Y | R | Pre Heater |
| 9827 | AO_LogicIndex_7 | Signed 16-bit | — | — | — | % | XXX.Y | R | Post Heater |
| 9828 | AO_LogicIndex_8 | Signed 16-bit | — | — | — | % | XXX.Y | R | Rotary Wheel / Exchanger |
| 9829 | AO_LogicIndex_9 | Signed 16-bit | — | — | — | % | XXX.Y | R | Humidifier |
| 9830 | AO_free1 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9831 | AO_free2 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9832 | AO_free3 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9833 | AO_free4 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9834 | AO_free5 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9835 | AO_free6 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9836 | AO_free7 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9837 | AO_free8 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9838 | AO_free9 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9839 | AO_free10 | Signed 16-bit | — | — | — | % | XXX.Y | R | — |
| 9840 | AI_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9841 | AI_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9842 | AI_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9843 | AI_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9844 | AI_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9845 | AI_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9846 | AI_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9847 | AI_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9848 | AI_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9849 | AI_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9850 | AI_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9851 | AI_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9852 | AI_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9853 | AI_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9854 | AI_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9855 | AI_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9856 | AI_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9857 | AI_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9858 | AI_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9859 | AI_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9860 | AI_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9861 | AI_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9862 | AI_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9863 | DI_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9864 | DI_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9865 | DI_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9866 | DI_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9867 | DI_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9868 | DI_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9869 | DI_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9870 | DI_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9871 | DI_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9872 | DI_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9873 | DI_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9874 | DI_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9875 | DI_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9876 | DI_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9877 | DI_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9878 | DI_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9879 | DI_Map_LogicIndex_16 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9880 | DI_Map_LogicIndex_17 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9881 | DI_Map_LogicIndex_18 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9882 | DI_Map_LogicIndex_19 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9883 | DI_Map_LogicIndex_20 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9884 | DI_Map_LogicIndex_21 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9885 | DI_Map_LogicIndex_22 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9886 | DI_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9887 | DI_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9888 | DI_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9889 | DI_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9890 | DI_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9891 | DI_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9892 | DI_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9893 | DI_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9894 | DI_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9895 | DI_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9896 | DO_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9897 | DO_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9898 | DO_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9899 | DO_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9900 | DO_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9901 | DO_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9902 | DO_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9903 | DO_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9904 | DO_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9905 | DO_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9906 | DO_Map_LogicIndex_10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9907 | DO_Map_LogicIndex_11 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9908 | DO_Map_LogicIndex_12 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9909 | DO_Map_LogicIndex_13 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9910 | DO_Map_LogicIndex_14 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9911 | DO_Map_LogicIndex_15 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9912 | DO_Map_LogicIndex_16 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9913 | DO_Map_LogicIndex_17 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9914 | DO_Map_LogicIndex_18 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9915 | DO_Map_LogicIndex_19 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9916 | DO_Map_LogicIndex_20 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9917 | DO_Map_LogicIndex_21 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9918 | DO_Map_LogicIndex_22 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9919 | DO_Map_LogicIndex_23 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9920 | DO_Map_LogicIndex_24 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9921 | DO_Map_LogicIndex_25 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9922 | DO_Map_LogicIndex_26 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9923 | DO_Map_LogicIndex_27 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9924 | DO_Map_LogicIndex_28 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9925 | DO_Map_LogicIndex_29 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9926 | DO_Map_LogicIndex_30 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9927 | DO_Map_LogicIndex_31 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9928 | DO_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9929 | DO_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9930 | DO_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9931 | DO_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9932 | DO_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9933 | DO_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9934 | DO_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9935 | DO_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9936 | DO_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9937 | DO_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9938 | AO_Map_LogicIndex_0 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9939 | AO_Map_LogicIndex_1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9940 | AO_Map_LogicIndex_2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9941 | AO_Map_LogicIndex_3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9942 | AO_Map_LogicIndex_4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9943 | AO_Map_LogicIndex_5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9944 | AO_Map_LogicIndex_6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9945 | AO_Map_LogicIndex_7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9946 | AO_Map_LogicIndex_8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9947 | AO_Map_LogicIndex_9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9948 | AO_Map_LogicIndex_free1 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9949 | AO_Map_LogicIndex_free2 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9950 | AO_Map_LogicIndex_free3 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9951 | AO_Map_LogicIndex_free4 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9952 | AO_Map_LogicIndex_free5 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9953 | AO_Map_LogicIndex_free6 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9954 | AO_Map_LogicIndex_free7 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9955 | AO_Map_LogicIndex_free8 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9956 | AO_Map_LogicIndex_free9 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9957 | AO_Map_LogicIndex_free10 | Unsigned 8-bit | — | — | — | — | — | R | Physical mapping of logic index i |
| 9980 | Unit_DD | Unsigned 16-bit | — | — | — | days | — | R | Unit Working Days |
| 9981 | Unit_HH | Unsigned 16-bit | — | — | — | hours | — | R | Unit Working Hours |
| 9982 | FanSupply_DD | Unsigned 16-bit | — | — | — | days | — | R | Supply Fan Working Days |
| 9983 | FanSupply_HH | Unsigned 16-bit | — | — | — | hours | — | R | Supply Fan Working Hours |
| 9984 | FanReturn_DD | Unsigned 16-bit | — | — | — | days | — | R | Return Fan Working Days |
| 9985 | FanReturn_HH | Unsigned 16-bit | — | — | — | hours | — | R | Return Fan Working Hours |
| 9986 | FanSupplyBck_DD | Unsigned 16-bit | — | — | — | days | — | R | Supply Fan 2 Working Days |
| 9987 | FanSupplyBck_HH | Unsigned 16-bit | — | — | — | hours | — | R | Supply Fan 2 Working Hours |
| 9988 | FanReturnBck_DD | Unsigned 16-bit | — | — | — | days | — | R | Return Fan 2 Working Days |
| 9989 | FanReturnBck_HH | Unsigned 16-bit | — | — | — | hours | — | R | Return Fan 2 Working Hours |
| 10000 | Status_PlantMode | 0=Cool; 1=Heat; 2=Auto | — | 0 | 2 | — | — | R | Unit Working Mode |
| 10001 | Status_PID_TSupplyCool | Signed 16-bit | — | — | — | % | — | R | Cooling Regulator Request |
| 10002 | Status_PID_TSupplyHeat | Signed 16-bit | — | — | — | % | — | R | Heating Regulator Request |
| 10003 | Status_PID_Humid | Signed 16-bit | — | — | — | % | — | R | Hmidification Regulator Request |
| 10004 | Status_PID_DeHumid | Signed 16-bit | — | — | — | % | — | R | Dehumidification Regulator Request |
| 10005 | Status_PID_AirQ | Signed 16-bit | — | — | — | % | — | R | Air Quality Regulator Request |
| 10006 | Status_PID_PrSupply | Signed 16-bit | — | — | — | % | — | R | Supply Fan Regulator Request |
| 10007 | Status_PID_PrReturn | Signed 16-bit | — | — | — | % | — | R | Return Fan Regulator Request |
| 10008 | Status_PID_PreHeater | Signed 16-bit | — | — | — | % | — | R | Preheater Regulator Request |
| 10009 | Status_OutCool | Signed 16-bit | — | — | — | % | — | R | Cooling Output |
| 10010 | Status_OutPre | Signed 16-bit | — | — | — | % | — | R | Preheating Output |
| 10011 | Status_OutHeat | Signed 16-bit | — | — | — | % | — | R | Heating Output |
| 10012 | Status_OutPost | Signed 16-bit | — | — | — | % | — | R | Post Heating Output |
| 10013 | Status_OutRec | Signed 16-bit | — | — | — | % | — | R | Recovery Output |
| 10014 | Status_OutHum | Signed 16-bit | — | — | — | % | — | R | Humidifier Output |
| 10015 | Status_FanSupply | Signed 16-bit | — | — | — | % | — | R | Fan Supply Speed |
| 10016 | Status_FanReturn | Signed 16-bit | — | — | — | % | — | R | Fan Return Speed |
| 10017 | Status_ExtDamper | Signed 16-bit | — | — | — | % | — | R | External Damper Status |
| 10018 | Status_FreeCooling | Boolean | — | — | — | — | — | R | Free Cooling Status |
| 10019 | Status_FreeHeating | Boolean | — | — | — | — | — | R | Free Heating Status |
| 10020 | Status_ActuatorsOffbyFCH | Boolean | — | — | — | — | — | R | Actuators off by Free Cooling/Heating |
| 10021 | Status_FCHreq | Signed 16-bit | — | — | — | % | — | R | Free Cooling/Heating Request |
| 10022 | Status_RecoveryCooling | Boolean | — | — | — | — | — | R | Cooling Recovery Status |
| 10023 | Status_RecoveryHeating | Boolean | — | — | — | — | — | R | Heating Recovery Status |
| 10024 | Status_DefrostFan | Boolean | — | — | — | — | — | R | Defrost with Fan Status |
| 10025 | Status_DefrostDamper | Boolean | — | — | — | — | — | R | Defrost with Damper Status |
| 10026 | Status_DefrostPreHeat | Boolean | — | — | — | — | — | R | Defrost with Preheating Status |
| 10027 | Status_DefrostFanRed | Signed 16-bit | — | — | — | % | XXX.Y | R | Defrost Supply Fan Speed Reduction |
| 10028 | Status_LowTempSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | Low Supply Limit Regulator Request |
| 10029 | Status_HighTempSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Supply Limit Regulator Request |
| 10030 | Status_HighTempPreHeatLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Preheater Limit Regulator Request |
| 10031 | Status_HighHumSupplyLimit | Signed 16-bit | — | — | — | % | XXX.Y | R | High Humidity Limit Regulator Request |
| 10032 | Status_ExtSHum | Signed 16-bit | — | — | — | g/Kg | XXX.Y | R | External Specific Humidity |
| 10033 | Status_RetSHum | Signed 16-bit | — | — | — | g/Kg | XXX.Y | R | Return Specific Humidity |
| 10034 | Status_Supply1_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Supply Ziehl/EBM Speed |
| 10035 | Status_Supply1_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Supply Ziehl/EBM DC Voltage |
| 10036 | Status_Supply1_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Supply Ziehl/EBM Current |
| 10037 | Status_Supply1_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Supply ATV212 Speed |
| 10038 | Status_Supply1_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply ATV212 DC Voltage |
| 10039 | Status_Supply1_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Supply ATV212 DC Current |
| 10040 | Status_Supply2_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Supply Backup Ziehl/EBM Speed |
| 10041 | Status_Supply2_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Supply Backup Ziehl/EBM DC Voltage |
| 10042 | Status_Supply2_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Supply Backup Ziehl/EBM Current |
| 10043 | Status_Supply2_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Supply Backup ATV212 Speed |
| 10044 | Status_Supply2_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Supply Backup ATV212 DC Voltage |
| 10045 | Status_Supply2_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Supply Backup ATV212 DC Current |
| 10046 | Status_Return1_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Return Ziehl/EBM Speed |
| 10047 | Status_Return1_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Return Ziehl/EBM DC Voltage |
| 10048 | Status_Return1_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Return Ziehl/EBM Current |
| 10049 | Status_Return1_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Return ATV212 Speed |
| 10050 | Status_Return1_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Return ATV212 DC Voltage |
| 10051 | Status_Return1_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Return ATV212 DC Current |
| 10052 | Status_Return2_FansActualSpeed | Signed 16-bit | — | — | — | rpm | — | R | Return Backup Ziehl/EBM Speed |
| 10053 | Status_Return2_FansVoltage | Signed 16-bit | — | — | — | V | — | R | Return Backup Ziehl/EBM DC Voltage |
| 10054 | Status_Return2_FansCurrent | Signed 16-bit | — | — | — | A | — | R | Return Backup Ziehl/EBM Current |
| 10055 | Status_Return2_FansActualSpeedHz | Signed 16-bit | — | — | — | Hz | XXX.Y | R | Return Backup ATV212 Speed |
| 10056 | Status_Return2_FansVoltagePerc | Signed 16-bit | — | — | — | % | XXX.Y | R | Return Backup ATV212 DC Voltage |
| 10057 | Status_Return2_FansCurrentPerc | Signed 16-bit | — | — | — | % | XX.YY | R | Return Backup ATV212 DC Current |
| 10100 | StartMonth | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | Start Month - Log Period Export to USB |
| 10101 | EndMonth | Unsigned 8-bit | 1 | 1 | 12 | — | — | RW | End Month - Log Period Export to USB |
| 10102 | StartYear | Unsigned 8-bit | 16 | 0 | 99 | — | — | RW | Start Year - Log Period Export to USB |
| 10103 | EndYear | Unsigned 8-bit | 16 | 0 | 99 | — | — | RW | End Year - Log Period Export to USB |
| 10104 | SavingInProgress | Boolean | — | — | — | — | — | R | Log Export to usb ongoing - Log Export to USB |
| 10105 | SaveOk | Unsigned 16-bit | — | — | — | — | — | R | Number of files correctly exported- Log Export to USB |
| 10106 | SaveFailed | Unsigned 16-bit | — | — | — | — | — | R | Number of files not exported- Log Export to USB |
| 10107 | SavePercent | Unsigned 16-bit | — | — | — | — | — | R | Percentage of exported files- Log Export to USB |
| 10108 | SavingAllowed | Boolean | — | — | — | — | — | R | Export can start - Log Export to USB |
| 10109 | LoggingError | Boolean | — | — | — | — | — | R | Log Error- Log Export to USB |
| 10110 | FileDimension | Unsigned 32-bit | — | — | — | — | — | R | Size of the current log file- Log Export to USB |
| 10112 | TotalRecordE2retain | Unsigned 32-bit | — | — | — | — | — | R | Record saved - Log Export to USB |
| 10114 | microSdMounted | Boolean | — | — | — | — | — | R | microSD Mounted |
| 10115 | microSdError | Boolean | — | — | — | — | — | R | microSD Error |
| 10116 | microSdStatus | 0=Not present; 1=Unsafe Removed; 2=Not Mounted; 3=Mounted | — | 0 | 3 | — | — | R | microSd Status |
| 10117 | microSdInfo | 0=...; 1=Release SD; 2=Ready to remove/mount; 3=Ready for log; 4=...; 5=insert SD..; 6=Release SD; 7=Retry command..; 8=Yet mounted | — | 0 | 8 | — | — | R | microSd Info |
| 10498 | BridgeStatus | Boolean | — | — | — | — | — | R | Bridge Function Status |
| 11500 | MdbZiehlSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11501 | MdbZiehlReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11502 | MdbZiehlSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11503 | MdbZiehlReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11504 | MdbEBMSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11505 | MdbEBMReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11506 | MdbEBMSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11507 | MdbEBMReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11508 | MdbATVSupplyMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11509 | MdbATVReturnMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11510 | MdbATVSupplyBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11511 | MdbATVReturnBckMsgError | Unsigned 16-bit | — | — | — | Num | — | R | — |
| 11512 | MdbZiehlSupply_1b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11513 | MdbZiehlReturn_1b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11514 | MdbZiehlSupply_2b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11515 | MdbZiehlReturn_2b_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11516 | MdbZiehlSupply_1c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11517 | MdbZiehlReturn_1c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11518 | MdbZiehlSupply_2c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11519 | MdbZiehlReturn_2c_MsgError | Unsigned 16-bit | — | — | — | Num | — | R |  |
| 11600 | CondUnit1_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 1 Working Days |
| 11601 | CondUnit1_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 1 Working Hours |
| 11602 | CondUnit2_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 2 Working Days |
| 11603 | CondUnit2_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 2 Working Hours |
| 11604 | CondUnit3_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 3 Working Days |
| 11605 | CondUnit3_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 3 Working Hours |
| 11606 | CondUnit4_DD | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 4 Working Days |
| 11607 | CondUnit4_HH | Unsigned 16-bit |  |  |  |  |  |  | Condensing Unit 4 Working Hours |

Tabella 100 - Tabella Modbus Stati