## Check # BACnet Objects
HVAC Solution Center
BACnet Objects EEPROM Size Calculator
BACnet Object | # Objects | Bytes/Obj | MAX Objs | calc | check num data |  | check max objs |  | err check
Device | 1 | 2 | 1 | 2 | 2 | 1 | ok | 1 | 1
Analog Value |  | 74 | 256 | 0 | 0 | 1 | ok | 1 | 1
Analog Input |  | 70 |  | 0 | 0 | 1 | ok | 1 | 1
Binary Value |  | 62 | 256 | 0 | 0 | 1 | ok | 1 | 1
Binary Input |  | 50 |  | 0 | 0 | 1 | ok | 1 | 1
Calendar |  | 512 | 4 | 0 | 0 | 1 | ok | 1 | 1
MSV |  | 58 | 32 | 0 | 0 | 1 | ok | 1 | 1
MSI |  | 54 |  | 0 | 0 | 1 | ok | 1 | 1
Schedule no exception |  | 558 | 16 | 0 | 0 | 1 | ok | 1 | 1
Schedule w exception |  | 1146 |  | 0 | 0 | 1 | ok | 1 | 1
1
Total amount | 0.002 | kbytes
Available EEPROM size | 16 | Kbytes
Does it fit in EEPROM? |  | YES
0

## Calc
Enumerativi: 32bit, DINT. String 32bit |  | amount inside of structure | type amount in object | single size [byte] | tot size
Object | Device |  |  |  |  | Data format | bits | bytes
Attributes in EEPROM | Type |  |  | TOT | 2 | BOOL | 16 | 2
Vendor_ID | UINT | 1 | 1 | 2 | 2 | WORD | 16 | 2
[6 empty] | DWORD | 32 | 4
Object | Analog Value |  |  |  |  | BYTE | 16 | 2
Attributes in EEPROM | Type |  |  | TOT | 74 | SINT | 16 | 2
Description | STRING | 1 | 1 | 32 | 32 | INT | 16 | 2
COV_Increment | REAL | 1 | 1 | 4 | 4 | DINT | 32 | 4
Time_Delay | UDINT | 1 | 1 | 4 | 4 | USINT | 16 | 2
High_Limit | REAL | 1 | 1 | 4 | 4 | UINT | 16 | 2
Low_Limit | REAL | 1 | 1 | 4 | 4 | REAL | 32 | 4
Deadband | REAL | 1 | 1 | 4 | 4 | STRING | 32 | 32
Limit_En[0] | BOOL | 1 | 1 | 2 | 2 | UDINT | 32 | 4
Limit_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2 | BACnet Object | Bytes per Object in EEPROM (based on Templates)
Event_En[2] | BOOL | 1 | 1 | 2 | 2 | Device | 2
Notification_Class | UDINT | 1 | 1 | 4 | 4 | Analog Value | 74
Notify_Type | DINT | 1 | 1 | 4 | 4 | Analog Input | 70
Relinquish_Default | REAL | 1 | 1 | 4 | 4 | Binary Value | 62
[6 empty] | Binary Input | 50
Object | Analog Input |  |  |  |  | Calendar | 512
Attributes in EEPROM | Type |  |  | TOT | 70 | MSV | 58
Description | STRING | 1 | 1 | 32 | 32 | MSI | 54
COV_Increment | REAL | 1 | 1 | 4 | 4 | Schedule no exception | 558
Time_Delay | UDINT | 1 | 1 | 4 | 4 | Schedule w exception | 1146
High_Limit | REAL | 1 | 1 | 4 | 4
Low_Limit | REAL | 1 | 1 | 4 | 4
Deadband | REAL | 1 | 1 | 4 | 4
Limit_En[0] | BOOL | 1 | 1 | 2 | 2
Limit_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[2] | BOOL | 1 | 1 | 2 | 2
Notification_Class | UDINT | 1 | 1 | 4 | 4
Notify_Type | DINT | 1 | 1 | 4 | 4
Object | Binary Value
Attributes in EEPROM | Type |  |  | TOT | 62
Time_Delay | UDINT | 1 | 1 | 4 | 4
Minimum_off_Time | UDINT | 1 | 1 | 4 | 4
Mnimum_on_time | UDINT | 1 | 1 | 4 | 4
alarm value | DINT | 1 | 1 | 4 | 4
Notification_Class | UDINT | 1 | 1 | 4 | 4
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[2] | BOOL | 1 | 1 | 2 | 2
Notify_Type | DINT | 1 | 1 | 4 | 4
Description | STRING | 1 | 1 | 32 | 32
Object | Binary Input
Attributes in EEPROM | Type |  |  | TOT | 50
Time_Delay | UDINT | 1 | 1 | 4 | 4
Notification_Class | UDINT | 1 | 1 | 4 | 4
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[2] | BOOL | 1 | 1 | 2 | 2
Notify_Type | DINT | 1 | 1 | 4 | 4
Description | STRING | 1 | 1 | 32 | 32
Object | MSV
Attributes in EEPROM | Type |  |  | TOT | 58
Number_of_states | UDINT | 1 | 1 | 4 | 4
RelDef | UDINT | 1 | 1 | 4 | 4
TimeDel | UDINT | 1 | 1 | 4 | 4
NotClass | UDINT | 1 | 1 | 4 | 4
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[2] | BOOL | 1 | 1 | 2 | 2
Notify_Type | DINT | 1 | 1 | 4 | 4
Description | STRING | 1 | 1 | 32 | 32
Object | MSI
Attributes in EEPROM | Type |  |  | TOT | 54
Number_of_states | UDINT | 1 | 1 | 4 | 4
RelDef | UDINT | 1 | 0 | 4 | 0
TimeDel | UDINT | 1 | 1 | 4 | 4
NotClass | UDINT | 1 | 1 | 4 | 4
Event_En[0] | BOOL | 1 | 1 | 2 | 2
Event_En[1] | BOOL | 1 | 1 | 2 | 2
Event_En[2] | BOOL | 1 | 1 | 2 | 2
Notify_Type | DINT | 1 | 1 | 4 | 4
Description | STRING | 1 | 1 | 32 | 32
Object | Schedule no exception
Attributes in EEPROM | Type |  |  | TOT | 558
Description | STRING | 1 | 1 | 32 | 32
Effective_period | USINT | 8 | 1 | 2 | 16
weekly_schedule | USINT | 4 | 42 | 2 | 336
weekly_schedule.value | UDINT | 1 | 42 | 4 | 168
schedule_default | UDINT | 1 | 1 | 4 | 4
priority_for_writing | USINT | 1 | 1 | 2 | 2
Object | Schedule w exception
Attributes in EEPROM | Type |  |  | TOT | 1146
Description | STRING | 1 | 1 | 32 | 32
Effective_period | USINT | 8 | 1 | 2 | 16
weekly_schedule | USINT | 4 | 42 | 2 | 336
weekly_schedule.value | UDINT | 1 | 42 | 4 | 168
schedule_default | UDINT | 1 | 1 | 4 | 4
priority_for_writing | USINT | 1 | 1 | 2 | 2
date | USINT | 4 | 7 | 2 | 56
daterange | USINT | 8 | 7 | 2 | 112
weeknday | USINT | 3 | 7 | 2 | 42
calendar_reference | UDINT | 1 | 7 | 4 | 28
listoftimevalues.time | USINT | 16 | 7 | 2 | 224
listoftimevalues.value | UDINT | 4 | 7 | 4 | 112
event_priority | USINT | 1 | 7 | 2 | 14
Object | Calendar
Attributes in EEPROM | Type |  |  | TOT | 512
Description | STRING | 1 | 1 | 32 | 32
Date_list[0].date | USINT | 4 | 16 | 2 | 128
Date_list[0].daterange | USINT | 8 | 16 | 2 | 256
Date_list[0].weeknday | USINT | 3 | 16 | 2 | 96

## L_lim
0 | 0 | 0 | 0
1 | 1 | 1 | 1
2 | 2 | 2 | 2
3 | 3 | 3 | 3
4 | 4 | 4 | 4
5 | 5 |  | 5
6 | 6 |  | 6
7 | 7 |  | 7
8 | 8 |  | 8
9 | 9 |  | 9
10 | 10 |  | 10
11 | 11 |  | 11
12 | 12 |  | 12
13 | 13 |  | 13
14 | 14 |  | 14
15 | 15 |  | 15
16 | 16 |  | 16
17 | 17
18 | 18
19 | 19
20 | 20
21 | 21
22 | 22
23 | 23
24 | 24
25 | 25
26 | 26
27 | 27
28 | 28
29 | 29
30 | 30
31 | 31
32 | 32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256