## Slide 1
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
Heat Recovery Application

## Slide 2: Heat Recovery Application
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
Main Board
User Interface
Max distance 100m
Notes: <number>
Text slide, with title and body text [from Slide Master]
This slide exists as a Slide Master and all type specifications and graphic elements are fixed. Simply type into the prompt boxes.
The layout is set as a Title Box and Text Box – within the Text Box there are five levels of type:
  Level 1 – Body text set in Verdana Regular (18pt on 24pt linefeed) with ‘0.5 line’ space below each paragraph.
  Level 2 – Bulleted body text set in Verdana Regular (18pt on 24pt linefeed) with ‘0.5 line’ space below each paragraph.
  Level 3 – Bulleted body text (using a horizontal dash) set in Verdana Regular (16pt on 20pt linefeed) with ‘0.5 line’ space below each paragraph.
  Level 4 – Bulleted body text set in Verdana Regular (15pt on 18pt linefeed) with ‘0.5 line’ space below each paragraph.
  Level 5 – Bulleted body text (using a horizontal dash) set in Verdana Regular (14pt on 17pt linefeed) with ‘0.5 line’ space below each paragraph.
Within standard body text, subheads are set in Verdana Bold at the same size as the body text.
Advancing through the text levels
To advance to each text level from the previous one you can use the ‘Increase Indent’ and ‘Decrease Indent’ buttons on the ‘Formatting’ toolbar in PowerPoint®.
While the text position is fixed, the text box will grow as you enter further content in the slide – therefore, care should be taken to keep within the present text box margins.

## Slide 3
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Application
Outdoor temperature
Digital Output
Analog Input
LAN
Digital Input
Bypass
Valve1
FAN
Remote OFF
Valve2/
EH

## Slide 4
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Unit (2 pipes)
Hardware configuration
Analog Inputs (2)
AI1: Room/inlet air temperature (or SKW22 sensor)
AI2: Outdoor air temperature
Digital Inputs (2)
DI1: Remote ON/OFF
DI2: Exhaust Air Filter
Digital Outputs (6)
DO1: Min Fan Speed
DO2: Med Fan Speed
DO3: Max Fan Speed
DO4: Open 3 point floating Valve (Cooling/Heating)
DO6: Close 3 point floating Valve (Cooling/Heating)
DO5: Bypass external air (external relay)
Valve 1

## Slide 5
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Unit (2 pipes + Electric Heater)
Hardware configuration
Analog Inputs (2)
AI1: Room/inlet air temperature (or SKW22 sensor)
AI2: Outdoor air temperature
Digital Inputs (3)
DI1:Remote ON/OFF
DI2: Exhaust Air Filter
DI3: Thermal Protection Electric Heater
Digital Outputs (7)
DO1: Min Fan Speed
DO2: Med Fan Speed
DO3: Max Fan Speed
DO4: Open 3 point floating Valve (Cooling)
DO6: Close 3 point floating Valve (Cooling)
AO1: Electric Heater (external relay)
DO5: Bypass external air (external relay)
Valve 1

## Slide 6
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Unit (4 pipes)
Hardware configuration
Analog Inputs (2)
AI1: Room/inlet air temperature (or SKW22 sensor)
AI2: Outdoor air temperature
Digital Inputs (2)
DI1: Remote ON/OFF
DI2: Exhaust Air Filter
Digital Outputs (8)
DO1: Min Fan Speed
DO2: Med Fan Speed
DO3: Max Fan Speed
DO4: Open 3 point floating Valve (Cooling)
DO6: Close 3 point floating Valve (Cooling)
AO1: Open 3 point floating Valve (Heating)
AO2: Close 3 point floating Valve (Heating)
DO5: Bypass external air (external relay)
Valve 1
Valve 2

## Slide 7
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Application
MAIN FUNCTIONS
Fan Speed Management
It’s possible to select manually min/med/max fan speed or AUTO fan speed based on the set point and proportional band
Mode
It’s possible to select manually Heating or Cooling mode (to be agreed the need of AUTO MODE)
3 point floating Valve 1 (proportional)
In “2 pipes” systems Valve 1 is used for both heating and cooling mode according to the selection
In “4 pipes” systems Valve 1 is used for both heating and cooling mode according to the selection
3 point floating Valve 2 (proportional)
Valve 2 is used in “4 pipes” system only when heating mode is selected
Electric Heaters (On/Off)
In “2 pipes + electric heater” system the electric heater are used in Heating mode
Postventilation
After Electric Heater Switch off the fan continue working for around 1 minute

## Slide 8
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Heat Recovery Application
MAIN FUNCTIONS
FREECOOLING/FREEHEATING BYPASS
Cooling: If outdoor temperature is below SET – DELTA FC the BYPASS is ON (Valve OFF)
Heating: If outdoor temperature is higher than SET + DELTA FHC the BYPASS is ON (Valve/EH OFF)
Clock
The USER can select within 4 predefined profiles
Diagnostic
Temperature Probe failure
Electric Heater Thermal protection (2 pipes + electric heater only)
Exhaust Air Filter

## Slide 9
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>
© Invensys 00/00/00
Invensys proprietary & confidential
Slide <number>