FC 100

Electronic Controller For Fancoil Units

# contents

1    Contents	3

2	Introduction	5

2.1	Components	5

2.1.1	Basic Module	5

2.1.2	Keyboards	5

2.1.3	Serial Interface EWTK	6

2.1.4	Param Manager	6

3	Installation	7

3.1	Instrument installation	7

3.2	Warnings	7

3.3	Connections	7

3.4	Connection diagrams	8

3.4.1	Connection of the loads to FC 100	8

3.4.2	Keyboards’ dip switch	9

3.4.3	FC 100 network	10

3.5	Configuration’s dip switch	11

3.6	Inputs configuration	11

3.6.1	Analogue inputs	11

3.6.2	Digital inputs	11

3.7	Inputs configuration	12

3.7.1	Digital inputs	12

3.8	Serial communication	12

4	User Interface	13

4.1	Local keyboard configuration	13

4.1.1	Buttons	13

4.1.2	Leds	13

4.1.3	Set Point knob	13

4.1.4	Keyboard with display configuration	13

4.1.5	Buttons	13

4.1.6	Button combinations	14

4.1.7	LEDS	14

4.1.8	Display	15

5	System configuration	16

5.1	Fan coil typology	16

5.2	Fans configuration	16

5.3	Valves configuration	16

5.3.1	ON/OFF valve	16

5.3.2	Proportional valve	16

5.4	Electrical heaters configurations	17

5.5	Probes configurations	17

5.6	Offset of the local keyboard potentiometer (knob)	17

5.7	Keyboard block	17

6	Temperature control functions	19

6.1	Set point setting	19

6.1.1	Manual selection of the set point	19

6.1.2	Automatic set point	20

6.2	Temperature detection	20

6.3	Remote controls	20

6.4	Proportional regulation algorithm	20

6.5	Temperature control in COOL mode	21

6.5.1	Fan control	21

6.5.2	Valve control	22

6.6	Temperature control in  HEAT mode	22

6.6.1	Fan control	22

6.6.2	Valve control	22

6.6.3	Electrical heaters control	23

6.7	Temperature control in FAN mode	23

6.8	Temperature control in AUTO mode	23

6.8.1	Fan control	24

6.8.2	Valve control	24

7	Functions	25

7.1	Hot start function	25

7.2	Too cool function	25

7.3	Post-fan controller heat mode	25

7.4	Periodical fan controller	25

7.5	Periodical opening of the valve	26

7.6	Valve forcing	26

7.7	Set point selection for night operation (night set back)	26

7.8	Keyboard sleep	27

7.9	Antifreeze	27

7.10	Voltage failure	27

8	Parameters	28

8.1	Access to parameters through keyboard with display	28

8.2	Parameters description	28

8.3	Table of  parameters	29

9	Diagnostics	31

9.1	Ambient temperature probe alarm	31

9.2	Water temperature probe alarm	31

9.3	Other cases of alarm signals	31

9.4	Temperature control deactivations for analogue inputs failure	31

10	Technical features	32

10.1	Basic card	32

10.2	Keyboards: local, with display (wall, living)	32

11	Use of the device	33

11.1	Allowed usages	33

11.2	Not allowed usages	33

11.3	Reference regulations	33

12	Responsibility and residual risks	34

13	Glossary	35

# Introduction

x

FC 100 is a device allowing the control of fan coil units, both for the heating and the cooling of the ambient.

It can manage two or four-pipe systems  (water valves control):

Furthermore, it allows to control the fan (three speeds) and the possible integration of the heating with electrical heater through the use of relays.

FC 100 is suitable for several applications: hotel and commercial complexes, public spaces and offices.

It is possible to connect several FC 100 among them (up to 15): the operation, which is centrally set through the keyboard, is flexible (possible limited intervention from local keyboard), easy to use and efficient (lower management costs).

Main characteristics:

- 3 relay outputs (1 for the integration electrical heater, 2 for fan)

- 2 proportional outputs TRIAC 24 V AC 500mA for water valves

- 2 analogue inputs for NTC temperature probe (ambient air and water)

- 3 digital inputs for remote control (heating, cooling, on/off).

- Possibility of communication with a  PC

- Possibility of network connection of several FC 100 (up to 15)

- Power supply 12V AC

## Components

All the basic components and accessories as well as the related connections are illustrated herebelow.

### Basic Module

The basic module is presented as an electronic card to be connected as specified in the chapter Connection Diagrams

Basic module

<IMG INFO>

197,9

112,9

0

2

113,4

14,15

-1

### Keyboards

Three kinds of keyboard are available:

- Local keyboard without display for wall or fan coil installation  (120x65 mm)

Local keyboard

Local keyboard- TL-W

<IMG INFO>

141,45

87,4

0

2

141,75

14,15

-1

- Keyboard with display for wall installation (123x80x23 mm) TM-W

Keyboard with display

Keyboard with display

<IMG INFO>

141,45

95,35

0

2

141,75

14,15

-1

- Keyboard for electric plate installation (74x38x20 mm) TM-L

Keyboard on electric plate

Keyboard on

Electric plate

<IMG INFO>

141,7

99,5

0

2

141,75

14,15

-1

### Serial Interface EWTK

It is a device allowing the control interfacing with the Personal Computer

It must be connected as indicated in the figure:

<IMG INFO>

339,85

117,45

0

2

42,55

14,15

-1

The connections between the PC and the key and the key and device must take place in absence of voltage for each one of the devices and according to the safety rules in force. Furthermore, the electrostatic shocks, especially on the visible metallic parts of each apparatus must be avoided. In this regard, it has to be verified that the electrostatic currents can be grounded using suitable tricks.

<IMG INFO>

31,1

25,65

1

2

76,55

-12,8

-1

### Param Manager

Having a suitable Personal Computer provided with Windows 95 or up as operating system, as well as the software Param Manager, suitable hardware and suitable cabling, it is possible to have full control of all the FC 100 parameters through Personal Computer.

Programming the device, guided by a series of interfaces allowing a logical and controlled approach, turns out to be very easy, fast and pleasant.

# Installation

x

## Instrument installation

The card is usually installed on the convector itself.

The local keyboard can be installed on:

- The convector’s housing

- The wall

The keyboard with display comprises two versions, according to the foreseen installation:

- Wall mounting

- Mounting on electrical plate

## Warnings

The use of a transformer of a protected kind is necessary.

<IMG INFO>

33,9

27,7

1

2

73,7

-13,85

-1

In normal conditions, the parts subject to dangerous voltage should not be accessible.

The basic card should be suitably protected from water and dust, depending on the kind of application and must be accessible only by using a suitable tool.

Avoid the mounting of the control and of the keyboards in ambients having the following characteristics:

- RH (non condensing) higher than 90%

- Considerable shaking or shocks

- Exposure to strong and continuous water jets

- Exposure to aggressive and polluting atmosphere, such as to cause corrosion, oxidation (e.g. sulphuric or ammoniacal substances, saline smokes, smokes)

- High magnetic interference o radiofrequencies (e.g. in proximity of transmitting antennas)

- Exposure to direct sun rays or to atmospheric agents.

While connecting the controls among them or with accessories, electrical loads and other devices, be particular careful with the following:

- The incorrect connection of the power supply voltage can damage the control.

- The use of wire terminals not suitable for the used terminals. Unloose the terminal screw, insert the wire terminal and then retighten the screw. Finally, verify the tightening by slightly pulling the wire. Do not use automatic coils (or adjust them at a torque lower than 50 N*cm)

- Possible electromagnetic static: wire the low voltage loads separately from the high voltage loads. Separate as much as possible the control, the wires of the probes and of the digital inputs with respect to the inductive or power load.

- Never insert the power and the probes’ wires in the same wire guides, including those of the electric wires. The probes wires must be far enough from power devices (e.g. contactors). Reduce as much as possible the length of these wires.

- Do not apply loads higher than those declared in this specification to the inputs.

- While connecting the loads, pay particular attention to the connection diagrams.

## Connections

Before performing any electrical connection, follow carefully the advice and the diagrams described in the following.

<IMG INFO>

33,9

27,7

1

2

73,7

-13,85

-1

The controller must be installed and used according to the instructions provided.

Remember that the unit must be provided with all the electromechanical safety devices required to guarantee the safety of the operator.

## Connection diagrams

### Connection of the loads to FC 100

Connections

<IMG INFO>

282,65

350,8

0

2

70,9

14,15

-1

For all the low voltage inputs: cross section of the wires 2.5 mm².

ANALOGUE INPUTS

Analogue

inputs

Analogue inputs

- probes, having a NTC sensor, to determine the ambient temperature (ST1) and that of the finned pack of the convector (ST2), reading range: -20…70 °C

see section P2 in connections

4 way screw connectors, pitch 5;

1; Analogue input ST2;

2; Analogue input Gnd ST2;

3; Analogue input ST1;

4; Analogue input Gnd ST1;

DIGITAL INPUTS

3 inputs (ID 1, 2, 3) of the on/off type, voltage-free contact, configurable for the cooling, heating, Night Set Back, remote on / off functions.

Digital inputs

See section P1 in connections

4 way screw connectors, pitch 5

1; ID1 (VOLTAGE-FREE CONTACT);

2; ID2 (VOLTAGE-FREE CONTACT);

3; ID3 (VOLTAGE-FREE CONTACT);

4; COMMON (VOLTAGE-FREE CONTACT);

DIP SWITCH

4 dip switch (DIP 1, 2, 3, 4), to enable the functions related to fan, electrical heater, zone master role, power supply of the keyboard associated to the master card.

POWER SUPPLY

3 way screw connectors, pitch 5

Power supply

1; Ground contact;

2; Power supply 12 V AC;

3; Power supply 12 V AC;

See section P3 in connections

CONNECTION TO KEYBOARD WITH DISPLAY

3 way screw connectors, pitch 5 (2400 baud rate); for connection to another master card or to keyboard with display.

Connection to keyboard with display

1; corresponds to terminal 24 on the keyboard

2; corresponds to terminal 25 on the keyboard

3; corresponds to terminal 26 on the keyboard

See section P4 in connections

CONNECTION TO LOCAL KEYBOARD

Connection card- local keyboard

Connection to local keyboard

See connections

10 way connector

“flat” cable provided together with the local keyboard, cable length: 40 cm

SERIAL COMMUNICATION PORT TTL (COM 1)

See connections

Serial communication port TTL

1 way MS40 multi pin connector, No. 4.

For PC Connection, of the TTL (9600,n,8,1) type or optional RS 485.

DIGITAL OUTPUTS 230 V AC

Three relays:

Digital outputs

- one 10(7) A 230V AC relay for electrical heaters;

- two 3(1) A 230V AC relays for the fan.

6.3 mm vertical fast-on connectors

1. Fan maximum speed

2. Fan medium speed;

3. Fan minimum speed;

4. Neutral 230V~ ;

5. Electrical heaters;

6. Phase 230V~ ;

7. Neutral 230V~ ;

See connections

24 V AC outputs

two 24 V AC / 500 mA triac for the water valves

24 V AC outputs

6.3 mm vertical fast-on connectors (see connections):

8. On/Off or proportional valve;

9. On/Off or proportional valve;

10. Common

### Keyboards’ dip switch

DIP SWITCH ON KEYBOARD “WITH DISPLAY”:

For the use of two keyboards with display in a devices’ network:

- a keyboard must be associated to the master card (in the following: primary keyboard),

- the other must necessarily be defined as secondary.

This is obtained by suitably setting the provided dip switch

- Primary keyboard: dip switch 1.2

- Secondary keyboard: dip switch 2.4 or 3.4 or 1.3.

<IMG INFO>

283,15

114,15

0

2

70,9

14,15

-1

INPUTS AND OUTPUTS IN KEYBOARD “WITH DISPLAY”:

- For connection to the master card: 3 way screw connectors, pitch 5 (2400 baud rate); for connections, terminals 24, 25, 26 (see connections.).

- Analogue input: NTC sensor installed directly on the keyboard, to detect the ambient (ST1) and the finned pack of the connector (ST2) temperatures.

Reading range: -20…70 °C

OTHER CHARACTERISTICS FOR KEYBOARD WITH DISPLAY:

- Leds: 10 (2 on the display for SET and NSB / 3 for the fan / 1 for OFF / 4 for HEAT, FAN, COOL, AUTO modes)

- Buttons: 4 (UP, DOWN, FAN/OFF, MODE)

- Three digit display, digit height 10 mm (only for keyboard «with display»), display interval of the temperature:  –9.9…70 °C, definition: 0.1 °C, precision: 1% of the full scale.

OTHER CHARACTERISTICS FOR LOCAL KEYBOARD:

- Leds: 8 (3 for the fan / 1 for OFF / 4 for HEAT, FAN, COOL, AUTO modes)

- Buttons: 2 (FAN/OFF, MODE)

### FC 100 network

It is possible to connect up to 15 FC 100 in a network:

Just one device determines the operation of the entire network and it is therefore called master

Master

device

The remaining devices (that follow the master operation) are called slave or local

To form the network, it is necessary to assign the master role to only one card through the dip switch. It is advisable to connect a keyboard with display to the master card for the complete management of functions and parameters of the entire network.

Master

card

In the case of a network, it is possible to install a further keyboard with display. Therefore the connection of no more then two keyboards with display is allowed. However, the setting thereof takes place in the only enabled master card.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

The assignment of the master card role can be changed at any time, by suitably setting the dip switch of any of the cards connected to the network.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Maximum length of the wiring between the two furthest elements of the installation: 30 m with normal cable, 100 m with shielded cable

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Diagram

FC 100 network diagram

<IMG INFO>

339,6

405,45

0

2

42,55

14,15

-1

## Configuration’s dip switch

On the card, four DIP SWITCHES selecting supplementary functions as listed herebelow are installed.

Dip switch

Dip switch

<IMG INFO>

56,6

45,3

0

2

184,3

14,15

-1

DIP1 is operative on the COOL mode;

- ON: when the set point is satisfied, the fan operates at the minimum speed

- OFF: when the set point is satisfied, the fan is off.

DIP2

- ON: the integration electrical heater is enabled

- OFF: the integration electrical heater is disabled

DIP3

- ON: the control is enabled as zone «master» (see master device). The so enabled instrument manages the keyboard directly.

- OFF: the control is enabled as slave.

DIP 4

- ON: the power supply of the keyboard associated to the master card is enabled (see master device)

- OFF: the power supply of the keyboard is disabled

DIP 4 must be OFF if the control is configured as slave

<IMG INFO>

33,9

27,7

1

2

73,7

-13,85

-1

## Inputs configuration

The control configuration is determined by the values assigned to the parameters associated to the inputs and the outputs.

### Analogue inputs

The analogue inputs are formed by two NTC sensor probes to detect the temperatures:

- Of the ambient (ST1)

- Of the finned pack of the convector (ST2)

The ambient temperature probe is installed:

- At the keyboard associated to the master control (master device)  (sensor mounted on the keyboard)

- Through inputs (1,2,  P2 section, see connections), on the card. The probe wire can be remoted of max. 15 metres.

Follow the indications concerning the connections and the electromagnetic static.

<IMG INFO>

33,9

27,7

1

2

73,7

-13,85

-1

The probe connected to the master device has the priority on the control.

If the zone serial connection is not present or the probe connected to the master control is in the error mode, the probe provided on the local card (at the convector) is chosen.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

### Digital inputs

There are three digital inputs, all voltage-free contacts.

The inputs called ID1, ID2, ID3, can be configured according to the present diagram:

|  | Value of Pa 34 POLARITY (Digital inputs configuration) |  |  |  |
| --- | --- | --- | --- | --- |
| DIGITAL INPUTS | 0 | 1 | 2 | 3 |
| ID1 | Remote ON/OFF Card is turned off if Contact Closed | Remote ON/OFF Card is turned off if Contact Closed | Remote ON/OFF Card is turned off if Contact Closed | Remote ON/OFF Card is turned off if Contact Closed |
| ID2 | Night Set Back Active if contact closed | Night Set Back Active if contact closed | Night Set Back Active if contact closed | Remote HEAT HEAT if contact closed |
| ID3 | Remote HEAT /COOL HEAT if contact closed COOL if contact open | Remote HEAT /COOL HEAT if contact open COOL if contact closed | Not used | Remote COOL COOL if contact closed |

If Pa34 = 3 and at the same time: ID2=close and ID3=close, then the COOL mode will prevail.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- If the card is in the ON mode, the closing of the contact ID1 causes the deactivation thereof. In such case, the electrical heaters, if present, and the fan are deactivated.

Furthermore, the water valve (or valves) is closed, unless the antifreeze alarm is on.

If no button is pressed for about 30 seconds, the keyboard (or the keyboards) is deactivated. The successive opening causes the starting thereof.

- If the NIGHT SET BACK function is on, the set point is changed as described later on.

## Inputs configuration

### Digital inputs

DIGITAL INPUTS ON RELAYS

There three relays available, apt to control the fan and the possible integration electrical heater:

RL1 - Fan control, 230V AC 3 (1)A;

Relays

RL2 - Fan control, 230V AC 3(1)A;

RL3 - Electrical heater control, 230V AC 10(7)A.

The combination of the two relays generates the different speed of the internal fan.

The table herebelow clarifies the relationship between the relays status and the speed:

Fan

speed

| Relay RL1 | Relay RL2 | Fan speed |
| --- | --- | --- |
| OFF | OFF | OFF |
| ON | OFF | Minimum |
| ON | ON | Medium |
| OFF | ON | Maximum |

TRIAC OUTPUTS

Two TRIAC outputs are available, apt to control 24 V AC valves of the type:

Triac digital

outputs

- Electromechanical ON/OFF (both for 2 and 4 pipe convectors)

- Three wire proportional motor-driven  (only for 2 pipe convectors).

Connection diagram:

valve connection

<IMG INFO>

367,9

201,05

0

2

28,35

14,15

-1

## Serial communication

Two ports for serial communication are available:

- COM1: Serial communication port TTL (9600,n,8,1)

- COM2: Serial communication port for the keyboard with display or the zone master device (2400 baud rate)

The communication protocol, related with the keyboards and the cards in the different configurations is MICROTECH standard.

The device selected as master device has the direct control of the keyboard through the Dip Switch (DIP3).

Periodically, the master device sends a suitable order to all the local devices so that they reach the set point, the ambient temperature detected at the master device and the setting of the digital inputs.

# User Interface

x

The user has two types of keyboards for the device control:

- Local keyboard

- Keyboard with display (keyboard on electric plate)

## Local keyboard configuration

The local keyboard is connected to the basic module by a “flat” cable (see connection diagrams)

### Buttons

The button is active when the card is powered and the keyboard is in ON. Allows the change of the operation mode of the fan coil.

Mode button

The selection among the possible modes occurs, at any pressure of the button, through the sequence: HEAT > FAN > COOL > AUTO.

<IMG INFO>

45,25

28,05

1

2

62,35

-14

-1

The button performs the following functions:

FAN/OFF button

- With the card powered, allows the deactivation of the instrument by a single pressure of the button.

With the card powered in the HEAT, FAN or COOL mode, allows furthermore to change the speed of the fan at any pressure of the button. Press repeatedly; 4 seconds after the last time the button is pressed, the selection is confirmed by time out.

<IMG INFO>

45,25

28,45

1

2

62,35

-14,25

-1

- With the card powered and in the remote HEAT or COOL functionality (set by digital input, see digital inputs), the pressure of the button allows only to switch the instrument off.

- With the local card previously switched off through the same button, it is possible to restart it in the same mode of the previous operation.

If the card is switched off through the digital input ON/OFF (digital inputs) the button does not allow for the restarting of the resources.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

However, the pressure of the button allows to reset only the status of the keyboard preceding the OFF remote control:

- If the instrument was in the local OFF mode, the keyboard shows the OFF condition for 15 seconds.

- Otherwise, the keyboard restarts the display for 15 seconds. The further pressure on the FAN/OFF button allows the setting of the fan speed (except in remote HEAT or COOL status, or in AUTO mode).

However, the temperature control remains deactivated.

### Leds

OFF LED:

<IMG INFO>

45,3

20,15

1

2

62,35

-10,05

-1

When it is on, it means that the FC 100 is deactivated (OFF) .

HEAT LED:

<IMG INFO>

45,3

26,65

1

2

62,35

-13,3

-1

When it is on, it means that the operation mode is HEAT.

FAN LED:

<IMG INFO>

45,2

26,95

1

2

62,35

-13,5

-1

When it is on, it means that the operation mode is FAN.

COOL LED:

<IMG INFO>

45,3

26,65

1

2

62,35

-13,3

-1

When it is on, it means that the operation mode is COOL.

AUTO LED:

<IMG INFO>

46,1

24,25

1

2

62,35

-8,75

-1

When it is on, it means that the operation mode is AUTO.

When it blinks, it means that FC 100 is in the alarm mode for failure of analogue inputs.

FAN SPEED LEDS:

Fan speed leds (on in the HEAT, FAN, COOL, AUTO modes):

MAX

<IMG INFO>

45,3

64,65

1

2

62,35

-32,35

-1

When it is on, it means that the set speed for the fan is maximum.

- MID

When it is on, it means that the set speed for the fan is medium.

- MIN

When it is on, it means that the set speed for the fan is minimum.

### Set Point knob

The knob allows the control of the set point by potentiometric control.

### Keyboard with display configuration

The keyboard with display allows for the control of several devices if connected to the master device of a FC 100 network.

It is connected to the basic module by three wires.

Keyboard and card cannot be more than 30 m distant.

### Buttons

The button is on when the card is powered and the keyboard is in ON. It allows to change the operation modes of the fan coil.

Mode button

The selection among the possible modes occur, at any pressure of the button, through the sequence: HEAT > FAN > COOL > AUTO.

<IMG INFO>

45,25

28,05

1

2

62,35

-14

-1

If it is pushed together with the button UP, allows the access in the parameters programming.

The button performs the following functions:

FAN/OFF button

- With the card powered, allows the deactivation of the instrument by a single pressure of the button.

- With the card powered in the HEAT, FAN o COOL mode, allows furthermore to change the speed of the fan at any pressure of the button. Press repeatedly; 4 seconds after the last time the button is pressed, the selection is confirmed by time out.

With the card powered and in the remote HEAT or COOL functionality (set by digital input, see digital), the pressure of the button allows only to switch the instrument off.

<IMG INFO>

45,25

28,45

1

2

62,35

-14,25

-1

- With the local card previously switched off through the same button it is possible to reactivate it in the same mode of the previous operation.

With the card powered, when it pressed together with the UP button, allows the keyboard block.

If the card is switched off through the digital input ON/OFF (digital inputs) the button does not allow for the reactivation of the resources.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

However, the pressure of the button allows to reset only the status of the keyboard preceding the OFF remote control:

- If the instrument was in the local OFF mode, the keyboard shows the OFF condition for 15 seconds.

- Otherwise, the keyboard resets the display for 15 seconds. The further pressure on the FAN/OFF button allows the setting of the fan speed (except in remote HEAT or COOL status, or AUTO mode).

However, the control remains deactivated.

This button allows to change the set set point. By pressing it once, the set point value is displayed on the DS1 display. With the successive pressures, the set point is increased.

Up button

If pushed together with the MODE button, it allows the access to the parameters programming.

<IMG INFO>

45,2

29,4

1

2

62,35

-14,7

-1

If pushed together with the ON/OFF button, allows the keyboard block.

This button allows to change the set set point. By pressing it once, the set point is displayed on the DS1 display. With the successive pressures, the set point is decreased.

Down button

<IMG INFO>

45,25

29,95

1

2

62,35

-15

-1

### Button combinations

UP BUTTON + MODE BUTTON:

allows the access to the parameters programming.

UP BUTTON + FAN/OFF BUTTON:

allows the block (and successively the release) of the keyboard.

### LEDS

OFF LED:

<IMG INFO>

45,3

20,15

1

2

62,35

-10,05

-1

When it is on, it means that the control is:

- deactivated (OFF), or

- configuring the parameters.

HEAT LED:

<IMG INFO>

45,3

26,65

1

2

62,35

-13,3

-1

When it is on, it means that the operation mode is HEAT.

FAN LED:

<IMG INFO>

45,2

26,95

1

2

62,35

-13,5

-1

When it is on, it means that the operation mode is FAN.

LED COOL:

<IMG INFO>

45,3

26,65

1

2

62,35

-13,3

-1

When it is on, it means that the operation mode is COOL.

LED AUTO:

<IMG INFO>

45,25

24,2

1

2

62,35

-8,75

-1

When it is on, it means that the operation mode is AUTO.

FAN SPEED LEDS:

Fan speed leds (on in the HEAT, FAN, COOL, AUTO modes):

MAX

<IMG INFO>

45,3

64,65

1

2

62,35

-32,35

-1

When it is on, it means that the set speed for the fan is maximum.

- MID

- When it is on, it means that the set speed for the fan is medium.

- MIN

When it is on, it means that the set speed for the fan is minimum.

SET LED:

<IMG INFO>

56,6

31,8

1

2

51

-15,9

-1

It is contained in the display of the keyboard with display. When it is on, it means that the display of the set point on the DS1 is taking place. Changes to the set point are therefore possible by pressing the UP or DOWN buttons.

If it is on together with the NSB LED, it means that the keyboard block is active.

LED NSB :

<IMG INFO>

56,6

31,8

1

2

51

-15,9

-1

It is contained in the display of the keyboard with display. When it is on, it means that the NIGHT SET BACK function is on.

If it is on together with the SET LED, it means that the keyboard block is active.

### Display

It is the display associated to the keyboard in order to display:

- Temperature detected in ambient (when the SET LED is off),

- Set point value (when the SET LED is on),

- Alarm message.

The values are expressed in °C.

For temperatures higher than or equal to a –9.9 °C, the temperature is displayed in the standard mode (with decimal point).

For temperatures lower than  –9.9 °C, the display is a blinking “-9.9”.

If the blinking “err” message appears, it means that FC 100 is the alarm mode for failure of analogue inputs Functions related to the keyboard

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

# System configuration

x

In this chapter it is explained how to configure the parameters relative to the different loads considering the type of installation to be controlled.

## Fan coil typology

FC 100 is capable of controlling two types of fan coil installations:

- Two-pipe: there is a single water flow (one inlet and one outlet) and it depends on the installations operating upstream (cold water or hot water);

In this case, the installation is configured only to produce only cold or only heat.

Integrating heater

Hot or cold water

inlet

Valve

Finned pack

Outlet

Two pipe installation

- Four-pipe: two water flows one of which is cold (inlet and outlet) and another hot (inlet and outlet);

In this case, the installation is configured to produce cold and heat depending on the user’s choice and on the temperature control functions

Hot water inlet

Two valves

Finned pack

Outlet

Cold water inlet

Four pipe installation

It is necessary to correctly configure the parameter Pa 04:

- Pa 04 = 0: Two pipe fan coil

- Pa 04 = 1: Four pipe fan coil

## Fans configuration

If correctly connected, FC 100 is capable of controlling 3 speeds of the fan (OFF, minimum, medium, maximum);

Fan

No further configurations are necessary.

## Valves configuration

The FC 100 control allows the management of one or two valves depending on the type of valves used and of the type of installation (see valve connections).

Valve

The management takes place through the TRIAC outputs; they are apt to control 24 V AC valves of the type:

- ON/OFF electromechanical or electrothermic

- Three wire proportionalmotor-driven.

Depending on the type of valves used, it is necessary to configure correctly the parameter Pa 05, as illustrated herebelow:

- Pa 05 = 0 : ON/OFF valve;

- Pa 05 = 1 : Proportional valve;

### ON/OFF valve

In the two-pipe installation case, one valve is managed.

In the four-pipe installation case, the management of two valves is possible, one for hot water and the other for cold water. The opening and the closing of the valves occur according to the operation mode and the water temperature in the two circuits (see temperature control functions).

### Proportional valve

The proportional regulating valve can operate only in the two-pipe installation.

It is necessary to check the characteristics of the installed valve so as to set the time require for the total opening (closure) of the valve. (“total time” in the following) and the minimum time for the movement of the valve. Therefore it is necessary to set the relative parameters:

Pa 27 T_VALV_MIN: opening-closing time of the proportional valve (minutes)

Pa 28 T_VALV_SEC: opening-closing time of the proportional valve (seconds)

Pa 14 DEAD_VALVPRO: minimum time for the movement of the proportional valve

Manual mode (Heat Cool)

In the manual mode (HEAT, COOL), the valve is open or closed so that the water flow is proportional to the speed of the fan, as it was selected according to the parameters:

Pa 11 FAN_MIN_PROP value of the proportional band for the minimum starting of the fan.

Pa 12 FAN_MED_PROP value of the proportional band for the medium starting of the fan.

Pa 13 FAN_MAX_PROP value of the proportional band for the maximum starting of the fan.

AUTO MODE

In the AUTO mode, the different movements of the valve are actuated for a time that is calculated as a percentage of the total time.

Opening/Closing time of the valve, in seconds = RP * (Pa 27 *60 +  Pa 28)

Opening/closing time

RP is the percentage value calculated by the device when the conditions of use change.

In order to have the movement of the valve, RP must exceed a minimum threshold based on the parameter Pa 14. The valve changes its position if > Pa14 / (Pa 27 *60 +  Pa 28)

For example: with a medium speed of the fans, seconds of opening of the valve =  Pa 12 *(Pa 27 *60 +  Pa 28)

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

Pa 12 is the speed percentage value.

The following diagram can be observed:

<IMG INFO>

226,2

146,35

0

2

99,25

14,15

-1

The movement of the valve can be actuated with a delay, set by the parameter Pa 14 (DEAD_VALVPRO S dead zone for starting valves in proportional).

- For opening time of the valve, the sum of all the periods when the valve is open, minus the sum of all the periods when the valve is closed is intended.

When the valve reaches the status of maximum opening (or closing), before turning the motor of the valve off, 20 seconds are waited in order to eliminate possible positioning misalignments.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- When there is no voltage, at the reset the valve is forced to close, with a mouvement time, in minutes, equal to:  Pa 27 + 1.

## Electrical heaters configurations

It is possible to enable or disable the electrical heaters through a Dip Switch (DIP2).

Electrical

heaters

- If the dip switch DIP2 = ON, the electrical heaters are used in the HEAT mode as an integration of the finned pack (powered with hot water).

## Probes configurations

It is possible to set an offset for the air ambient probe, the water temperature probe and the keyboard with display probe;

Probes

The predetermined parametres are:

- Pa 36 OFFST1 : Ambient probe offset

- Pa 37 OFFST2 : Water probe offset

- Pa 39 OFFST5 : Ambient probe for keyboard with display offset

This function allows to cope with possible problems of air stratification or probe positioning.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

Through the parameter Pa 17 it is possible to find out if the ambient temperature is detected all the time or only during fan controller:

- Pa 17 = 0 : all the time

- Pa 17 = 1: only with fan in operation

## Offset of the local keyboard potentiometer (knob)

It is possible to set an offset for the local keyboard potentiometer (knob) by acting on the parameter Pa 38

## Keyboard block

Keyboard with dispaly

BLOCK OF THE KEYBOARD WITH DISPLAY:

By pressing at the same time the buttons UP and FAN/OFF for 10 seconds, the keyboard is blocked.

The SET and NSB leds remain both on.

To release the keyboard, repeat the same operation.

BLOCK OF THE LOCAL KEYBOARD:

Local keyboard

It is possible to block the local keyboards by acting on the keyboard associated to the master card. In this case, the local keyboards will behave only as display of the installation status.

To carry out such a block, set the parameter Pa 42 = 1.

To release the local keyboards, set Pa 42 = 0.

# Temperature control functions

x

Once it is configured, the FC100 installation is ready to control the loads according to the detected temperatures and to the temperature control that can be defined by suitable parameters.

Four operation modes are possible

COOL

Operation mode

- FAN

- HEAT

- AUTO

Cooling: is the “summer” operation mode; the installation is configured to produce cold.

Cool

Fan: the installation is configured to manage only the fans and the speed thereof.

Fan mode

Heating: is the “winter” operation mode; the installation is configured to produce heat.

Heat

Auto: the installation is configured to pass from the cool to the heat mode and viceversa automatically depending on the temperature values and on the values of some parameters.

Auto

In the following table the loads controlled in the various modes are detailed:

Operation modes:

table

| Mode | Setting | Management of: |
| --- | --- | --- |
| HEAT | MANUAL | Valve: water (for two-pipe fan coil), hot water (for four-pipe fan coil) Fan (3 manually set speeds) Electrical heater (enabled through dip switch dip) |
| FAN | MANUAL | Fan (3 manually set speeds) |
| COOL | MANUAL | Valve: water (2 pipe), cold water (4 pipe) Fan (3 manually set speeds) |
| AUTO | AUTOMATIC | Dynamic management, in the modes: HEAT COOL “STAND BY” mode (for neutral zone), according to the comparison between the ambient temperature and the set point |

The operation mode can be manually set by means of:

- local keyboard

- remote keyboard (keyboard with display)

- digital input

The following table can be observed:

Operation mode selection:

table

| Selection from: | Procedure | Notes |
| --- | --- | --- |
| Local keyboard | MODE button, through the sequence HEAT, FAN, COOL |  |
| Remote keyboard (keyboard with display) | MODE button, through the sequence HEAT, FAN, COOL |  |
| Remote digital input | HEAT function: - ID3 = close and Pa 34 = 0 - ID3 = open and Pa 34 = 1 - ID2 = close, ID3 = open, Pa 34 = 3 | The card can be locally or centrally disabled |
| Remote digital input | COOL function: - ID3 =open and Pa 34 = 0 - ID3 =close and Pa 34 = 1 - ID3 =close, ID2=close or open, Pa 34= 3 |  |

## Set point setting

The management of the loads will dynamically depend on the set temperature control functions, from the temperature values detected by the probes and by the set set point.

The set point can be changed:

Set point

- with the suitable SET buttons from the keyboard with display (UP, DOWN buttons).

- through a knob from local keyboard.

- through parameter (Pa 29) in the AUTO mode.

### Manual selection of the set point

The manual setting can be carried out:

- centrally (through keyboard associated to a master card) or

- locally (through a knob on the local keyboard).

If the set point is changed through the keyboard associated to the master card, all the local controls connected thereto take the same value for temperature control.

This is possible providing the keyboard associated to the master card is present and there are no failures in the card or in the serial communication.

Otherwise each local card takes the local set point and temperature.

If the setting takes place through the local keyboard (knob), the control associated thereto takes the specifically selected value.

The set point can assume values comprise in a range determined by the parameters Pa 03 – Pa 02.

- The locally set set point is kept also when the related card is deactivated.

The set point value on a local level is always given by the last local or remote setting peformed.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- In case of restart after a voltage failure, the local control assumes the set point set on the keyboard associated to the master card.

- If the local keyboard is absent or in failure, the temperature control is based on the setting related to the keyboard associated to the master card.

- If the communication between the local and the master card is impossible, the local card has no temperature control capability and therefore switches to the OFF mode. The error mode is signalled only on the local keyboard.

### Automatic set point

An automatic temperature control set point can be enabled in the AUTO operation mode.

The parameter Pa 30 allows to enable or not the temperature control through the parameter Pa 29:

- If Pa 30 = 1 the temperature control is based on the set point set through the parameter Pa 29 AUTO_SET: automatic temperature control set.

- Otherwise, the set point can be controlled from the keyboard (the same criteria related to the manual setting are applicable: priority to the “remote” set point, otherwise “local” set point).

See the chapter Temperature control in AUTO mode

If the automatic set point is enabled and Pa 30 =1, the relative value cannot be changed through the keyboard (neither local, nor with display).

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Temperature detection

The “ambient” temperature probe is available at:

Ambient probe

- each card (local probe), at each convector

- keyboard with display, associated to the master card (sensor mounted on the keyboard, i.e. remote probe)

In case of a FC 100 network, more temperature probes are available.

To detect the temperature, the remote probe has priority (since this is normally associated to the master card), provide this is present and the communication is correct. In this case, the temperature control is one for the entire network.

If one of the following conditions occurs:

- the remote probe (therefore the keyboard with display) is not connected

- the remote probe is in error mode

- the zone serial connection is not present

then each card refers to the local temperature (local temperature control), since each card belonging to the network detects the temperature through the probe associated thereto.

If also the card (or the probe associated thereto) is in failure, there is no temperature control. An error mode is signalled (at the keyboard related to the card) (see ambient temperature probe alarm).

The error mode of the local card is not displayed on the keyboard associated to the master card.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

If the water probe is in failure, with a two-pipe convector, the error mode is signalled. Therefore no temperature control is activated (see water probe temperature alarm).

Water probe

In case of four-pipe convector, the temperature control is not compromised by the alarm mode.

## Remote controls

The functions:

- COOL

- HEAT

- ON/OFF

- NIGHT SET BACK

can be remotely managed through the digital inputs.

With these inputs it is possible to centralise the management of the FC 100 network, permitting to each FC 100 control the temperature control based on the temperature measured at the control itself.

In case a zone master device is present, only the inputs related to the master card can be used.

Therefore, the remote controls are sent to the master device, while all the slave controls receive the same signal thanks to the serial connection between slave and master.

If one of the remote inputs is active, the local keyboards and those associated to the master card are blocked.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

In this case, any change in the operation mode or in the fan speed is prevented. The only allowed change is the set point setting.

## Proportional regulation algorithm

The valves, the fans and the electrical heaters are managed according to the signal coming from a “proportional regulation algorithm”.

The concerned parameters are:

Pa07 HYST_COOL_ MODE hysteresis in COOL mode to determine the operation mode

Parameters

Pa08 HYST_ HEAT_MODE hysteresis in HEAT mode to determine the operation mode

Pa10 PROP_BAND: proportional band of the regulation algorithm

Pa09 ENA_HYST_MODE: enables the mode hysteresis; allows to enable Pa07 or Pa08, thus choosing between the following temperature controls:

- Proportional output at the set point (Pa 09 =  0),

- Neutral zone temperature control (set point + hysteresis, Pa 09 = 1).

The following explaining diagrams can be observed:

Legend:  ST1 = ambient temperature, SET = keyboard set set point

Proportional temperature control in the event Pa 09 = 0

<IMG INFO>

253,9

148,05

0

2

85,05

14,15

-1

Proportional temperature control in the event Pa 09 = 1 (set point + hysteresis)

<IMG INFO>

254,05

144,3

0

2

85,05

14,15

-1

## Temperature control in COOL mode

The operation of the COOL mode is a function of ambient temperature and set point.

The description on how the respective loads are controlled follows;

### Fan control

It is off if:

- The thermostat is satisfied and the dip switch DIP1 is OFF.

- There are failures in the analogue inputs (see analogue inputs failures).

- On two-pipe installation, if the water temperature is not cold enough (TOO COOL function not satisfied)

To avoid stratification problems, only periodical fan controller is performed.

It is active at the minimum speed if:

- The thermostat is satisfied, the dip switch DIP1 is ON

Otherwise it is on at the speed set through the keyboard.

The following diagram is to be observed:

ST1 = ambient temperature;

SET = keyboard set set point.

Pa 16 DEAD_FANMAN hysteresis temperature of the fans in manual operation

<IMG INFO>

226,65

149,1

0

2

99,25

14,15

-1

### Valve control

ON/OFF VALVE CASE (2 or 4 pipes)

The valve is closed if:

On/off

valve case

- The thermostat is satisfied

- There is a probe error (air)

- There is a probe error (water ; for two-pipe convector only)

- OFF control performed remotely or from keyboard

For two-pipe installation, the valve is also closed for:

- Season contrast (water temperature > HOT START temperature)

Otherwise it is open

PROPORTIONAL VALVE CASE (2 pipes)

The valve is closed if:

Proportional valve case

- There is a probe error (air)

- There is a probe error (water; for two-pipe convector only)

- OFF control performed remotely or from keyboard

For two-pipe installation, the valve is also closed for:

- Season contrast (water temperature > HOT START temperature)

Otherwise it is open, according to a temperature control and temperature set point (modulation with respect to the proportional regulation algorithm, 0…100%)

## Temperature control in  HEAT mode

The operation of the HEAT mode is a function of ambient temperature and set point.

The description on how the respective loads are controlled follows;

### Fan control

It is off if:

- The thermostat is satisfied and the dip switch DIP1 is OFF.

- There are failures in the analogue inputs (see analogue inputs failures).

- On two-pipe installation, if the water temperature is not hot enough (HOT START function not satisfied)

To avoid stratification problems, only periodical fan controller is performed.

Otherwise it is on at the speed set through the keyboard.

The following diagram is to be observed:

ST1 = ambient temperature;

SET = keyboard set set point.

Pa 16 DEAD_FANMAN hysteresis manual temperature of the fans

<IMG INFO>

226,65

149,1

0

2

99,25

14,15

-1

### Valve control

ON/OFF VALVE CASE (2 or 4 pipes)

The valve is closed if:

- The thermostat is satisfied

- There is a probe error (air)

- There is a probe error (water; for two-pipe convector only)

- OFF control performed remotely or from keyboard

For two-pipe installation, the valve is also closed for:

- Season contrast (water temperature < TOO COOL temperature)

Otherwise it is open

PROPORTIONAL VALVE CASE (2 pipes)

The valve is closed if:

Proportional valve case

- There is a probe error (air)

- There is a probe error (water; for two-pipe convector only)

- OFF control performed remotely or from keyboard

For two-pipe installation, the valve is also closed for:

- Season contrast (water temperature < TOO COOL temperature)

Otherwise it is open, according to a temperature control and temperature set (modulation with respect to the proportional regulation algorithm, 0…100%)

### Electrical heaters control

The following parameters are available:

- Pa 21 HEAT_INTEG: proportional regulation algorithm value for starting heaters in INTEGRATION

- Pa 22 DEAD_RESIST: Defines the value of the hysteresis for starting the heaters

The following diagram can be observed

<IMG INFO>

226,65

145,05

0

2

99,25

14,15

-1

Delayed start

The starting of the electrical heaters can be delayed through the parameter:

- Pa 33 PRE_HEA: delay in starting the electrical heaters in order to allow the water flow and therefore to bring the installation at a steady state.

Post fan controller

After the electrical heaters are switched off, the fans continue operating for time that can be set from the parameter Pa 24 (POST_FAN_HEAT: post-fan controller with heaters only).

If the electrical heaters are started, the fan is always started as well.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- In order to avoid damages to the electrical heater and to the convector, the electrical heaters are on only if the fan works.

## Temperature control in FAN mode

In this operation mode, the only exploited resource is the internal fan, whose speed can be manually set using the ON/OFF button on the keyboard:

- MINIMUM

- MEDIUM

- MAXIMUM

## Temperature control in AUTO mode

In this mode the device sets automatically the operation mode of the installation (HEAT or COOL) according to the ambient temperature and to the set set point. According to the ambient situation;

The control can also set the equipment in the “STAND BY” mode

No temperature control is possible in case of failure of analogue inputs.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

The following diagram is to be observed:

ST1 = ambient temperature;

SET = set point set by parameter if Pa 30 =1, by keyboard if Pa 30 = 0;

Pa 07 HYST_COOL_ MODE: hysteresis in COOL mode to determine the operation mode

Pa 08 HYST_ HEAT_MODE: hysteresis in HEAT mode to determine the operation mode.

<IMG INFO>

254

112,5

0

2

85,05

14,15

-1

In the AUTO mode, by pressing the FAN/OFF button: the instrument is switched off, all the resources are disabled and the OFF Led switches on.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

### Fan control

The fan is off if:

- The thermostat is satisfied and the dip switch  DIP1 is OFF;

Only for two-pipe installation:

- The  HOT START or TOO COOL functions are on;

However, the fan is started in case of periodical fan controller.

Otherwise the fan is on, with a speed automatically detected by the proportional regulation algorithm (see diagram herebelow).

According to the operation in the AUTO_HEAT o AUTO_COOL (see AUTO) modes, the possible admitted conditions for the fan correspond to those described for the HEAT mode and the COOL mode.

The following diagram is to be observed:

RP = Proportional regulation algorithm

Pa 11 FAN_MIN_PROP: value of the proportional band for the minimum starting of the fan

Pa 12 FAN_MED_PROP: value of the proportional band for the medium starting of the fan

Pa 13 FAN_MAX_PROP: value of the proportional band for the maximum starting of the fan

Pa 15 DEAD_FANAUTO: hysteresis proportional band to start the fans

<IMG INFO>

254,7

136,75

0

2

85,05

14,15

-1

In the AUTO mode, the fan speed cannot be changed from the keyboard.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

### Valve control

ON/OFF VALVE CASE (2-4 pipes):

According to the operation in the AUTO_HEAT o AUTO_COOL (see AUTO) modes, the possible admitted conditions for the valve correspond to those described for the HEAT mode and the COOL mode.

PROPORTIONAL VALVE CASE (2 pipe)

According to the operation in the AUTO_HEAT o AUTO_COOL (see AUTO) modes, the possible admitted conditions for the fan correspond to those described for the HEAT mode and the COOL mode.

# Functions

x

## Hot start function

This function is provided only for the HEAT and AUTO (HEAT) modes.

Allows the operation of the fan only if the convector is hot enough, avoiding therefore unpleasant cold water flows.

Hot start

The function is active only if the probe ST2 (water temperature) is present (see analogue inputs).

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Concerned parameters:

Pa 18 HOT_START hot enabling temperature

Pa 20 DEAD_CONS temperature hysteresis on HOT START and TO COOL

<IMG INFO>

254,05

155,15

0

2

85,05

14,15

-1

## Too cool function

This function is provided for the COOL and AUTO (COOL) modes.

Allows the operation of the fan only if the convector is cold enough, avoiding useless hot air flows.

Too cool

The function is active only with two-pipe fan coils and if the probe ST2 (water temperature) is present (see analogue inputs).

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Concerned parameters:

Pa 19 TO_COOL cooling enabling temperature

Pa 20 DEAD_CONS temperature hysteresis on HOT START and TO COOL

<IMG INFO>

254,15

155,9

0

2

85,05

14,15

-1

## Post-fan controller heat mode

In the HEAT mode, if there is an electrical heater, the fan continues operating even if the control is switched off.

Post fan-controller

The operation continues for a time equal to Pa 24, in order to avoid dangerous overheating caused by the electrical heaters.

This safety timing takes place also if there are alarms to disable the fan or when the switching off of the control is operated.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Periodical fan controller

The fan performs operating cycles having on and off times established through parameters.

This function eases the ambient air circulation, preventing the stratification that could compromise the optimal operation thereof

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

If in the HEAT or COOL mode the fan remains off for a predetermined time, a periodical fan controller at a minimum speed can take place.

The time during which the fan remains off is determined through the parameter

- Pa 26 FAN_PERIOD_OFF: break time of periodical fan controller.

The timing of the minimum speed fan controller is determined through the parameter

- Pa 25 FAN_PERIOD_ON: time of periodical fan controller.

The periodical fan controller is always enabled in the COOL mode.

The periodical fan controller can enabled or not in the HEAT mode through the parameter Pa 23:

- Pa 23 = 1 : enables periodical fan controller in HEAT

- Pa 23 = 0: disables periodical fan controller in HEAT.

Pa 25 FAN_PERIOD_ON time of periodical fan controller;

Pa 26 FAN_PERIOD_OFF break time of periodical fan controller;

The following diagram is to be observed:

<IMG INFO>

255

105,8

0

2

85,05

14,15

-1

## Periodical opening of the valve

For two-pipe fan coils only.

The selection of the operating mode, based on ambient temperature and set point, can contrast with the water temperature in the pack.

Season

contrast

Therefore, it could be necessary to periodically close/open the water valve.

The valve is closed in the following cases:

- COOL mode: the water temperature is higher than the temperature set for the HOT START function (the operation of the convector is deactivated since the water is too hot).

- HEAT mode: the water temperature is lower than the temperature set for the TOO COOL function (the operation of the convector is deactivated since the water is too cold).

It is possible to set the time that has to pass before the successive reopening of the valve, through the parameter Pa 31 (periodical opening of the valve in two-pipe fan coil).

The opening cycle of the valve is repeated in case of:

- Changing of the operation mode

- Switching off and switching on again of the control

## Valve forcing

This function allows to avoid the possible block of the valves after a long time they have remained in the same position.

The forcing has priority with respect to the periodical opening. Therefore, even if the predetermined time for the periodical opening of the valve is not reached, the above listed parameters prevail, causing the forced opening.

The concerned parameter is Pa 40:

- If Pa 40 = 0, the function is disabled.

- Otherwise, Pa 40 represents the time in hours after which the valve is forced

At any starting of the valves, the device starts a meter in hours. If this meter reaches the value of Pa 40, the valves are forcibly switched.

If the valves are of the ON/OFF type (Pa 05 = 0 valve ON/OFF) they are forcibly switched for a time equal to Pa 41. Therefore for a time Pa 41 /2 the valve opens; successively, for a time equal to Pa 41 /2, the valve closes.

If the valves are of a proportional type (Pa 05 = 1 proportional valve) a complete opening/closing cycle is performed.

## Set point selection for night operation (night set back)

This function allows to change the set point, for instance for night time.

This reduces the energy need (both for the cooling and the heating of the ambient).

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

The set point value is increased in case of a cooling request and viceversa, through the parameter Pa 35, as described herebelow:

Night set back

- cooling:                            	Set  NSB COOL  =  Set COOL  +  Pa 35

- heating:                             	Set NSB HEAT  =  Set HEAT  -  Pa 35

- cooling, AUTO mode:  		Set NSB AUTO COOL  =  SET AUTO  +  Pa 35

- heating, AUTO mode:    		Set NSB AUTO HEAT  =  SET AUTO  -  Pa 35

If this function is active, the NBS led is on.

## Keyboard sleep

It is possible to programme the switching off of the remote keyboard after a certain time following the pressing of any button.

The function is performed through the parameter Pa 08 (Sleep):

- Pa 08 = 1, the function Keyboard Sleep is enabled,

- Pa 08 = 0, the keyboard remains always on.

## Antifreeze

This function prevents the forming of ice in the water pipes and the consequent breaking thereof in the period when the equipment is not in operation.

The antifreeze function is possible even if the control is in the OFF position.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

The condition is not displayed on the interface.

If the temperature detected by the ambient probe ST1 (analogue inputs) is lower than the value predetermined through the parameter Pa 32, the following actions are taken:

- Opening of the water valve (two-pipe convectors), or of both the valves (four-pipe convectors). The opening is permanent throughout the alarm time, even if the conditions for closing (based on the parameters Pa 18, Pa 19 for HOT START, TOO COOL) occur; therefore there is no periodical opening/closing.

- Starting of the fan at maximum speed, if electrical heaters are present (otherwise the fan remains off).

- Starting of the electrical heaters, if present.

These operations take place with a fixed 2°C hysteresis.

<IMG INFO>

254,4

152,85

0

2

85,05

14,15

-1

## Voltage failure

At the reset after a voltage failure, the control will restart with the operation mode it was in when the voltage failure took place.

In the AUTO mode, the control operates according to the mode it was in when the power is restored.

The possible running timing are reset.

# Parameters

x

A series of parameters to configure FC 100 is available, for different equipment and system architectures.

The parameters can only be set through:

- the  keyboard with display, associated to the master card or

- personal computer (with the PARAM MANAGER tool).

The access to the setting is protected by a password.

Remember that it is impossible to set the parameters on a slave card, unless the roles “master” / “slave” are modified by a dip switch.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Access to parameters through keyboard with display

- Set the keyboard in the OFF mode.

- Press the UP and MODE buttons together for 5 seconds, until the value “00” appears on the display.

- If a password was previously set, type the value with the UP, DOWN buttons. Otherwise, pass to the successive step 4.

- Confirm the procedure pressing the FAN/OFF button. The access to the setup of the parameters is granted.

- On the display, the parameter index appears, starting from the first parameter (0). The OFF led is on.

- Browse the list of the parameters with the UP, DOWN buttons.

- After the desired parameter is found, press the MODE button to display the present value.

- The value can be changed using the UP, DOWN buttons.

- Once the desired value is set, confirm it by pushing the FAN/OFF button. The display of the parameters list, as in step 5, starts again.

- The scrolling of the parameters (steps 6-9) can be continued or exit the programming.

- To exit the parameters menu, press the UP and MODE buttons together again for 5 seconds. The exit from the programming takes anyhow place by time out after 10 seconds from the last action.

The keyboard can be set in the OFF mode even when the digital inputs are active (see remote controls).

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Parameters description

PASSWORD: password to change the parameters.

Pa 00

Allow to select the password required to access to the parameters list. If this parameter is not changed, the password is set to the value “00” and the access to the setup of the parameters takes place by pushing the FAN/OFF button.

ADDR_BRD protocol address: Shows the serial address of the instrument.

Pa 01

SET_MAX maximum set point: Allows to define the maximum allowed value for the set point.

Pa 02

SET_MIN minimum set point. Allows to define the minimum allowed value for the set point.

Pa 03

TYPE_FC: type of fan coil

Pa 04

- 0 = two-pipe fan coil

- 1= four-pipe fan coil

TYPE_VALV : Selection of the type of valve to control the water.

Pa 05

- 0 = ON OFF valve

- 1= proportional valve.

T_SLEEP : interval to switch the keyboard off.

Pa 06

defines the time after which the keyboard automatically deactivates following the pressure of a button;

- 0 = always active keyboard.

HYST_COOL_ MODE: hysteresis in COOL mode to determine the operation mode.

Pa 07

Allows the setting of a temperature differential for the summer set point, in automatic operation.

HYST_ HEAT_MODE: hysteresis in HEAT mode to determine the operation mode.

Pa 08

Allows the setting of a temperature differential for the winter set point, in automatic operation.

ENA_HYST_MODE: enables the mode hysteresis.

Pa 09

Allows the use or not of the hysteresis (Pa 07, Pa 08) for the temperature control in the COOL, HEAT modes.

PROP_BAND: proportional band of the regulation algorithm.

Pa 10

Defines the proportional bandwidth.

FAN_MIN_PROP: value of the proportional band for the minimum starting of the fan.

Pa 11

Defines the value for the proportional regulation algorithm wherein the fan starts at a minimum speed.

FAN_MED_PROP: value of the proportional band for the medium starting of the fan.

Pa 12

Defines the value proportional regulation algorithm wherein the fan starts at a medium speed.

FAN_MAX_PROP: value of the proportional band for the maximum starting of the fan.

Pa 13

Defines the value proportional regulation algorithm wherein the fan starts at a maximum speed.

DEAD_VALVPRO: dead zone for starting valves in proportional.

Pa 14

Defines the minimum time for the movement of the proportional water valve.

DEAD_FANAUTO: hysteresis proportional band to start the fans.

Pa 15

Defines the value of the hysteresis for the control of the fan in automatic operation.

DEAD_FANMAN: hysteresis temperature of the fans in manual operation.

Pa 16

Defines the value of the hysteresis for the temperature control of the fan in manual operation.

ENA_CAMPCOOL: enables sampling in cooling only if fans are on.

Pa 17

Enables the sampling only when the fan is in operation.

1 = sampling only with fan in operation.

HOT_START enabling temperature (for HOT START).

Pa 18

Is the value to which the water temperature is compared in order to enable the selected operation mode:

in heating (“HEAT” or “AUTO HEAT”): if water temperature < HOT START temperature, then only periodical fan controller is performed (the water is not hot enough).

TO_COOL enabling temperature (for TOO COOL).

Pa 19

Is the value to which the water temperature is compared in order to enable the selected operation mode:

in cooling (“COOL” or “AUTO COOL”): if water temperature > TOO COOL temperature, then only periodical fan controller is performed (the water is not cold enough).

DEAD_CONS: temperature hysteresis on HOT START and TO COOL.

Pa 20

Defines the hysteresis value of the regulation algorithm for the HOT START and TOO COOL functions.

HEAT_INTEG: value of the proportional band starting heaters in INTEGRATION.

Pa 21

Defines the value of the temperature control proportional band for which heaters are started in order to integrate the heat contribution.

DEAD_HEAT: hysteresis proportional band for heaters deactivation.

Pa 22

Defines the value of the hysteresis for deactivating the heaters

FAN_PER_HEAT: Enables periodical fan controller in HEAT.

Pa 23

Allows or not the periodical fan controller in heating

- 0 = no fan controller,

- 1= yes fan controller.

POST_FAN_HEAT: post-fan controller with heaters only.

Pa 24

Defines the time of the post-fan controller after the heaters are switched off.

FAN_PERIOD_ON: time of periodical fan controller.

Pa 25

Defines the operation time of the fan in relation with the periodical fan controller.

FAN_PERIOD_OFF: break time of periodical fan controller.

Pa 26

Defines the time where the fan is off in relation with the periodical fan controller.

T_VALV_MIN: opening-closing time of proportional valve.

Pa 27

Defines the time in minutes required for a complete opening (or closing) of the proportional valve.

T_VALV_SEC: opening-closing time of proportional valve.

Pa 28

Defines the time in seconds required for a complete opening (or closing) of the proportional valve.

AUTO_SET: automatic temperature control set.

Pa 29

Is the temperature control set point in automatic operation (AUTO)

ENA_AUTO_SET: enables automatic temperature control set.

Pa 30

Allows to set the automatic set point during automatic operation (AUTO).

If the automatic set point is enabled, the setting of the set point through the keyboard is disabled.

T_TASTH2O: periodically opens the valve according to the water temperature.

Pa 31

For two-pipe convector. Defines the time required between two successive openings of the water valve when the water temperature is not compatible with the selected operation mode. In such a case, the control sets repeated openings of the valve until compatible conditions are reached.

T_ANTIFREEZE: ambient antifreeze temperature.

Pa 32

Defines the operation temperature starting the antifreeze alarm.

PRE_HEA: delay in heater starting

Pa 33

POLARITY digital inputs polarity.

Pa 34

For the configuration of the digital inputs.

NIGHTSET_B: selection of the night set point for the Night Set Back function

Pa 35

OFFST1: Ambient probe Offset

Pa 36

OFFST2: Water probe Offset

Pa 37

OFFST3: Potentiometer Offset

Pa 38

OFFST5: Ambient probe for keyboard with display Offset

Pa 39

TIM_CLO_VAL: time after which the switching of the valve is forced

Pa 40

CLOS_TIME: time of periodical closing of the valve

Pa 41

BLOKEY: Block of the local keyboard

Pa 42

## Table of  parameters

Table of parameters

| Par. | Description | Default Value | Limits | Unit |
| --- | --- | --- | --- | --- |
| Pa 00 | PASSWORD: password to change the parameters | 0 | 0  99 | No. |
| Pa 01 | ADDR_BRD: serial protocol address | 0 | 0  99 | No. |
| Pa 02 | SET_MAX: maximum set point | 27 | Pa 03  40 | C |
| Pa 03 | SET_MIN: minimum set point | 11 | 5  Pa 02 | C |
| Pa 04 | TYPE_FC: ( 0 = two pipe fan coil 1=four pipe fan coil) | 0 | 0  1 | Flag |
| Pa 05 | TYPE_VALV: (0 = ON/OFF valve, 1 = proportional valve) | 0 | 0  1 | Flag |
| Pa 06 | T_SLEEP: sleep function: interval to deactivate the keyboard 0=always on | 0 | 0  99 | Min |
| Pa 07 | HYST_COOL_MODE: hysteresis in COOL mode to determine the operation mode | 20 | 0  200 | C/10 |
| Pa 08 | HYST_HEAT_MODE: hysteresis in HEAT mode to determine the operation mode | 20 | 0  200 | C/10 |
| Pa 09 | ENA_HYST_MODE: enables the mode hysteresis (in the proportional regulation algorithm) | 0 | 0  1 | Flag |
| Pa 10 | PROP_BAND: proportional band of the regulation algorithm | 80 | 0  99 | °C/10 |
| Pa 11 | FAN_MIN_PROP: value of the proportional band for the minimum starting of the fan | 10 | 0  100 | % |
| Pa 12 | FAN_MED_PROP: value of the proportional band for the medium starting of the fan | 50 | 0  100 | % |
| Pa 13 | FAN_MAX_PROP: value of the proportional band for the maximum starting of the fan | 75 | 0  100 | % |
| Pa 14 | DEAD_VALVPRO: dead zone for starting proportional valve | 1 | 0  100 | Seconds |
| Pa 15 | DEAD_FANAUTO: hysteresis proportional band to start the fans | 3 | 0  99 | % |
| Pa 16 | DEAD_FANMAN: hysteresis temperature of the fans in manual opeation | 10 | 0  99 | C/10 |
| Pa 17 | ENA_CAMPCOOL: temperature sampling in cooling (1 = sampling only with fan in operation) | 0 | 0 1 | Flag |
| Pa 18 | HOT_START: enabling temperature for HOT START | 35 | 0  99 | C |
| Pa 19 | TO_COOL: enabling temperature for TOO COOL | 10 | 0  99 | C |
| Pa 20 | DEAD_CONS: temperature hysteresis on HOT START and TOO COOL | 20 | 0  99 | C/10 |
| Pa 21 | HEAT_INTEG: value of the proportional band starting integration heaters | 80 | 0  200 | % |
| Pa 22 | DEAD_HEAT: hysteresis proportional band for heaters deactivation | 20 | 0  30 | % |
| Pa 23 | FAN_PER_HEAT: Enables periodical fan controller in HEAT (0=no periodical fan controller, 1=periodical fan controller) | 1 | 0  1 | Flag |
| Pa 24 | POST_FAN_HEAT: post-fan controller with heaters only | 30 | 0  99 | Seconds |
| Pa 25 | FAN_PERIOD_ON: time of periodical fan controller | 30 | 0  99 | Seconds |
| Pa 26 | FAN_PERIOD_OFF: break time of periodical fan controller | 5 | 0 99 | Mins |
| Pa 27 | T_VALV_MIN (MINUTES): total opening (closing) time for proportional valve | 3 | 0  9 | Mins |
| Pa 28 | T_VALV_SEC (SECONDS): total opening (closing) time for proportional valve | 30 | 0  59 | Seconds |
| Pa 29 | AUTO_SET: automatic temperature control set | 21 | 10  40 | C |
| Pa 30 | ENA_AUTO_SET: enables temperature automatic control set | 1 | 0  1 | Flag |
| Pa 31 | T_TASTH2O: periodical opening of the valve in two-pipe fan coils, according to the water temperature | 1 | 0  200 | Hours |
| Pa 32 | T_ANTIFREEZE: antifreeze temperatures | 5 | 0  15 | °C |
| Pa 33 | PRE_HEA: delay in heater starting | 100 | 0  200 | Seconds*10 |
| Pa 34 | POLARITY: polarity for configuration of digital inputs | 2 | 0  3 | No. |
| Pa 35 | NIGHTSET_B: selection of night set point (offset Night Set Back) | 8 | 0  99 | °C/10 |
| Pa 36 | OFFST1: Ambient probe Offset | 0 | 0  99 | °C/10 |
| Pa 37 | OFFST2: Water probe Offset | 0 | 0  99 | °C/10 |
| Pa 38 | OFFST3: Potentiometer Offset (setting of the set point on local keyboard) | 0 | 0  99 | °C/10 |
| Pa 39 | OFFST5: Ambient probe for keyboard with display Offset | 0 | 0  99 | °C/10 |
| Pa 40 | TIM_CLO_VAL: time after which the switching of the valve is forced | 178 | 0  200 | Hours |
| Pa 41 | CLOS_TIME: time of periodical closing (forcing) of the valve | 20 | 0  200 | Seconds |
| Pa 42 | BLOKEY: block of the local keyboard | 0 | 0  1 | Flag |

# Diagnostics

x

The control is capable of carrying out a complete diagnostic of the installation and provides a series of alarms.

All the alarm conditions are signalled at the keyboard associated thereto for each analogue input.

The signal consists in:

Alarm

signals

- Blinking of AUTO led in the local keyboard;

- Error message “err” on the display for the keyboard with display.

The description of the types of alarms detected by FC 100 follows

## Ambient temperature probe alarm

Failure or bad connection of the probe (air temperature) installed at each convector or at the keyboard display.

For the detection of the temperature of the ambient air, a distinction is made between:

- installation of single device (the locally available inputs are used),

- installation of a FC 100 network. In this case, the probe located at the keyboard with display (i.e. “remote” since it is normally associated to the master card) is primarily used. In such case, a unified temperature control for the entire network takes places.

Should one of these events occur:

- the “remote” probe (and therefore the keyboard with display) is not present or is not connected,

- the probe associated to the keyboard with display is in failure,

- there are errors in the network communication of FC 100, i.e. the serial zone connection is absent

local probes are used for each card (local control).

If the local probe is absent or in failure, the temperature control is impossible: all the loads (except for post fan controller) are deactivated and the alarm is signalled.

The error mode in the card is displayed on the relative keyboard, not on the one associated to the master card.

## Water temperature probe alarm

Failure or bad connection of the probe (water temperature) installed at the convector.

It is signalled for the two-pipe configuration only.

The alarm signal appears only on the card related to the water probe.

In such a case, the alarm causes the deactivation of the device (except for post-fan controller).

In case of four-pipe convector, the control continues with no deactivation of the loads.

## Other cases of alarm signals

If the communication between the local card and the master card is impossible, the local card does not have the temperature control capability and therefore switches in the OFF mode.

The error mode is signalled only on the local keyboard.

The communication error affects the management of the set point, besides that of the inputs (air and water temperature).

Remember that priority is given to the set point set on the keyboard associated to the master card (provide this is present and the serial communication correct); otherwise the set point set on the local keyboard is adopted.

## Temperature control deactivations for analogue inputs failure

According to the operation modes, in case of failure of the analogue inputs, temperature controls are deactivated according to the following table:

Failure of the analogue inputs

| Operation mode | COOL | HEAT | AUTO |
| --- | --- | --- | --- |
| Deactivated functions | - Fan - Water valve (both ON/OFF and proportional) | - Fan - Water valve (both ON/OFF and proportional) | - Regulation algorithm for the switching between the COOL and the HEAT mode - Fan - Water valve (both ON/OFF and proportional) |

In any case, the post fan controller is guaranteed if:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- The alarm is started when the electrical heater is in operation: the electrical heater is disabled, the post-fan controller is started for a time equal to Pa 24.

- The alarm is started when post-fan controller has already started: the fan continues operating until the end of the time (Pa 24).

# Technical features

x

## Basic card

|  | Typical Value | Min. Value | Max Value |
| --- | --- | --- | --- |
| Power supply voltage | 12 V~ | 10 V~ | 14 V~ |
| Power supply frequency | 50 Hz / 60 Hz | --- | --- |
| Power | 5 VA | --- | --- |
| Isolation class | // |  |  |
| Protection degree | // |  |  |
| Ambient temperature for operation | 25°C | 0°C | 60°C |
| Ambient humidity for operation (non condensing) | 30% | 10% | 90% |
| Ambient temperature for storage | 25°C | -20°C | 75°C |
| Ambient humidity for storage (non condensing) | 30% | 10% | 90% |

For all the low voltage inputs: wires cross section 2.5 mm².

DIMENSIONS:

dimensions 120x65 mm,

for installation on convector

## Keyboards: local, with display (wall, living)

|  | Typical Value | Min. Value | Max Value |
| --- | --- | --- | --- |
| Isolation class | SELV KEYBOARD(SAFETY EXTRA LOW VOLTAGE) |  |  |
| Protection degree | IP 65 |  |  |
| Ambient temperature for operation | 25°C | 0°C | 60°C |
| Ambient humidity for operation (non condensing) | 30% | 10% | 90% |
| Ambient temperature for storage | 25°C | -20°C | 75°C |
| Ambient humidity for storage (non condensing) | 30% | 10% | 90% |

DIMENSIONS:

- Local keyboard:

frontal 120x70 mm,

depth 21 mm,

for wall installation or as a panel on the convector.

- Keyboard with display, wall installation:

frontal 123x80 mm,

depth 23 mm,

for wall installation.

- Keyboard with display, living:

frontal 74x38 mm,

depth 20 mm,

for living installation.

# Use of the device

x

## Allowed usages

For security reasons, the control must be installed and used according to the provided instructions.

In normal conditions, parts subject to dangerous voltage should not be accessible.

The basic card must be suitably protected from water and dust, according to the type of application, and must be accessible only using a tool.

Be particularly careful to the instructions on the installation safety.

The basic card is apt to be installed in household appliances and/or similar equipment in the air conditioning field.

As to the reference regulations, the device is classified:

- According to the construction: as an automatic electronic control device with independent installation for the keyboard or to be integrated for the basic card.

- According to the characteristics of the automatic operation: as action control device of the type 1 in relation with the fabrication tolerances and with the creeps.

- As device belonging to Class 2 in relation with the protection against electric shocks.

- As device belonging to Class A in relation with the class and the structure of the software.

## Not allowed usages

Any usage different from those allowed is NOT ALLOWED.

It is hereby pointed out that the provided relays are of the functional type and subject to failure (since they are managed by an electronic device, they can short circuit or remain open).

Possible protection devices provided by the product regulations or suggested by commons sense for evident safety reasons must therefore be installed outside the instrument

## Reference regulations

Compliance, if applicable, with:

the following EC directives:

- LOW VOLTAGE:

EEC DIRECTIVE73/23/EEC

complying with the harmonised regulation EN60335-1, if applicable.

- ELECTROMAGNETIC COMPATIBILITY:

In relation to this, all the standard precautions have been taken.

However, since the card is considered as an open component, with no direct functionalities, no declaration of conformity is issued in relation with electromagnetic compatibility.

# Responsibility and residual risks

x

Microtech S.r.l. is not responsible for damages deriving from:

- Installation and/or uses different from those provided and in particular differing from the safety rules provided by regulations in force and/or with the present manual

- Use on equipment that are not safe enough against electric shocks, water and dust when installed

- Use on equipment allowing the access to dangerous parts without the use of suitable tools

- Tampering and/or alteration of the product

- Installation and/or use in apparatuses not compliant with the rules and regulations in force.

# Glossary

x

Having several inputs in OR relation means having a single input assuming the following mode:

Logical OR

On if at least one input is on

Off if no input is on.

To scroll up a menu means listing in order the various parametres from bottom to top.

Scroll up

(Pa08 -> Pa09 -> Pa10 ....)

Means that all the instruments functions are suspended.

Stand by

Means to set at zero.

Reset

To reset an alarm means resetting it and make it active for new signals.

Alarm reset

An alarm having an manual reset can be reset only by operating on the keyboard.

Manual alarm reset

Scroll down

To scroll down a menu means listing in order the various parametres from top to bottom.

(Pa10 -> Pa09 -> Pa08 ....)

Generally refers to led.

BLINK

The average is calculated as the ratio between the sum of the hours of the available compressors and the number of the compressors of the circuit.

Average of the hours

The various device of the installation are intended, i.e. compressors, fans, hydraulic pump, antifreeze resistors etc.

Loads

It is a reference value (that can be set by the user) definining the operating status of the installation. An example is provided by the thermostat regulating the house temperature: if we want to maintain the temperature at 20°C, we set the setpoint at 20°C. The heating will start if the detected ambient temperature is lower than 20°, otherwise it will deactivate.

SetPoint

An interval of values is intended. For example the Range 1...100 specifies all the values comprises between 1 and 100.

Range

Usually a hysteresis is set on a set point in order to avoid frequent oscillation of the modification of the status of the controlled load;

Hysteresis

For example: suppose a setpoint is set at 20 °C on a probe that detects the ambient temperature and once this is exceeded a compressor activates;

When the ambient temperature assumes values close to the setpoint (20 °C), there will be an instability phase where the relay starting the compressor will switch frequently between the ON and OFF mode; such a behaviour might seriously damage the installation.

In order to avoid the problem, a hysteresis as a tolerance interval where no change of position takes place is defined; in this case, supposing a 1°C hysteresis, the compressor will activate at  21 °C (setpoint  + hysteresis) and deactivate at 19 °C (setpoint - hysteresis).

It is a memory that maintains the data even when the device is off (differs from the volatile memory that loses the data when the device is turned off) .

Non volatile memory

Is the change of the operation mode (e.g.: from Cooling to heating).

Change over

Usually indicates a compensation value that is to be added or subtracted e.g. to a setpoint.

Offset

# analitic index

2

24 V AC outputs	9

A

Access to parameters through keyboard with display	28

Alarm reset	35

Allowed usages	33

Ambient probe	20

Ambient temperature probe alarm	31

Analogue inputs	11

Antifreeze	27

Auto	19

Automatic set point	20

Average of the hours	35

B

Basic card	32

Basic Module	5

BLINK	35

Button combinations	14

Buttons	13

FAN/OFF button	13

Mode button	13

C

card	10

Change over	35

Components	5

Configuration’s dip switch	11

Connection diagrams	8

Connection of the loads to FC 100	8

Analogue	8

Digital inputs	8

Digital outputs	9

inputs	8

Connection of the loads to FC 100:	8

Connection to keyboard with display	9

Connection to local keyboard	9

Connections	7; 8

contrast	26

Cool	19

D

device	10

DIAGNOSTICS	31

Digital inputs	11; 12

Dip switch	11

Display	15

Down button	14

E

Electric plate	6

Electrical	17

Electrical heaters configurations	17

Electrical heaters control	23

F

Fan	12; 16

Fan coil typology	16

Fan control	21; 22; 24

Fan mode	19

FAN/OFF button	14

Fans configuration	16

FC 100 network	10

Diagram	10

Four pipe installation	16

FUNCTIONS	25

G

GLOSSARY	35

H

Heat	19

heaters	17

Hot start	25

Hot start function	25

Hysteresis	35

I

Inputs configuration	11; 12

INSTALLATION	7

Instrument installation	7

INTRODUCTION	5

K

Keyboard block	17

Keyboard on	6

Keyboard sleep	27

Keyboard with display	5

Keyboard with display configuration	13

Keyboards	5

local, with display (wall, living)	32

Keyboards’ dip switch	9

L

Leds	13

LEDS	14

Loads	35

Local keyboard	5

Local keyboard configuration	13

Logical OR	35

M

Manual alarm reset	35

Manual selection of the set point	19

Master	10

Mode button	13

N

Night set back	26

Non volatile memory	35

Not allowed usages	33

O

Offset	35

Offset of the local keyboard potentiometer (knob)	17

ON/OFF valve	16

Operation mode	19

Operation mode selection:	19

Operation modes:	19

Other cases of alarm signals	31

outputs	12

P

Param Manager	6

PARAMETERS	28

Parameters description	28

Periodical fan controller	25

Periodical opening of the valve	26

Post fan-controller	25

Post-fan controller heat mode	25

Power supply	8

Probes	17

Probes configurations	17

Proportional regulation algorithm	20

Parameters	20

Proportional valve	16

R

Range	35

Reference regulations	33

Relays	12

Remote controls	20

Reset	35

RESPONSIBILITY AND RESIDUAL RISKS	34

S

Scroll down	35

Scroll up	35

Season	26

Serial communication	12

Serial communication port TTL	9

Serial Interface EWTK	6

Set point	19

Set Point knob	13

Set point selection for night operation (night set back)	26

Set point setting	19

SetPoint	35

speed	12

Stand by	35

SYSTEM CONFIGURATION	16

T

table	19

Table of  parameters	29

Table of parameters	29

TECHNICAL FEATURES	32

Temperature control deactivations for analogue inputs failure	31

TEMPERATURE CONTROL FUNCTIONS	19

Temperature control in  HEAT mode	22

Temperature control in AUTO mode	23

Temperature control in COOL mode	21

Temperature control in FAN mode	23

Temperature detection	20

Too cool	25

Too cool function	25

Triac digital	12

Two pipe installation	16

U

Up button	14

USE OF THE DEVICE	33

USER INTERFACE	13

V

Valve	16

valve connection	12

Valve control	22; 24

On/off	22

Proportional valve case	22

valve case	22

Valve forcing	26

Valves configuration	16

Voltage failure	27

W

Warnings	7

Water probe	20

Water temperature probe alarm	31

|  |  | FC 100 2000/10 Cod. 8MA10104 |
| --- | --- | --- |