ENERGY 400

4 Steps Chiller Heat Pump Controller

User Manual

# CONTENTS

1    Contents	3

2	How to use this manual	5

3	Introduction	6

3.1	Components	6

3.1.1	Basic Module	6

3.1.1	Expansion	6

3.1.2	Keyboards	6

3.1.3	CF (Control Fan) Modules	6

3.1.4	Copy Card	6

3.1.5	Serial Interface (EWTK)	6

3.1.6	Param Manager	6

4	Installation	7

4.1	Connection diagrams	7

4.2	Dimensions	9

4.3	Configuration of analogue inputs	10

4.4	Configuration of digital inputs	11

4.5	Configuration of outputs	12

4.5.1	Power outputs	12

4.5.2	Low voltage outputs	12

4.5.3	Serial outputs	12

4.6	Physical quantities and units of measurement	12

5	User Interface	13

5.1	Keys	13

5.2	Display	13

5.2.1	Display	13

5.2.2	Led	13

5.3	Wall-mounted keyboard	14

5.4	Programming parameters – Menu levels	14

5.5	Visibility of parameters and submenus	16

5.5.1	Copy Card	16

6	System configuration	17

6.1	Compressors	17

6.2	Compressor configuration	17

6.2.1	Compressor (or power step) on/off sequences	18

6.2.2	Compressor timing	19

6.3	Condensation fan	20

6.3.1	Fan configuration	20

6.3.2	Fan control configuration	21

6.4	Reversing valves	21

6.5	Hydraulic pump	21

6.6	Anti-freeze/supplementary electrical heaters	21

6.7	Internal fan	22

6.8	Condensation-Defrost probes	22

7	Temperature control functions	23

7.1	Setting set points	23

7.2	Dynamic Set point	23

7.3	Load control	25

7.3.1	Compressor control – regulation algorithm	25

7.3.2	Condensation fan control	26

7.3.3	Combined or Separate Condensation	28

7.3.4	Hydraulic pump control	28

7.3.5	Anti-freeze/supplementary electrical heater control	29

7.3.6	Reversing valve control	29

8	Functions	30

8.1	Recording hours of operation	30

8.2	Defrost	30

8.2.1	Defrost start	30

8.2.2	Control during defrost	31

8.2.3	Defrost end	31

9	Parameters	33

9.1	Description of Parameters	33

9.2	Parameters table	38

10	Diagnostics	42

10.1	List of alarms	42

11	Technical features	49

11.1	Technical data	49

11.2	Electromechanical features	49

11.3	Regulations	49

12	Use of the device	50

12.1	Permitted use	50

12.2	Forbidden use	50

13	Responsibility and residual risks	51

14	Glossary	52

# How to use this manual

x

This manual is designed to permit quick, easy reference with the following features:

References column:

References

A column to the left of the text contains references to subjects discussed in the text to help you locate the information you need quickly and easily.

Cross references:

Cross references

All words written in italics are referenced in the subject index to help you find the page containing details on this subject;

supposing you read the following text:

”when the alarm is triggered, the compressors will be shut down”

The italics mean that you will find a reference to the page on the topic of compressors listed under the item compressors in the index.

If you are consulting the manual “on-line” (using a computer), words which appear in italics are hyperlinks: just click on a word in italics with the mouse to go directly to the part of the manual that discusses this topic.

Some segments of text are marked by icons appearing in the references column with the meanings specified below:

Icons for emphasis

<IMG INFO>

36,75

24,25

0

2

0

14,15

-1

Take note: 	information on the topic under discussion which the user ought to keep in mind

<IMG INFO>

28,3

29,3

0

2

0

14,15

-1

Tip: 	a recommendation which may help the user to understand and make use of the information supplied on the topic under discussion.

<IMG INFO>

33,9

27,7

0

2

0

14,15

-1

Warning! : 	information which is essential for preventing negative consequences for the system or a hazard to personnel, instruments, data, etc., and which users MUST read with care.

# Introduction

x

Energy 400 is a compact device that permits control of air conditioning units and heat pump of the following types:

- air-air

- air-water

- water-water

- water-air

- motor-condensing

The controller can manage machines with up to four power steps distributed in a maximum of 2 cooling circuits (for example, 2 circuits, with 2 compressors per circuit).

Main characteristics:

- Outflowing water temperature control

- Condensation control

- 2 inputs which may be configured for NTC or 4-20mA (through parameters)

- 11 configurable digital inputs  + (4 four optional)

- Dynamic set point

- Setting of parameters from the keyboard, with a personal computer or with a memory card

- Remote keyboard (100 m) which may be connected up directly without serial interfaces.

- 3 4-20 mA outputs

- Control of 1, 2, 3, or 4 compressors.

## Components

We will now look at the basic components and accessories in the system and how they are connected.

### Basic Module

The basic module is an electronic card for connection with I/O resources and a CPU as described in the section on connection diagrams.

### Expansion

The expansion module is an electronic card for connection as described in the section on connection diagrams.

### Keyboards

Two types of keyboard are available:

- TS-P: Panel keyboard (32x74)

- TS-W: Wall-mounted keyboard

### CF (Control Fan) Modules

Used to connect fans with Energy 400 low voltage outputs.

### Copy Card

Can be used to upload and download the Energy 400 parameter map.

### Serial Interface (EWTK)

A device which permits the controller to interface with a Personal Computer

It must be connected up as illustrated in the figure

<IMG INFO>

311,6

108,25

0

2

56,7

14,15

-1

The PC must be connected with the interface module, and the interface module with the device, with no power on to any of the devices, and in compliance with current safety regulations . Be careful to avoid electrostatic shocks, especially on exposed metal parts of the devices; allow electrostatic shocks to discharge into the ground before handling.

<IMG INFO>

31,1

25,65

1

2

76,55

-12,8

-1

### Param Manager

If you have an adequate Personal Computer with Windows 95 or a more recent operating system, the Param Manager software,  an adequate interface module and proper wiring, you can have full control over all Energy 400 parameters via Personal Computer.

The instrument can be programmed easily and quickly using a series of interfaces which permit a logical, guided approach.

# Installation

x

Before proceeding with any operation, first make sure that you have connected up the power supply to the device through an appropriate external current trransformer.

Always follow these rules when connecting boards to one another and to the application:

<IMG INFO>

31,1

25,65

1

2

76,55

-12,8

-1

Never apply loads which exceed the limits set forth in these specifications to outputs;

Always comply with connection diagrams when connecting up loads;

To prevent electrical couplings, always wire low voltage loads separately from high voltage loads;

## Connection diagrams

Basic module

ALARM RELAY

RELAY COMMON

RELAY 1

RELAY 2

RELAY 3

RELAY 4

RELAY 5

RELAY 6

RELAY 7

CONN A

CONN B

EXPANSION

KBD

SERIAL

-     S    +

Basic Module

Detail of connectors

12 AC

ST1

ID1

GND

AN1

GND

ST4

ST3

ST2

ID2

12 AC

12 DC

TK1

ID5

ID4

ID3

NC

ST5

ID6

GND

AN2

GND

NC

ID11

ST6

ID7

NC

12 DC

TK2

ID10

ID9

ID8

CF CONTROL

CF CONTROL

Line

EMI

FILTER

Connections with NTC sensors

Connections with pressure sensor

12 AC

ST1

ID1

GND

AN1

GND

ST4

ST3

ST2

ID2

12 AC

12 DC

TK1

ID5

ID4

ID3

CF CONTROL

Line

CONN A

NC

ST5

ID6

GND

AN2

GND

NC

ID11

ST6

ID7

NC

12 DC

TK2

ID10

ID9

ID8

CF CONTROL

CONN B

EMI

FILTER

Expansion Connectors

RELAY 9

RELAY 10

EXPANSION

CONN C

CONN C

ID 15

ID 14

ID 13

ID 12

Common

Expansion Connectors diagram

Keyboard connectors

Panel keyboard rear

S    +    -

24

25

26

Wall mounted keyboard rear

S    +    -

Keyboard connectors

## Dimensions

Basic Module Dimension

Expansion module dimension

## Configuration of analogue inputs

There are 6 analogue inputs:

Analogue inputs

- 4 NTC transducers,

- 2 configurable NTC/4-20mA transducers.

The following devices shall henceforth be referred to by the codes ST1….ST6:

ST1 – Temperature control probe: inflowing water or air, reading range : -30°C ¸ 90°C;

ST2 – Configurable probe, reading range: -30°C ¸ 90°C;

ST3 - Configurable NTC probe, 4-20mA

ST4 - Configurable probe, reading range : -30°C ¸ 90°C;

ST5 - Configurable NTC probe, 4-20mA

ST6 - Configurable probe, reading range: -30°C ¸ 90°C;

4 analogue inputs are available on the extension.

Analogue inputs: resolution and precision

The resolution of NTC analogue inputs is one tenth of a Kelvin degree;

They are precise to within 0.8C within the range of 035C and to within 0.8C ¸ 3C in the remainder of the scale.

The 4-20mA input is precise to within 1% FS, with a resolution of one tenth of a Kelvin degree, if the input is configured as a dynamic set point, or Kpa*10 if the input is configured as a pressure probe.

ST1-ST6 probes can be configured according to the following table:

Analogue inputs: configuration table

| - Pa. | - Description | - Value |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | - 0 | - 1 | - 2 | - 3 | - 4 | - 5 |
| - H11 | - Configuration of analogue input ST1 | Probe absent | NTC input - inflowing water or air | Digital input request for heating | Digital input request for temperature control | - Differential NTC input | - Not permitted |
| - H12 | - Configuration of analogue input ST2 | Probe absent | - NTC input outflowing water/air, anti-freeze | Digital input request for cooling | Not permitted | Not permitted | Not permitted |
| - H13 | - Configuration of analogue input ST3 | Probe absent | - NTC input condensation | - 4...20 mA condensation input | - 4...20 mA input for dynamic set point | - NTC antifreeze for water-water gas reversal machines | - NTC heating control for water-water water reversal machines |
| - H14 | - Configuration of analogue input ST4 | Probe absent | - NTC input condensation | - Multifunctional digital input | - NTC input for outdoor temperature | Not permitted | Not permitted |
| - H15 | - Configuration of analogue input ST5 | Probe absent | NTC input outflowing water/air | Not permitted | Not permitted | Not permitted | Not permitted |
| - H16 | - Configuration of analogue input ST6 | Probe absent | NTC input condensation circuit 2 | 4-20mA input condensation | Not permitted | Antifreeze input for water-water gas reversal machines | Not permitted |

If inputs ST3 and ST6 are defined as 4-20mA inputs under pressure, the scale bottom value of the pressure input is also significant:

Pa H17= Maximum input value; set the corresponding value to a current of 20 mA

## Configuration of digital inputs

There are 11 voltage-free digital inputs, which will henceforth be identified as ID1….ID11.

Digital inputs

ST1, ST2, and ST4 may be added to these if they are configured as digital inputs (through parameters Pa H11, Pa H12, Pa H14). 4 more digital inputs are available on the expansion.

The polarity of digital inputs is determined by the parameters listed below:

Digital inputs: polarity

ID1, ID2, ID3, ID4 defined by parameter Pa H18,

ID5, ID6, ID7, ID8 defined by parameter Pa H19

ID9, ID10, ID11, ST4 (if configured as digital) defined by parameter Pa H20

ID12,ID13,ID14,ID15 on extension defined by parameter Pa N01

Digital inputs: Polarity table

| - Pa H18 - Pa H19 - Pa H20 - Pa H21 | - ID1 | - ID2 | - ID3 | - ID4 |
| --- | --- | --- | --- | --- |
|  | - ID5 | - ID6 | - ID7 | - ID8 |
|  | - ID9 | - ID10 | - ID11 | - ST4 |
|  | - ID12 | - ID13 | - ID14 | - ID15 |
| - 0 | - Closed | - Closed | - Closed | - Closed |
| - 1 | - Open | - Closed | - Closed | - Closed |
| - 2 | - Closed | - Open | - Closed | - Closed |
| - 3 | - Open | - Open | - Closed | - Closed |
| - 4 | - Closed | - Closed | - Open | - Closed |
| - 5 | - Open | - Closed | - Open | - Closed |
| - 6 | - Closed | - Open | - Open | - Closed |
| - 7 | - Open | - Open | - Open | - Closed |
| - 8 | - Closed | - Closed | - Closed | - Open |
| - 9 | - Open | - Closed | - Closed | - Open |
| - 10 | - Closed | - Open | - Closed | - Open |
| - 11 | - Open | - Open | - Closed | - Open |
| - 12 | - Closed | - Closed | - Open | - Open |
| - 13 | - Open | - Closed | - Open | - Open |
| - 14 | - Closed | - Open | - Open | - Open |
| - 15 | - Open | - Open | - Open | - Open |

Example: A value of “10” for parameter Pa H18 indicates that digital inputs ID1 and ID3 are active when their contacts are closed and digital inputs ID2 and ID4 are active when their contacts are open:

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

| - Pa H18 | - ID1 | - ID2 | - ID3 | - ID4 |
| --- | --- | --- | --- | --- |
| - 10 | - Closed | - Open | - Closed | - Open |

If ST1 is configured as digital, its polarity is defined by parameter Pa H21

If ST2 is configured as digital, its polarity is defined by parameter Pa H22

| Parameter Value | Description |
| --- | --- |
| 0 | Active if closed |
| 1 | Active if open |

All digital inputs are configurable and may be given the meanings listed below by setting parameters Pa H23 through Pa H34 and Pa N02 through Pa N05

Digital inputs: Configuration Table

| Parameter Value | Description |
| --- | --- |
| 0 | Input disabled |
| 1 | Flow switch |
| 2 | Remote OFF |
| 3 | Remote Heat/Cool |
| 4 | Thermal switch compressor 1 |
| 5 | Thermal switch compressor 2 |
| 6 | Thermal switch compressor 3 |
| 7 | Thermal switch compressor 4 |
| 8 | Thermal switch fan circuit 1 |
| 9 | Thermal switch fan circuit 2 |
| 10 | High pressure circuit 1 |
| 11 | High pressure circuit 2 |
| 12 | Low pressure circuit 1 |
| 13 | Low pressure circuit 2 |
| 14 | High pressure compressor 1 |
| 15 | High pressure compressor 2 |
| 16 | High pressure compressor 3 |
| 17 | High pressure compressor 4 |
| 18 | End of defrost circuit 1 |
| 19 | End of defrost circuit 2 |
| 20 | 2° power step request |
| 21 | 3° power step request |
| 22 | 4° power step request |

In the case of multiple inputs configured with the same value, the function associated with the input will carry out a Logical OR among the inputs.

Configuration of outputs

Outputs

There are two basic types of outputs: power outputs, and low voltage outputs.

### Power outputs

There are 8 power outputs, which shall henceforth be referred to as RL1…RL8 (relays).

RL1 - compressor 1, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL2 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL3 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL4 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL5 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL6 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL7 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL8 – cumulative alarm, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

There are 2 additional digital  outputs in the extension module:

RL9 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

RL10 - configurable, 5 A 125VAC/230VAC Res; ¼ HP 230VAC, 1/8 HP 125VAC;

Configurable outputs may be given the following meanings by setting parameters Pa H35 through Pa H40 and Pa N06 through Pa N07

Configuration table

| Value | Description |
| --- | --- |
| 0 | Disabled |
| 1 | Reversal valve circuit 1 |
| 2 | Reversal valve circuit 2 |
| 3 | Condenser fan circuit 1 |
| 4 | Condenser fan circuit 2 |
| 5 | Electrical heater 1 |
| 6 | Electrical heater 2 |
| 7 | Pump |
| 8 | Evaporator fan |
| 9 | Power Step 2 |
| 10 | Power Step 3 |
| 11 | Power Step 4 |

Polarity of RL2,RL3,RL4,RL5,RL8 may be selected using Pa H41-Pa H45

Polarity Table

| Parameter Value | Description |
| --- | --- |
| 0 | Relay closed if output active |
| 1 | Relay open if output not active |

If multiple outputs are configured with the same resource, the outputs will be activated in parallel.

### Low voltage outputs

There are a total of 4 low voltage outputs available: 2 phase cut outputs and 2 4-20 mA outputs:

TK1 – Output for piloting external fan control modules in circuit 1.

TK2 – Output for piloting external fan control modules in circuit 2.

AN1 - 4-20mA output for control of fans in circuit 1

AN2 - 4-20mA output for control of fans in circuit 2

Outputs AN1 and AN2, though their connections are physically separate, are alternatives to outputs TK1 and TK2 which are selected by parameters Pa H45 and Pa H46

Configuration of fan outputs

| Fan config. parameter | Index | Value 0 | Value 1 |
| --- | --- | --- | --- |
| Fan 1 output | H45 | Fan 1 output in phase cut | Fan 1 output in 4-20 mA |
| Fan 2 output | H46 | Fan 2 output in phase cut | Fan 2 output in 4-20 mA |

### Serial outputs

There are 2 asynchronous serials on the control:

- channel for serial communication with a personal computer through a Microtech interface module (966,e,8,1)

- channel for serial communication with a standard Microtech keyboard. Power supply 12 VDC (2400,e,8,1).

## Physical quantities and units of measurement

Parameter Pa H64 may be used to set temperature display in either degrees °C or degrees °F:

Unit of measurement:

selection

| Pa H64 | Unit of measurement |
| --- | --- |
| 0 | Degrees °C |
| 1 | Degrees °F |

# User Interface

x

The interface on the front panel of the instrument can be used to carry out all the operations connected to the use of the instrument, and in particular to:

- Set operating mode

- Respond to alarm situations

- Check the state of resources

Front panel of the instrument

Keyboard

<IMG INFO>

212

100,25

0

2

106,35

14,15

-1

The instrument can function without the aid of a keyboard

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

## Keys

Selects operating mode:

Mode

If the heating mode is enabled, each time the key is pressed the following sequence occurs:

Stand-by - cooling  heating  stand-by

<IMG INFO>

36,8

29,3

1

2

70,85

-14,65

-1

if heating mode is not enabled:

Stand-by   cooling  stand-by

In menu mode, this key acts as a SCROLL UP or UP key (increasing value).

Resets alarms, and turns the instrument on and off.

On-off – Alarms reset

Press once to reset all manually reset alarms not currently active; all the alarm events per hour will also be reset even if the alarms are not active.

Hold down the key for 2 seconds to turn the instrument from on to off or vice versa. When it is off, only the decimal point remains on the display. In menu mode this key acts as a SCROLL DOWN or DOWN key (decreasing value).

<IMG INFO>

36,8

28,85

1

2

70,85

-14,45

-1

Pressing the “mode” and “on-off” keys at the same time:

Combination mode – onoff keys

If you press both keys at the same time and then release within 2 seconds, you will move one level deeper in the display menu.

If you press both keys for more than 2 seconds you will move one level up.

If you are currently viewing the lowest level in the menu and you press both keys and release within 2 seconds, you will go up one level.

<IMG INFO>

50,85

52,05

1

2

56,7

-26

-1

## Display

The device can communicate information of all kinds on its status, configuration, and alarms through a display  and a number of leds on its front panel.

### Display

Normal display shows:

- regulation temperature in tenths of degrees celsius or fahrenheit

- the alarm code, if at least one alarm is active. If multiple alarms are active, the one with greater priority will be displayed, according to the Table of Alarms.

If temperature control is not analogue and depends on the status of a digital input (ST1 or ST2 configured as digital inputs), the “On” or “Off” label will be displayed, depending on whenther temperature control is active or not.

<IMG INFO>

56,5

27,05

1

2

51

-13,5

-1

- When in menu mode, the display depends on the current position; labels and codes are used to help the user identify the current function.

### Led

Led 1 compressore 1.

ON if compressor 1 is active

<IMG INFO>

42,45

38,35

1

2

65,2

-19,15

-1

- OFF if compressor 1 if off

- Rapid BLINK if safety timing is in progress

- Slow BLINK if compressor is currently set to defrost

Power step 2 led

ON if power step 2 is active

<IMG INFO>

42,45

38,35

1

2

65,2

-19,15

-1

- OFF if power step 2 is not active

- Rapid BLINK if safety timing is in progress

- Slow BLINK if step 2 is currently defrosting

Led  step 3 di potenza

ON se lo step 3 di potenza è attivo

<IMG INFO>

42,45

38,35

1

2

65,2

-19,15

-1

- OFF se lo step 3 di potenza non è attivo

- BLINK veloce se sono in corso temporizzazioni di sicurezza

- BLINK lento se step 3 in sbrinamento

Power step 4 led

ON if power step 4 is active

<IMG INFO>

42,45

38,35

1

2

65,2

-19,15

-1

- OFF if power step 4 is not active

- Rapid BLINK if safety timing is in progress

- Slow BLINK if step 4 is defrosting

Electrical heater/boiler led

ON if at least one internal anti-freeze electrical heater or boiler is enabled

<IMG INFO>

28,3

30,45

1

2

79,35

-15,25

-1

- OFF if both are off

Heating Led

ON if the device is in heating mode.

<IMG INFO>

28,3

28

1

2

79,35

-14

-1

Cooling Led

ON if the controller is in cooling mode

<IMG INFO>

28,3

27,35

1

2

79,35

-13,7

-1

If neither the HEATING led nor the COOLING led are in, the controller is in STAND-BY mode.

When it is off, only the decimal point appears on the display.

## Wall-mounted keyboard

The remote keyboard a on the display is an exact copy of the information displayed on the instrument, with the same leds;

Remote keyboard

Remote keyboard

<IMG INFO>

282,8

148,35

0

2

70,9

14,15

-1

It performs exactly the same functions as those described in the display section.

The only difference is in use of the UP and DOWN keys (to increase and decrease value), which are separate from the MODE and ON/OFF keys.

## Programming parameters – Menu levels

Device parameters may be modified using a Personal Computer (with the required software, interface key and cables), or using the keyboard;

If using the keyboard, access to parameters is arranged in a hierarchy of levels which may be accessed by pressing the “mode and “on-off” keys at the same time (as described above).

Each menu level is identified by a mnemonic code which appears on the display.

The structure is set up as shown in the diagram below:

Control probe

Current alarm

Set point:

Analogue Inp.:

Alarms:

Digital input:

Op. hours:

Password:

Parameters:

Label cooling set:

Label heating set:

Input code.: 
-

Current alarms Code:

Input code: 
-

Value heating set

Value cooling set

Configuration par.:

Compressor par.:

Fan control par.:

Alarms par.:

Pump par.:

Antifreeze par.:

Defrost par.:

Par. index 
-

Parameter value

Number of hours par.

Parameter value

Parameter value

Parameter value

Parameter value

Parameter value

Parameter value parametro

Comp. hours: 
-

Password value

Status of digital input

Val. analogue input

Par. index 
-

Par. index 
-

Par. index  
-

Par. index 
-

Par. index 
-

Par. index 
-

Pump hours:

Number of hours par.

Expansion par.:

Par. index. 
..

Parameter value

Menu structure

## Visibility of parameters and submenus

With a personal computer, interface key, suitable cables and the “Param Manager” software, it is possible to restrict the visibility and modification of parameters and entire submenus.

A “visibility value” may be assigned to each parameter, as described below:

label

| Value | Meaning |
| --- | --- |
| 0003 | Parameter or label visible at all times |
| 0258 | Parameter or label visible if user password entered correctly (password = Pa H67) |
| 0770 | Parameter or label visible if user password entered correctly (password = Pa H67). Parameter cannot be modified. |
| 0768 | Parameter visible from PC only. |

Some visibility settings are factory set.

For more information, please refer to the “Param Manager” instructions.

### Copy Card

The copy card can store the whole map of Energy 400 parameters;

To download the map present in the copy card, proceed as follows:

- Connect the key to the appropriate Energy 400  output (refer to connection diagrams) while the device is off.

- Turn on the Energy 400: the parameters map in the copy card will be copied to the Energy 400.

To store the Energy 400 parameters map in memory, proceed as follows:

- Connect the copy card to the appropriate Energy 400 output (refer to connection diagrams) while the device is on.

- From the keyboard, access the “password” submenu (refer to menu structure) and set the value contained in parameter Pa H46: The instrument’s map will be downloaded to the copy card.

- Disconnect the copy card when finished.

# System configuration

x

In this section we will look at how to configure parameters for various loads on the basis of the type of installation to be controlled.

## Compressors

Energy 400 can control systems consisting of up to two cooling circuits with 1 to 4 compressors.

If there is a capacity step, it will be considered as a compressor.

Each compressor is piloted by a device relay (power outputs) (each capacity step requires an additional output).

The first compressor must be connected to output RL1; the remaining outputs (RL2…RL7) (RL9…RL10 on extension) may be assigned at will, setting the value of the parameters Pa H35 …. PaH40 (Pa N06 … Pa N07 if there is no extension).

The compressors will be turned on or off depending on the temperatures detected and the temperature control functions that have been set (refer to the section on Compressor controls – Regulation algorithml )

## Compressor configuration

The turning on of an additional compressor (or capacity step) will henceforth be referred to as a Power step (power level).

Power step

It’s of main importance to identify the right compressor indexes to be assigned to the related diagnostic digital inputs. In a 2 circuit with 1 compressor each machine, for example (see next table), compressors 1 and 3 are enabled. The compressor n° 3 stops if an alarm occurs on digital input 3: the related alarm code appears on the diusplay. If an alarm occurs on digital input 2, an alarm code appears on the display, but no compresssor will be stopped for that, since there is no compressor number 2.

<IMG INFO>

28,3

23,55

1

2

79,35

-11,75

-1

Partializations belonging to a compressor in alarm condition are shut down. The leds of working compressors refer to power step indexes

The following configurations are available for compressors without capacity steps (Pa H07=0):

Simple compressors

|  |  | Number of compressors per circuit |  |
| --- | --- | --- | --- |
|  |  | 1 (Pa H06=1) | 2 (Pa H06=2) |
| Number of circuits | 1 (Pa H05=1) | RL1=comp. 1 circ.1 (alarm index 1) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = comp 2 circ.1 (alarm index 2) |
|  | 2 (Pa H05=2) | RL1=Comp. 1 circ.1 (alarm index 1) Step3 = comp. 1 circ.2 (alarm index 3) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = comp 2 circ.1 (alarm index 2) Step3 = comp 1 circ.2 (alarm index 3) Step4 = comp 2 circ.2 (alarm index 4) |

|  |  | Number of compressors per circuit |  |
| --- | --- | --- | --- |
|  |  | 3 (Pa H06=1) | 4 (Pa H06=2) |
| Number of circuits | 1 (Pa H05=1) | RL1=comp. 1 circ.1 (alarm index 1) Step2 = comp 2 circ.1 (alarm index 2) Step3 = comp. 3 circ.1 (alarm index 3) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = comp 2 circ.1 (alarm index 2) Step3 = comp 3 circ.1 (alarm index 3) Step4 = comp 2 circ.1 (alarm index 4) |
|  | 2 (Pa H05=2) | Configuration error | Configuration error |

The following configurations are available for compressors with 1 capacity step (Pa H07=1):

with 1 capacity step

|  |  | Number of compressors per circuit |  |
| --- | --- | --- | --- |
|  |  | 1 (Pa H06=1) | 2 (Pa H06=2) |
| Number of circuits | 1 (Pa H05=1) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = cap. step1 Comp.1 circ.1 | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = cap. step1 Comp.1 circ.1 Step3 = comp.2 circ.1 (alarm index 2) Step4 = cap. step1 Comp.2 circ.1 |
|  | 2 (Pa H05=2) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = cap. step1 comp.1 circ.1 Step3 = comp.1 circ.2 (alarm index 3) Step4 = cap. step1 comp.1 circ.2 | Configuration error |

The following configurations are available for compressors with 2 or 3  capacity steps (Pa H07=2 or Pa H07=3):

with 2 or 3 capacity steps

|  |  | Number of compressors per circuit |  |
| --- | --- | --- | --- |
|  |  | 1 (Pa H06=1 and Pa H07=2) | 2 (Pa H06=2 and Pa H07=3) |
| Numbero of circuits | 1 (Pa H05=1) | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = cap. step1 comp.1 circ.1 Step4 = cap. step2 comp.1 circ.1 | RL1=comp. 1 circ. 1 (alarm index 1) Step2 = cap. step1 comp.1 circ.1 Step3 = cap. step2 comp.1 circ.1 Step4 = cap. step3 comp.1 circ.1 |
|  | 2 (pa H05=2) | Configuration error | Configuration error |

### Compressor (or power step) on/off sequences

Depending on the temperature conditions detected by the probes, the temperature control functions of the “Energy 400” may request turning on and off of compressors/capacity steps (power steps).

The sequence in which compressors/capacity steps (steps) are turned on and off may be determined by adjusting the values of parameters Pa H08 and Pa H09 as described below:

|  |  | Parameter value |  |
| --- | --- | --- | --- |
| Par | Description | 0 | 1 |
| Pa H08 | Power step on sequence | Depends on number of hours of operation | Unvaried on sequence |
| Pa H09 | Circuit balacing | Circuit saturation | Circuit balancing |

When on sequences depend on the number of hours of operation, of 2 available compressors, the one which has been operated for less hours will come on first, and the one which has been operated for more hours will always go off first. In an unvaried on sequence, the compressor with the lower number will always come on first (compressor 1 before compressor 2) and the compressor with the higher number will always go off first.

The circuit balancing parameter is significant only if there are 2 circuits and 2 steps per circuit. If we select H09=0, all power steps in one circuit will come on before those in the other circuit. If H09=1 (balancing), power steps will come on in such a way that both circuits are delivering the same power, or the difference is no more than one step.

Let us take a closer look at the various combinations:

Pa H08=0 Pa H09=0

Compressors: coming on on the basis of hours of operation and circuit saturation

| CASE OF 1 COMPRESSOR WITH CAPACITY STEP PER CIRCUIT: | CASE OF 2 COMPRESSORS PER CIRCUIT: |
| --- | --- |
| The compressor with the least hours of operation comes on first, then the capacity step for the same circuit, the compressor on the other circuit, and, lastly, its capacity step. When turning off, the capacity step of the compressor with the most hours of operation goes off first, then the corresponding compressor, then the other capacity step and finally the other compressor. Example: Supposing the system has been configured as follows: RL1=Compressor 1 circuit 1 Step2 = capacity step compressor 2 Step3 = compressor 2 circuit 2 Step4 = capacity step compressor 2 If hours comp.1 > hours comp.2 they will come on in this order Step3Step4RL1Step2 and go off in this order Step2RL1Step4Step3 | If all compressors are off to start with, the circuit which has the lower average number of hours for all its compressors will come on first. In this circuit the compressor with the least hours of operation will come on first, followed by the other compressor in the same circuit: thus the circuit is saturated. The next step is chosen between the two compressors in the other circuit with fewer hours. Example: Supposing the system has been configured as follows: RL1=Compressor 1 circuit 1 Step2 = compressor 2 circuit 1 Step3 = compressor 3 circuit 2 Step4 = compressor 4 circuit 2 If hours comp.1 > hours comp.2 hours comp.4 > hours comp.3 (hours comp.1 + hours comp.2)/2>(hours comp.4 + hours comp.3)/2 they will come on in this order Step3Step4Step2RL1 and go off in this order RL1Step2Step4Step3 |

Pa H08=0 and Pa H09=1

Compressors: coming on on the basis of hours of operation and circuit balancing

| CASE OF 1 COMPRESSOR WITH CAPACITY STEP PER CIRCUIT: | CASE OF 2 COMPRESSORS PER CIRCUIT |
| --- | --- |
| The compressor with the least hours of operation comes on first, followed by the compressor in the other circuit, the capacity step of the first circuit to come on, and, lastly, the other capacity step. When going off, the capacity step of the compressor with the most hours goes off first, followed by the capacity step of the other compressor, the compressor with the most hours and, lastly, the remaining compressor. Example: Supposing the system has been configured as follows: RL1=Compressor 1 circuit 1 Step2 = capacity step compressor 2 Step3 = compressor 3 circuit 2 Step4 = capacity step compressor 3 if hours comp.1 > hours comp.3 they will come on in this order Step3RL1Step4Step2 and go off in this order Step2Step4RL1Step3 | If all compressors are off to start with, the circuit with the lower average number of hours for its compressors will come on first. The average is calculated as the ratio between the total number of hours of the compressors available and the number of compressors in the circuit. In this circuit, the compressor with the least hours will come on first, then the compressor in the other circuit with the least hours, the other compressor in the first circuit and, lastly, the remaining compressor. Example: Supposing the system has been configured as follows RL1=Compressor 1 circuit 1 Step2 = compressor 2 circuit 1 Step3 = compressor 3 circuit 2 Step4 = compressor 4 circuit 2 if hours comp.1 > hours comp.2 hours comp.4 > hours comp.3 (hours comp.1 + hours comp.2)/2>(hours comp.4 + hours comp.3)/2 they will come on in this order Step3Step2Step4RL1 and go off in this order RL1Step4Step2Step3 |

Pa H08=1 and Pa H09=0

Compressors: unvaried on sequence with circuit saturation

| CASE OF 1 COMPRESSOR WITH CAPACITY STEP PER CIRCUIT | CASE OF 2 COMPRESSORS PER CIRCUIT |
| --- | --- |
| The compressor con with the lower number comes on first, then its capacity step, then the compressor in the other circuit and, lastly, its capacity step. The capacity step for the compressor with the highest number is the first to go off, followed by the capacity step of the other compressor, and finally the compressor. Example: Supposing the system has been configured as follows: RL1=Compressor 1 circuit 1 Step2 = capacity step compressor 2 Step3 = compressor 3 circuit 2 Step4 = capacity step compressor 3 they will come on in this order RL1Step2Step3Step4 and go off in this order Step4Step3Step2RL1 | Exactly the same as the first case. |

Pa H08=1 e Pa H09=1

Compressors: unvaried on sequence with circuit balancing

| CASE OF 1 COMPRESSOR WITH CAPACITY STEP PER CIRCUIT | CASE OF 2 COMPRESSORS PER CIRCUIT |
| --- | --- |
| The compressor with the lowest number comes on first, then the compressor in the other circuit, the capacity step of the first compressor and then the capacity step of the second compressor. They go off in reverse order. Example: Supposing the system has been configured as follows: RL1=Compressor 1 circuit 1 Step2 = capacity step compressor 2 Step3 = compressor 3 circuit 2 Step4 = capacity step compressor 3 they will come on in this order RL1Step3Step2Step4 and go off in this order Step4Step2Step3RL1 | Exactly the same as the first case. |

In the unvaried sequence, if the compressor with the lower number is unavailable, the compressor with the higher number comes on.

If the compressor comes available and the amount of power required is equal to the amount of power being delivered, the machine will continue to function in its current state: it will not turn off a compressor with a higher number to turn on a compressor with a lower number.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

A compressor is unavailable when it is shut down due to an alarm or is currently counting safety timing.

<IMG INFO>

28,3

23,55

1

2

79,35

-11,75

-1

### Compressor timing

The turning on and off of compressors must comply with safety times which may be set by the user using the parameters specified below:

Safety timing

There is a safety interval between the time a compressor goes off and the time the same compressor comes back on (compressor on…off safety time, controlled by parameter Pa C01);

Off-on timing

This interval of time must elapse when the “Energy 400” is turned on.

There is a safety interval between the time a compressor is turned on and the time it is turned on again (compressor on...on safety time, controlled by parameter Pa C02) .

On-on timing

Off-on and on-on diagram for 1 compressor

Compressor

ON

OFF

OFF – ON safety time

Pa C01

Seconds*10

ON – ON safety time

Pa C02

If the machine has multiple power steps, there are intervals of time which must pass between turning on of 2 compressors (Pa C06) and turning off of 2 compressors (Pa C07). An amount of time determined by parameter Pa C08 (capacity step on delay) must elapse between the turning on of one compressor or capacity step and the turning on of any other compressor or capacity step on the machine. The greatest of the currently active safety times must be applied to each compressor.

On-on off-off times for 2 comp.

The off time interval between compressors is not applied in the event of a compressor shutdown alarm, in which case they stop immediately.

Comp.1

ON

OFF

Interval between turning off compressors Pa C07

Seconds

Interval between turning on compressors Pa C05

Comp.2

ON

OFF

Seconds

Condensation fan

on-on and off-off diagram 2 comp

“Energy 400” may be connected with two types of fan piloting unit:

- Triak

- 4-20 mA

### Fan configuration

First of all, correctly configure the type of analogue output (low voltage outputs) to which the fan control module(s) are connected;

the relevant parameters are Pa H46 for the first circuit and Pa H47 for the second circuit, as shown in the table below:

| Parameter value | Circuit 1 – Pa H46 | Circuit 2 – Pa H47 |
| --- | --- | --- |
| 0 | TK output enabled for phase cut | TK output enabled for phase cut |
| 1 | Enable 4-20 mA output AN1 | Enable 4-20 mA output AN2 |

If the output is configured as a proportional triac, the parameters PICK-UP, PHASE SHIFT, and IMPULSE DURATION are also significant.

Every time the external fan is started up, power is supplied to the exchanger fan at maximum voltage, and the fan operates at maximum speed, for an amount of time equal to Pa F02 seconds/10; after this time the fan operates at the speed set by the regulator.

Pick-up

Pa F02 = Fan pick-up time (seconds/10)

Determines a delay during which it is possible to compensate the different electrical characteristics of the fan drive motors:

Phase shift

Pa F03 = duration of fan phase shift expressed in microseconds*200 (1 unit = 200 microseconds).

Determines the duration of the TK output piloting impulse in microseconds*200 (1 unit = 200 microseconds).

Impulse duration

Pa F04= triak piloting impulse duration

### Fan control configuration

The fan control may be configured to supply a proportionate output (0-100%) or to function as “ON OFF” by setting the value of the parameter Pa F01:

Pa F01 = Selection of control output type

Fan configuration: selection of output type

| Pa F01 = 0 | proportionate fan output (from 0 to 100% depending on parameters) |
| --- | --- |
| Pa F01 = 1 | fan “on-off” output; in this mode the control performs the same calculations as in proportionate output, but if the outcome is greater than 0, the control output will be 100. |
| Pa F01 = 2 | on-off operation as called by compressor. In this mode output is 0 if no compressor is on in the circuit, or 100% if at least one compressor in the circuit is on |

If some of the relays are configured as condensation fan outputs (Pa H35- Pa H40 and  Pa N06- Pa N07=3 or 4), they will be on if the control output for each fan is greater than 0; otherwise, they will be off.

<IMG INFO>

36,6

24,2

1

2

70,85

-12,15

-1

## Reversing valves

The reversing valve is used only when operating in “heat pump” mode.

Reversing valve

“Energy 400” can control up to 2 reversing valves in a dual circuit system.

The reversing valve in circuit 1 is active only if:

- a relay (power output) is configured as reversing valve for circuit 1 (Pa H35-Pa H40 or Pa N06 and Pa N07= 1).

The reversing valve in circuit 2 is active only if:

- a relay (power output) is configured as reversing valve for circuit 2 (Pa H35-Pa H40 or Pa N06 and Pa N07= 2)

- there are 2 circuits

Both of them will be active only if

the heat pump is in operation (Pa H10=1 )

If the relay (power outputs) configured as inversion valve is one of RL1 - RL5, it is possible to invert the polarity using the parameters Pa H41 – Pa H44.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Hydraulic pump

The hydraulic pump is active only if at least one relay (power output) is configured as pump output (Pa H35-Pa H40 or Pa N06-Pa N07= 7 ) .

The pump may be configured to function independently of the compressor or whenever called up using parameter Pa P01:

Pa P01 = Pump operating mode

0=continuous operation

1=operation when called up by regulation algorithm

with a flow switch alarm (table of alarms) which is active with automatic reset, the pump will be on even if the compressis off.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

## Anti-freeze/supplementary electrical heaters

“Energy 400” can control up to 2 anti-freeze/supplementary electrical heaters.

The electrical heater output is active only if the relays (power outputs) are configured as electrical heaters 1 or 2 (Pa H35-Pa H40 or Pa N06-Pa N07= 5 or 6) .

If configured in this way, the outputs will command the electrical heater to come on or go off, depending on the parameters of configuration of electrical heaters Pa R01 … Pa R06, as described below:

configuration

| Parameter | Description | Value |  |
| --- | --- | --- | --- |
|  |  | 0 | 1 |
| Pa R01 | Defrost configuration | comes on only when requested by control | always on during defrost |
| Pa R02 | Cooling mode configuration | off during cooling | on during cooling (depending on anti-freeze electrical heater control) |
| Pa R03 | Heating mode configuration | off during heating | on during heating (depending on anti-freeze electrical heater control) |
| Pa R06 | OFF or STAND-BY configuration | off when OFF or on STAND-BY | Electrical heaters on when OFF or on STAND-BY |

Parameters r04 and r05 determine which probe the electrical heaters will control.

Each of the two electrical heaters may be set to any one of probes ST1, ST2 or ST5.

If the is absent or configured as a digital input, the electrical heaters will always be off.

Pa r04 configuration probe set to electrical heater 1

Pa r05 configuration probe set to electrical heater 2

probe configuration

| Value Parameters | Description |
| --- | --- |
| 0 | Electrical heater off |
| 1 | Set to ST1 |
| 2 | Set to ST2 |
| 3 | Set to ST5 |

## Internal fan

The fan output will be active only if one relay is configured as evaporator fan output.

The output is ON if at least one compressor is ON; otherwise it is off. During defrost the output is always off.

## Condensation-Defrost probes

“Energy 400” can control defrosting of one or more circuits depending on system configuration.

Defrost is enabled if:

- stated by the “Enable defrost” parameter (Pa d01 = 1)

- the condensation probe for circuit 1 is present (connected to analogue input ST3) and the relative parameter Pa H13 = 1 (in the case of an NTC probe) or Pa H13 = 2 (in the case of a 4-20mA probe) and ST4 = 1

- the reversing valve is present

In the case of a dual circuit system, defrost may be separate or combined (this will be the case of a system with a single condenser) depending on the setting of the parameter

Pa F22 : condensation type

separate or combined condensation

|  | 0 | 1 |
| --- | --- | --- |
| Pa F22: condensation type | Separate condensers | Combined condensation |

Defrost end and start depends on the values of the condensation probes, which may be configured as follows:

Let SCC1 be the condensation probe of circuit 1; it may be connected to analogue input ST3 or ST4;

depending on the type of probe, the configuration will be as shown in the table below:

probe configuration

|  | Probe connection |  |
| --- | --- | --- |
| Probe type | Probe connected to ST3 | Probe connected to ST4 |
| SCC1 NTC type | Pa H13 = 1 | Pa H14 = 1 |
| SCC1 4-20mA type | Pa H13 = 2 | - |

The following table applies to a dual circuit system:

|  | 1 circuit | 2 circuits, separate defrost | 2 circuits, combined defrost (*) |
| --- | --- | --- | --- |
| Defrost circuit 1 | SCC1 | SCC1 | MIN(SCC1;ST6) |
| Defrost circuit 2 | --- | ST6 | MIN(SCC1;ST6) |

(*) If A and B are control probes, MIN(A;B) represents

the smaller of A and B, if A and B are declared present.

It will be value A if B is not declared present.

It is impossible for A not to be declared present.

# Temperature control functions

x

Once ”Energy 400” has been configured, loads may be controlled on the basis of temperature and pressure conditions detected by probes and temperature control functions which may be defined using the appropriate parameters.

There are 4 possible operating modes:

Operating modes

- cooling

- heating

- stand-by

- off

Cooling: this is the “summer” operating mode; the machine is configured for cooling.

Cooling

Heating: this is the “winter” operating mode; the machine is configured for heating.

Heating

Stand-by: the machine does not govern any temperature control function; it continues to signal alarms

Stand-by

Off: machine is turned off.

Device off

The operating mode is determined by settings entered on the keyboard and by the following

Parameters:

Configuration parameter ST1  (Pa  H11) ( refer to Analogue inputs: configuration table)

Configuration parameter ST2  (Pa  H12) ( refer to Analogue inputs: configuration table)

Operating mode selection parameter (Pa  H49)

Heat pump parameter (Pa H10 )

Operating mode selection parameter (Pa  H49)

0= Selection from keyboard

1= Selection from digital input (refer to digital inputs)

Heat pump parameter (Pa H10)

0 = Heat pump not present

1 = Heat pump present

Combinations of these parameters will generate the following rules:

Operating modes: configuration table

| Operating mode | Mode selection parameter Pa H49 | Configuration parameter ST1 Pa H11 | Configuration parameter ST2 Pa H12 |
| --- | --- | --- | --- |
| Mode selection from keyboard | 0 | Other than 2 | Other than 2 |
| Mode selection from digital input. | 1 | Other than 2 | Other than 2 |
| If input ST1 is on, operating mode is heating; if not, stand-by | Any | 2 | Other than 2 |
| If input ST2 is on, operating mode is cooling; if not, stand-by | Any | Other than 2 | 2 |
| If input ST1 is on, operating mode is heating; if input ST2 is on, operating mode is cooling; if ST1 and ST2 are both on, there is a control error; if neither is on, operating mode is stand-by | Any | 2 | 2 |

## Setting set points

Unless the machine is configured as a motor condenser, loads will come on and go off dynamically depending on the temperature control functions set, the temperature/pressure values detected by the probes, and the set points that have been set:

There are two set point values:

Cooling Set point: this is the set point used as a reference when the device is in cooling mode

Heating Set point: this is the set point used as a reference when the device is in heating mode

The set points may be modified from the keyboard by accessing the “SET” submenu (refer to menu structure).

Their values must fall within a range determined by parameters Pa H02 – Pa H01 (Heating) and Pa H04 – Pa H03 (Cooling).

## Dynamic Set point

The regulation algorithm may be used to modify the set point automatically on the basis of outdoor conditions.

This modification is achieved by adding a positive or negative offset value to the set point, depending on:

- 4-20 mA analogue input (proportionate to a signal set by the user)

or

- temperature of outdoor probe

This function has two purposes: to save energy, or to operate the machine under particularly harsh outdoor temperature conditions.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

The dynamic set point is active if:

- Activation parameter Pa H50 = 1

- Probe ST3 (analogue inputs) is configured as a dynamic set point input (Pa H13 = 3) or probe ST4 (analogue inputs) is configured as an outdoor probe (Pa H14 = 3)

Parameters for control of the dynamic set point:

Control parameters

- Pa H51= max. offset during cooling.

- Pa H52= max. offset during heating

- Pa H53= Outdoor temperature set point during cooling

- Pa H54= Outdoor temperature set point during heating

- Pa H55= Delta of cooling temperature

- Pa H56= Delta of heating temperature

The interaction of these parameters is illustrated in the graphs below:

Positive Offset (H51>0 or  H52>0)

Modification depending on current input with positive offset

Offset

Set point

Current

20 mA

4 mA

Max

offset

Negative Offset (H51<0 or H52<0)

Modification depending on current input with negative offset

Current

20 mA

4 mA

Max

offset

Positive

Temp.

Delta <0

Outdoor temp. set point (H53 or H54)

Delta >0

Offset

Modification depending on outdoor temperature with positive offset

Negative Offset

Modification depending on outdoor temperature with negative offset

Temp.

Delta <0

Outdoor temp. set point. (H53 or H54)

Delta >0

## Load control

We will now look at how to set parameters for load control on the basis of temperature/pressure conditions detected by probes.

### Compressor control – regulation algorithm

The regulation algorithm calculates the load to be supplied through the compressors for both heating and cooling.

REGULATION ALGORITHM IN COOL MODE

Regulation algorithm in cool mode

If probe ST2 (analogue inputs) is not configured as a digital input for requests for cooling (Pa H11=2) or probe ST1(analogue inputs)  as a digital input for regulation algorithm requests (Pa H12=3), compressor management will depend on ambient temperature and a SET POINT.

ST1 = temperature of inflowing water or inlet air

SET COOL= cooling set point set from keyboard.

Pa C03 = hysteresis of cooling thermostat

Pa C05 = delta of power step intervention

Power

1st step

ST1

Pa C03

Pa C03

2nd step

Pa C05

Pa C05

Pa C05

Pa C03

Pa C03

3rd step

4th step

Cooling diagram

If Pa H011 = 3, the power step requested will depend on the status of input ST1 (analogue inputs).

If Pa H012 = 2, the power step requested will depend on the status of input ST2 (analogue inputs).

If probe ST5 (analogue inputs) is configured as a second step request (Pa H15 =2),  the second step (power step) will be requested on the basis of this input.  This function will be active only if either Pa H11=3 or Pa H12=2.

Only motor condensers may be controlled, up to 2 steps only.

REGULATION ALGORITHM IN HEAT MODE

Regulation algorithm in heat mode

If probe ST1(analogue inputs) is not configured as a digital input for requests for heat (Pa H05=2) or digital input for requests for regulation algorithm (Pa H05=3), compressor management will depend on

- temperature ST3 (analogue inputs), if configuration parameter ST3 = 5 (for water/water manual reversal machines)

- otherwise, temperature ST1(analogue inputs)

- a HEATING set point which may be set from the keyboard

ST1/ST3 =Temperature of inflowing water or inlet air

HEATING SET = Heating set point that has been set

Pa C04 = Heating thermostat hysteresis

Pa C05 = Delta of step intervention

Power

1st step

Pa C03

Pa C03

2nd step

Pa C05

Pa C05

Pa C03

Pa C03

3rd step

4th step

ST1/ST3

Heating diagram

If Pa H11 = 2-3, the compressors will be turned off and on depending on the status of input ST1.

If probe ST5 (analogue inputs) is configured as a second step request (Pa H15 =2),  the second step (power step) will be requested depending on this input. This function will be active only if Pa H11=2,3 or Pa H12=2.

DIFFERENTIAL TEMPERATURE CONTROL

Differential temperature control

This function may be used to control temperature according to both ST1(analogue inputs) and ST4 (analogue inputs). The function will be active

- if ST1 is configured as differential NTC input (Pa H11 = 4)

- if ST4 is configured as outdoor temperature input (Pa H14 = 3)

In this case, the controller will not control on the basis of ST1, but on the basis of the difference between ST1-ST4; if configuration parameter ST3  is equal to 5 (for water/water machines with manual reversal) in heating mode the controller will always control on the basis of ST3.

Differential temperature control can be used, for instance, to maintain a constant difference in temperature between the outdoor environment and a liquid being heated or cooled.

A compressor will always be off if:

It is not associated with a relay (power output)

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- The compressor has been shut down (refer to table of alarms)

- Safety timing is in progress

- The time lapse between pump on and compressor on is in progress (safety timing)

- Preventilation is in progress in cooling mode

- Energy 400 is in stand-by or off mode

- The parameter for configuration of probe ST1 Pa H11 = 0 (probe absent)

### Condensation fan control

Condensation control is dependent on the condensation temperature or pressure for the circuit.

Fan control will be on if:

- at least one probe per circuit is configured as a condensation probe (pressure or temperature); if not, the fan for the circuit will come ON and go OFF in response to the circuit compressors.

Fan control may be independent of the compressor, or it may be carried out in response to requests from compressors;

Operating mode is determined by parameter Pa F05:

|  | Value |  |
| --- | --- | --- |
|  | 0 | 1 |
| Pa F05: fan output mode | if all compressors in the circuit are off, the fan is off | condensation control is independent of the compressor |

The cut-off is bypassed for an amount of time equal to Pa F12 after the compressor is turned on. If the control requests cut-off during this time period, the fan will run at minimum speed.

If parameter Pa F05 is set to 1, condensation control will be dependent on condensation temperature or pressure, depending on how the following parameters are set:

CONDENSATION FAN CONTROL IN COOL MODE

Cool mode

Pa F06 = Minimum fan speed in COOL mode;

Pa F07 = Maximum silent fan speed in COOL mode

Pa F08 = Minimum fan speed temperature/pressure set point in COOL mode

Pa F09 = Fan prop. band in COOL mode

Pa F10 = Fan cut-off delta

Pa F11 = Cut-off hysteresis.

Pa F13 = Maximum fan speed in COOL mode

Pa F14 = Maximum fan speed temperature/pressure set point in COOL mode

An example of interaction of these parameters is shown in the figure below:

Fan control in cool mode: diagram

Fan control in cool mode

<IMG INFO>

282,8

222,2

0

2

70,9

14,15

-1

In cooling mode only, if Pa F05= 0 (if the compressor is turned off the fan is off), parameter Pa F21 (preventilation time for outdoor fan) is active.

Before turning on the compressors in the circuit the fan must be turned on for an amount of time equal to Pa F21; fan speed is proportionate to condensation temperature, but if the control requests cut-off during this time period the fan will run at the minimum speed setting.

This parameter prevents the compressor from starting up with a condensation temperature that is too high.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

CONDENSATION FAN CONTROL IN HEAT MODE

Heat mode

Pa F15 = Minimum fan speed in HEAT mode;

Pa F16 = Maximum silent fan speed in HEAT mode;

Pa F17 = Minimum fan speed temperature/pressure set point in HEAT mode;

Pa F18 = Fan prop. band in HEAT mode;

Pa F10 = Fan cut-off delta;

Pa F11 = Cut-off hysteresis;

Pa F19 = Maximum fan speed in HEAT mode;

Pa F20 = Maximum fan speed temperature/pressure set point in HEAT mode.

An example of interaction of these parameters is shown in the figure below:

Fan control in heat mode: diagram

Fan control in heat mode

<IMG INFO>

282,8

226,3

0

2

70,9

14,15

-1

If circuit is in defrost mode and the condensing pressure is less then (Pa F23-Pa F24), the fan is off, otherwise if the condensing pressure is greater then Pa F23 the fan is OFF.  During drip time, if Pa d07 <> 0 the fans run at maximunm speed for allowing fast battery water dispersion.

The cut-off is bypassed for an amount of time equal to Pa F12 after the compressor is turned on.

If the control requests cut-off during this time period, the fan will run at minimum speed.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

The fan will always be off if:

there is an alarm indicating that a condensation fan has shut down (refer to table of alarms).

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

Energy 400 is on stand-by or off.

### Combined or Separate Condensation

Parameter Pa F22 may be used to configure a dual circuit machine with a combined condenser.

|  | Value |  |
| --- | --- | --- |
|  | 0 | 1 |
| Pa F22: condensation type | separate condensers | combined condenser |

If Pa F22 = 0 the two fans are independent and are controlled by condensation pressure/temperature and the status of the compressors in the circuits.

If Pa F22= 1 the outputs of the 2 fans are in parallel and will be controlled as follows:

by the greater of the condensation probes in the circuits in cooling  mode

by the smaller of the condensation probes in the circuits in heating  mode

### Hydraulic pump control

If the pump is configured for continuous operation (Pa P01 = 0) it will stay on at all times; if not (Pa P01 = 1) it will be turned on in response to a request from the regulation algorithm.

Interaction between the pump, the compressors and the regulation algorithm status is determined by the following parameters:

- Pa P02: Delay between pump on and compressors on.

- Pa P03: Delay between regulation algorithm off and pump off.

An example is provided in the diagram below:

diagram

Temperature control algorithm

Compressor

ON

OFF

Pump

ON

OFF

Time

ON

OFF

Status

Compressor off – pump off delay Pa P03

Pump on – compressor on delay Pa P02

During a defrost, when the compressor is off, the pump will stay on.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

The pump will go off if:

There is a pump shut-down alarm, such as a flow switch alarm requiring manual reset (refer to table of alarms)

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- The instrument is on stand-by or off (it goes off after the delay determined by Pa P03)

### Anti-freeze/supplementary electrical heater control

Energy 400 can control 2 anti-freeze electrical heaters;

Each electrical heater is controlled with its own set point, which is different for heating and cooling modes, by means of the following parameters :

- Pa r07: set point of electrical heater 1 in heating mode

- Pa r08: set point of electrical heater 1 in cooling mode

- Pa r13: set point of electrical heater 2 in heating mode

- Pa r14: set point of electrical heater 2 in cooling mode

The two set points of the anti-freeze electrical heaters fall within a maximum and a minimum value which the user may set in the form of the following parameters:

- Pa r09: maximum set point for anti-freeze electrical heater

- Pa r10:  minimum set point for anti-freeze electrical heater

When off or on stand-by. control is based on the cooling set point and the control probe used in heating mode.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

Parameter Pa R11 determines hysteresis around the set points for the anti-freeze/supplementary electrical heaters.

An example of operation is shown in the diagram below

diagram

Diagram illustrating anti-freeze/supplementary electrical heaters control

Electric. Heater

ON

OFF

Temperature

Hysteresys

Set point

PARALLEL ELECTRICAL HEATERS

Parallel electrical heaters

Parameter r12 enables the parallel electrical heaters function..

This function is useful if the system incorporates 2 hydraulic circuits, each with its own anti-freeze probe, and there is only one anti-freeze electrical heater.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

The following conditions must apply for the function to be active:

- Pa r12 = 1

- Pa r05 other than 0

- Pa r06 other than 0.

Control is based on the minimum value detected by the 2 probes, using the set points of electrical heaters 1 (Pa r07 and Pa r08)

If Pa r15 = 1 and the system is in heating mode, electrical heater 1 will start up under the command of its own control or if ST1 <(SET HEATING-Pa r16-Pa C04) and will go off when ST1 >= (SET HEATING-Pa r16); heater 2  will start up if ST1 <(SET HEATING-Pa r17 – Pa C04) and will go off when ST1 >= (SET HEATING – Pa r17) . The control hysteresis is Pa C04 (heating control hysteresis).

Supplementary electrical heaters

### Reversing valve control

The reversing valves are turned off if Energy 400 is off or on stand-by;

The valves are ON in cooling mode and OFF in heating and defrost modes.

# Functions

x

## Recording hours of operation

The devices stores the number of hours of operation of the following in permanent memory:

- hydraulic pump

- compressors.

It is precise to within one minute.

Hours of operation may be displayed by entering the appropriate menu with the label Ohr (refer to menu structure).

The whole value is displayed if it is less than 999 hours; if it exceeds this value, the hundreds of hours will be shown and the decimal point will appear:

For example, 1234 hours will be displayed as follows:

<IMG INFO>

84,75

37,4

0

2

170,1

14,15

-1

To set the number of hours to zero, hold the DOWN key (refer to keys) down for two seconds while displaying the number of hours of operation.

MEMORY

35.48

MEMORY

35

Power failure

In the event of a power failure, the latest fraction of an hour recorded is set to 0, so that duration is rounded down:

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

## Defrost

The defrost function is active in heating mode only.

It is used to prevent ice formation on the surface of the external exchanger, which can occur in locations with low temperatures and high humidity and will considerably reduce the machine’s thermodynamic performance, creating a risk of damage to the machine.

Defrost start and end depends on the condensation probe values (refer to condensation probes–defrost) and the settings of the parameters listed below:

### Defrost start

The defrost starts as a result of three parameters:

- Pa d02  : temperature/pressure at which defrost starts

- Pa d03 : defrost interval

When the probe detects temperature/pressure values below the value of parameter Pa d02 it starts the timer, and when the number of minutes determined by parameter Pa d03 has expired the defrost will start;

Stopping timer

The timer will stop if:

- Temperature/pressure rises above the value of parameter Pa d02

- The compressor is turned off

The timer will be set to zero if:

Setting timer to zero

- a defrost cycle is completed

- “Energy 400” is turned off

- operating mode is changed (refer to operating modes)

- temperature rises above the value of parameter Pa d04 (defrost end temperature/pressure)

During the defrost the compressors are handled as follows:

Defrost: compressor management

- combined defrost: all compressors are turned on at full power;

- separate defrost: all compressors in the circuit being defrosted are turned on at full power;

there may be a delay between compressor coming on and Defrost start imposed by parameter Pa d11

Defrost will take place only if the following conditions are met: :

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- The safety timing of compressors in the circuit must be 0

- The delay between circuit defrosts must have expired since the last circuit defrost (Pa d08)

On a dual circuit machine with combined defrost, the following condition must apply:

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- in the circuit for which  defrost start is not requested, compressor safety time = 0 (refer to safety timing) so that the two circuits may both start a defrost at the same time.

If at the time of  defrost start the compressor-4-way valve delay time Pa d06 = 0, the compressor will stay on; if not, the adjustment shown in the diagram  below will be carried out.

diagram

<IMG INFO>

368

171,4

0

2

28,35

14,15

-1

### Control during defrost

During the defrost cycle loads are controlled as described below:

compressors in the circuit for which defrost is underway will be turned on to full power, if not already on at full power

Compressors

The reversing valve in the circuit for which defrost is underway will behave the way it does in the summer cycle.

Reversing valve

When the valve is reversed, a timer begins counting the minimum by-pass time for the circuit involved, equal to “minimum by-pass time during cooling” (Pa A01).

If the condensation pressure detected falls below (Pa F23 - Pa F24), the fan will be OFF; if it exceeds Pa F23, the fan will be ON. At the end of the drip stage, if parameter Pa D07 is not 0 the fans will operate at full speed for an amount of time equal to Pa F25 in order to remove water from the batteries as quickly as possible.

Fans

### Defrost end

Defrost end may be determined by temperature/pressure values read by analogue probes ST3, ST2, ST6 (analogue inputs) or by digital input (digital inputs).

The configuration parameters are:

- Pa d09 : Circuit 1 defrost end probe

- Pa d10: Circuit 2 defrost end probe

Parameter configuration

Possible values and meanings of these parameters are shown below:

| Value Parameters | Description |
| --- | --- |
| 0 | defrost end in response to digital input |
| 1 | defrost end in response to ST3 |
| 2 | defrost end in response to ST4 |
| 3 | defrost end in response to ST6 |

If Pa d09=0 (defrost end in response to digital input) the digital input configured as “End of defrost circuit 1” (digital inputs) will be taken into consideration; if Pa d10=0 input “circuit 2 defrost end”(digital inputs) .

In this configuration, as soon as the input becomes active the circuit will have a defrost end.

If an analogue input is selected for defrost end, the defrost will end will pressure/temperature rises above the value of parameter Pa d04 (defrost end temperature/pressure).

If the input is not configured, defrost will end only when pressure/temperature rises above the maximum duration set by parameter Pa d05

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

Defrost will always end if duration exceeds the maximum duration set by parameter Pa D05.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

After defrost end, if drip time Pa d07= 0 the compressors will stay on; if not, the adjustment shown in the figure below will take place:

Drip time

diagram

<IMG INFO>

368

166,5

0

2

28,35

14,15

-1

# Parameters

x

Parameters make the ”Energy 400” a fully configurable device.

They may be modified through:

- instrument keyboard

- Personal computer (with a suitable connection and “Param manager” software)

We will now take a detailed look at all the parameters, divided by category.

## Description of Parameters

CONFIGURATION PARAMETERS:

Determine the features of the machine.

If one or more of the parameters in this category are modified, the cotnroller must be switched off after the modification and switched on again to ensure correct operation.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Set point “cooling”

Pa G01

setpoint in “cooling” mode

Set point “heating”

Pa G02

setpoint in “heating” mode

Maximum set point during “heating”

Pa H01

Upper limit on set point in “heating” mode

Minimum set point during “heating”

Pa H02

Lower limit on set point in “heating” mode

Maximum set point during “cooling”

Pa H03

Upper limit on set point in “cooling” mode

Minimum set point during “cooling”

Pa H04

Lower limit on set point in “cooling” mode

Number of circuits on machine ()

Pa H05

Number of cooling circuits

0= not permitted

1= 1 cooling circuit

2= 2 cooling circuits

Number of compressors per circuit ()

Pa H06

0= no compressors

1= 1 compressor

2= 2 compressors

3= 3 compressors

4= 4 compressors

Number of capacity steps per compressor  ()

Pa H07

0= no capacity steps

1= 1 capacity step per compressor

2= 2 capacity steps per compressor

3= 3 capacity steps per compressor

Compressor on sequence

Pa H08

0= depending on hours of operation

1= unvaried on sequence

Compressor selection algorithm

Pa H09

0= circuit saturation

1= circuit balancing

Heat Pump Presence

Pa H10

0= Heat Pump not Present

1= Heat Pump Present

ST1 configuration

Pa H11

Used to configure analogue input ST1

0= No probe

1= Inflowing air/water analogue input

2= Heating request digital input

3= Regulation algorithm request digital input

4= NTC differential input

ST2 configuration

Pa H12

0= No probe

1= Circuit 1 outflowing water/antifreeze/inlet air analogue input

2= Cooling request digital input

ST3 configuration

Pa H13

0= No probe

1= Condensation control analogue input

2= 4...20 mA condensation input

3= 4...20 mA dynamic set point input

4= Antifreeze analogue input for water-water machines with gas reversal, circuit 1

5= Regulation algorithm input in “heating” mode for water-water machines with manual reversal

ST4 configuration

Pa H14

0= No probe

1= Condensation control analogue input

2= Multifunctional digital input

3= Outdoor temperature analogue input

ST5 configuration

Pa H15

0= No probe

1= Outflowing water/anti-freeze/inlet air analogue input, circuit 2

ST6 configuration

Pa H16

0= No probe

1= Condensation control analogue input

2= 4...20 mA condensation input

3= Not permitted

4= Antifreeze analogue input for water-water machines with gas reversal, circuit 2

Bottom of scale pressure value

Pa H17

Pressure value corresponding to an analogue input value (ST3 or ST6) on the 20mA input (if configured as a current input). Example:

if using a pressure transducer with limits of 0-30.0 bar/4-20mA, set PaH17=300

Polarity of digital inputs ID1,ID2,ID3,ID4

Pa H18

Polarity of digital inputs ID5,ID6,ID7,ID8

Pa H19

Polarity of digital inputs ID9,ID10,ID11,ST4

Pa H20

Polarity of digital inputs ID12,ID13,ID14,ID15

Pa H21

These parameters may be used to select the polarity which will activate the digital inputs to suit them to various operating requirements. Refer to Digital inputs: polarity when setting input polarity.

Configuration of digital input ID1

Pa H23

Configuration of digital input ID2

Pa H24

Configuration of digital input ID3

Pa H25

Configuration of digital input ID4

Pa H26

Configuration of digital input ID5

Pa H27

Configuration of digital input ID6

Pa H28

Configuration of digital input ID7

Pa H29

Configuration of digital input ID8

Pa H30

Configuration of digital input ID9

Pa H31

Configuration of digital input ID10

Pa H32

Configuration of digital input ID11

Pa H33

Configuration of digital input ST4 if configured as digital

Pa H34

| 0 | Input disabled | 12 | Low pressure circuit 1 |
| --- | --- | --- | --- |
| 1 | Flow switch | 13 | Low pressure circuit 2 |
| 2 | Remote OFF | 14 | High pressure compressor 1 |
| 3 | Remote Heat/Cool | 15 | High pressure compressor 2 |
| 4 | Thermal switch compressor 1 | 16 | High pressure compressor 3 |
| 5 | Thermal switch compressor 2 | 17 | High pressure compressor 4 |
| 6 | Thermal switch compressor 3 | 18 | Defrost end circuit 1 |
| 7 | Thermal switch compressor 4 | 19 | Defrost end circuit 2 |
| 8 | Thermal switch fan circuit 1 | 20 | Request for power step 2 |
| 9 | Thermal switch fan circuit 2 | 21 | Request for power step 3 |
| 10 | High pressure circuit 1 | 22 | Request for power step 4 |
| 11 | High pressure circuit 2 |  |  |

Configuration of output RL2

Pa H35

Configuration of output RL3

Pa H36

Configuration of output RL4

Pa H37

Configuration of output RL5

Pa H38

Configuration of output RL6

Pa H39

Configuration of output RL7

Pa H40

These parameters are used to assign various functions to relays as required by the type of application.

0= Not in use

1= Reversing valve circuit 1

2= Reversing valve circuit 2

3= Condensation fan circuit 1

4= Condensation fan circuit 2

5= Electrical heater 1

6= Electrical heater 2

7= Hydraulic pump

8= Evaporator fan

9= Power Step 2

10= Power Step 3

11= Power Step 4

Polarity of output RL2

Pa H41

Polarity of output RL3

Pa H42

Polarity of output RL4

Pa H43

Polarity of output RL5

Pa H44

Polarity of output alarm relay

Pa H45

Relay polarity may be set for the corresponding outputs.

0=relay on if output active

1=relay off if output not active

Configuration of analogue output 1 (AN1 or TK1)

Pa H46

Configuration of analogue output 2 (AN2 or TK2)

Pa H47

Condensation fan control outputs are available with 2 types of signal.

0= Signal for phase cut fan control

1= 4-20mA output

Not in use

Pa H48

Selection of operating mode

Pa H49

0= Selection from keyboard

1= Selection from digital input

Enable dynamic set point

Pa H50

If enabled, this function permits automatic variation of the working set point depending on outdoor temperature or on a 4-20mA analogue input. The parameter has no meaning if Pa H133 or Pa H143.

0= Function disabled

1= Function enabled

Maximum dynamic set point offset in cooling mode

Pa H51

The maximum value that may be added to the set point in cooling mode (COO) when the DYNAMIC SET POINT function is enabled.

Maximum dynamic set point offset in heating mode

Pa H52

The maximum value that may be added to the set point in heating mode (HEA) when the DYNAMIC SET POINT function is enabled.

Outdoor temperature set point in cooling mode

Pa H53

The parameter is significant only if the dynamic set point function is enabled and probe ST4 is configured as an outdoor temperature probe.

Outdoor temperature set point in heating mode

Pa H54

The parameter is significant only if the dynamic set point function is enabled and probe ST4 is configured as an outdoor temperature probe.

Outdoor temperature differential in cooling mode

Pa H55

The parameter is significant only if the dynamic set point function is enabled and probe ST4 is configured as an outdoor temperature probe.

Outdoor temperature differential in heating mode

Pa H56

The parameter is significant only if the set point function is enabled and probe ST4 is configured as an outdoor temperature probe.

Offset ST1,

Pa H57

Offset ST2,

Pa H58

Offset ST3

Pa H59

These parameters may be used to compensate the error that may occur between the temperature or pressure reading and the actual temperature or pressure.

Offset ST4

Pa H60

Offset ST5

Pa H61

These parameters may be used to compensate the error that may occur between the temperature reading and the actual temperature.

Offset ST6

Pa H62

This parameter may be used to compensate the error that may occur between the temperature (or pressure) reading and the actual temperture or pressure.

Mains frequency

Pa H63

Mains frequency 50 Hz

Mains frequency 60 Hz

Selection °C or °F

Pa H64

0= degrees °C

1= degrees °F

Family serial address,

Pa H65

Device serial address

Pa H66

These parameters may be used to address the device when connected to a personal computer or supervision system. Normally both are  0.

User password

Pa H67

May be used to enter a password for access to level two parameters, and to copy parameters from the instrument to the copy card.

Copy card write password

Pa H68

The password that must be entered to copy parameters to the copy card.

Presence of keyboard

Pa H68

ALARM PARAMETERS:

Low pressure pressure switch by-pass time.

Pa A01

Determines the delay between starting up the compressor and starting up the low pressure digital alarm diagnostics. Expressed in seconds.

Low pressure alarm events per hour

Pa A02

Used to set the number of low pressure digital alarm events per hour beyond which the system will switch from automatic reset to manual reset.

Bypass pump activation flow switch

Pa A03

Determines the delay between activation of the hydraulic pump and activation of the flow switch alarm diagnostics. Expressed in seconds.

Duration of active flow switch input

Pa A04

May be used to set the amount of time for which the flow switch digital input must remain active to generate a flow switch alarm. The timer starts after the flow switch by-pass time. Expressed in seconds.

Duration of inactive flow switch input

Pa A05

May be used to set the time for which the flow switch digital input must remain inactive to be included in the corresponding alarm. Expressed in seconds.

Number of flow switch alarms/hour

Pa A06

May be used to set the number of flow switch digital alarms per hour after which the alarm is switched from automatic to manual reset. When this occurs, the hydraulic pump is deactivated.

By-pass compressor thermal switch following compressor on

Pa A07

Determines the delay between compressor activation and activation of the compressor thermal switch digital diagnostics alarm. Expressed in seconds.

Compressor thermal switch alarm events per hour

Pa A08

May be used to set a number of compressor thermal switch alarm events per hour beyond which the alarm is switched from automatic to manual reset.

Number of fan thermal switch events per hour

Pa A09

May be used to set a number of fan thermal events per hour beyond which the alarm is switched from automatic to manual reset.

Anti-freeze alarm by-pass

Pa A10

Determines the delay between turning on the machine (selection of an operating mode or switch from OFF->ON) and activation of the compressor thermal switch digital alarm diagnostics. Expressed in seconds. Active only in heating mode.

Anti-freeze alarm set point

Pa A11

May be used to set the temperature below which the anti-freeze alarm is triggered.

Anti-freeze alarm hysteresis

Pa A12

May be used to set the differential value of the anti-freeze alarm.

Anti-freeze alarm events per hour

Pa A13

May be used to set a number of anti-freeze alarm events per hour beyond which the alarm is switched from automatic to manual reset.

Analogue input high pressure/temperature activation set point

Pa A14

May be used to set a condensation pressure/temperature value beyond which the high pressure alarm will be triggered.

Analogue input high pressure/temperature hysteresis

Pa A15

May be used to set the differential for the analogue high pressure alarm.

Analogue input high pressure/temperature activation bypass

Pa A16

Determines the delay after turning on of the first compressor in the cooling circuit and activation of the corresponding analogue input low pressure/temperature analogue alarm diagnostics. Expressed in seconds.

Analogue input low pressure/temperature activation set point

Pa A17

May be used to set a temperature/pressure value below which the low pressure alarm will be triggered.

Analogue input low pressure/temperature hysteresis

Pa A18

May be used to set the differential for the analogue low pressure/temperature alarm.

Number of analogue input low pressure alarm events per hour

Pa A19

May be used to set a number of low pressure analogue alarm events per hour beyond which the alarm will be switched from automatic to manual reset.

Machine out of coolant differential

Pa A20

If the difference between the absolute value of the set point and of the control probe exceeds this parameter, the machine out of coolant timer will start.

Bypass machine out of coolant

Pa A21

Determines the delay between the turning on of the first compressor in the corresponding cooling circuit and activation of the machine out of coolant alarm diagnostics. Expressed in minutes.

Duration of machine out of coolant

Pa A22

Determines the duration of the condition described under parameter Pa A20 beyond which the machine out of coolant alarm will be triggered.

Machine out of coolant alarm triggered

Pa A23

Enables machine out of coolant alarm diagnostics

0= diagnostics disabled

1= diagnostics enabled

Enable low pressure alarm during defrosting

Pa A24

Enables the minimum alarm during defrosting.

0= Low pressure alarm diagnostics disabled during defrosting

1= Low pressure alarm diagnostics enabled during defrosting

Input over-temperature set point

Pa A25

Temperature value ST1 above which the high temperature alarm E46 is triggered.

Input over-temperature duration

Pa A26

Determines the duration of the condition described for parameter Pa A25 beyond which the input over-temperature alarm is triggered.

COMPRESSOR PARAMETERS

OFF-ON safety time

Pa C01

The minimum amount of time that must pass between turning off the compressor and turning it on again. Expressed in tens of seconds.

ON-ON safety time

Pa C02

The minimum amount of time that must pass between turning the compressor on and turning it on again. Expressed in tens of seconds.

Hysteresis regulation algorithm during cooling

Pa C03

May be used to select intervention differential in cooling mode.

Hysteresis regulation algorithm during heating

Pa C04

May be used to select intervention differential in heating mode.

Regulation algorithm step intervention differential

Pa C05

May be used to set a temperature differential in relation to the set point beyond which the second step is activated.

Compressor on interval

Pa C06

May be used to set a delay between turning on of two compressors.

Compressor off interval

Pa C07

May be used to set a delay between turning off of two compressors.

Capacity step on interval

Pa C08

May be used to set a delay between turning on of compressor and of capacity steps.

FAN CONTROL PARAMETERS:

Fan output configuration

Pa F01

0 = proportional fan output (from 0 to 100% depending on parameters)

1 = fan output “on-off”; in this mode the regulation algorithm performs the same calculation as in proportional fan output, but if the result is greater than 0, regulation algorithmoutput will be 100.

2 = on-off operation in response to request from compressor. In this mode output is 0 if no compressor in the circuit is on, or 100% if at least one compressor in the circuit is on.

Fan pick-up time

Pa F02

Time for which fan runs at maximum speed after starting up. Expressed in seconds/10.

Fan phase shift

Pa F03

This parameter may be used to calibrate fan control output in proportion to the type of fan in use, adjusting it to suit the fan’s typical current/voltage phase shift.

Impulse duration of triac on

Pa F04

May be used to vary the length of the impulse from the triac command.

Functioning in resposne to compressor request

Pa F05

0= if compressor is off, fan is off

1= condensation control independent of compressor

Minimum speed during cooling

Pa F06

Minimum value of proportional fan control during cooling. Expressed as a percentage of the power supply voltage, from 0 to 100%,.

Maximum silent speed during cooling

Pa F07

Maximum value of proportional fan control during cooling. Expressed as a percentage of the power supply voltage, from 0 to 100%,.

Minimum fan speed temperature/pressure set point during cooling

Pa F08

Condensation pressure/temperature value below which the fan runs at minimum cooling speed.

Proportional band during cooling

Pa F09

Temperature/pressure differential corresponding to change from minimum to silent maximum fan speed during cooling (Pa F07).

Fan cut-off differential

Pa F10

Condensation temperature/pressure differential in relation to temperature/pressure set point (Pa F08 or pa F14) beyond which fan is cut off.

Cut-off hysteresis.

Pa F11

Condensation temperature/pressure differential for cut-off.

Cut-off bypass time

Pa F12

Determines the amount of time after fan start-up during which fan cut-off is excluded. Expressed in seconds.

Maximum speed during cooling

Pa F13

May be used to set a speed step corresponding to a given temperature/pressure value in cooling mode.

Maximum fan speed temperature/pressure during cooling

Pa F14

Condensation pressure/temperature value corresponding to the fan speed set for par. Pa F13.

Minimum speed during heating

Pa F15

Minimum proportional fan control value in heating mode. Expressed as a percentage of the power supply voltage, from 0 to 100%,.

Maximum silent speed during heating

Pa F16

Maximum value of proportional fan control during heating. Expressed as a percentage of the power supply voltage, from 0 to 100%,.

Minimum fan speed temperature/pressure set point during heating

Pa F17

Condensation temperature/pressure value above which the fan operates at minimum heating speed.

Proportional band during heating

Pa F18

Temperature/pressure differential corresponding to a change from minimum to maximum silent fan speed during heating (Pa F16).

Maximum speed during heating

Pa F19

May be used to set a speed step corresponding to a given temperature/pressure value during heating.

Maximum fan speed temperature/pressure set point during heating

Pa F20

Condensation temperature/pressure value corresponding to the fan speed set for Pa F19.

Preventilation in cooling mode

Pa F21

May be used to set a preventilation time in cooling mode before compressor on.

Combined or separate fan control

Pa F22

Parameter F22 may be used to configure dual circuit machines with a single condenser.

Parameter F22 condensation type

0= separate condensers

1= combined condenser.

If Pa F22 = 0 the fans are independent and depend on condensation pressure/temperature and the status of the compressors in the circuits. If Pa F22= 1 the outputs of the 2 fans are parallel and they are controlled:

on the basis of the greater of the two circuit condensation probes in cooling mode

on the basis of the smaller of the two circuit condensation probes in heating mode

If there is no condensation probe in one of the 2 circuits, a configuration alarm will be generated.

Fan activation temperature/pressure set point during defrosting

Pa F23

During defrosting, if temperature/pressure exceeds the “fan activation during defrosting” threshold (Pa F23) the fans will come on at full power.

Fan activation hysteresis during defrosting

Pa F24

Condensation temperature/pressure differential for fan control during defrosting.

Fan running time after defrost end

Pa F25

It’s the time the fans go on running after defrost time in order to quickly disperse the water in the battery.

PUMP PARAMETERS

Pump operating mode

Pa P01

May be used to determine pump operating mode:

0=continuous operation

1=operation in response to a request from the regulation algorithm

Delay between pump ON and compressor ON

Pa P02

May be used to set a delay between starting a pump and starting a compressor, expressed in seconds.

Delay between compressor OFF and pump OFF

Pa P03

May be used to set a delay between turning off a compressor and turning off a pump, expressed in seconds.

ANTI-FREEZE/BOILER PARAMETERS

Configuration of electrical heaters in defrost mode

Pa r01

Determines electrical heater operation during defrosting

0=come on only in response to a request from the regulation algorithm

1=always on during defrosting

Configuration of electrical heaters on in cooling mode

Pa r02

Determines electrical heater operation in cooling mode

0=off during cooling

1=on during cooling (in response to anti-freeze electrical heater regulation algorithm)

Configuration of electrical heaters on in heating mode

Pa r03

Determines electrical heater operation  in heating mode

0=off during heating

1= on during cooling (in response to anti-freeze electrical heater regulation algorithm)

Configuration of electrical heater 1 control probe

Pa r04

Configuration of electrical heater 2 control probe

Pa r05

Determines the control probes belonging to electrical heaters in heating mode

0= Not present

1=Control probe ST1

2=Control probe ST2

3= Control probe ST5

Configuration of electrical heaters when OFF or on stand-by

Pa r06

Determines the status of electrical heaters when the instrument is OFF or on stand-by

0=Always off when OFF or on stand-by

1=On when OFF or on stand-by (in response to anti-freeze electrical heater control algorithm)

Set point of anti-freeze electrial heater 1 in heating mode

Pa r07

Temperature value below which anti-freeze electrical heater 1 comes on in heating mode.

Set point of anti-freeze electrical heater 1 in cooling mode

Pa r08

Temperature value below which anti-freeze electrical heater 1 comes on in cooling mode.

Maximum set point of anti-freeze electrical heaters

Pa r09

Determines the maximum setting of the anti-freeze electrical heater set points.

Minimum set point of anti-freeze electrical heaters

Pa r10

Determines the minimumsetting of the anti-freeze electrcial heater set points.

Anti-freeze heater hysteresis

Pa r11

Anti-freeze electrical heater control algorithm hysteresis.

Set point of external anti-freeze electrical heaters

Pa r12

Temperature below which anti-freeze electrical heaters in the secondary circuit come on in gas-inversion machine.

Set point of electrical heater 2 in heating mode

Pa r13

Temperature below which anti-freeze electrical heaters 2 come on in heating mode.

Set point of electrical heater 2 in cooling mode

Pa r14

Temperature below which anti-freeze electrical heaters 2 come on in cooling mode.

Enable supplementary electrical heaters

Pa r15

DEFROST PARAMETERS::

Defrost enabled

Pa d01

0= defrost function disabled

1= defrost function enabled

Defrost start temperature / pressure

Pa d02

Temperature/pressure below which the defrost cycle is started.

Defrost interval (response time)

Pa d03

Duration for which probe remains below defrost start temperature/pressure, expressed in minutes.

Defrost end temperature/pressure

Pa d04

Temperature/pressure above which defrost ends.

Maximum defrost time (time-out)

Pa d05

Maximum duration of defrost in minutes.

Compressor-reversing valve wait time (anti-bleeding)

Pa d06

Wait time between compressor going off and reversal of the 4-way valve at the beginning of the defrost cycle.

Drip time

Pa d07

Wait time at the end of the defrost cycle between the compressor going off and the reversal of the 4-way valve.

Delay between defrosting of circuits.

Pa d08

Wait time between defrost end and next defrost start (independent by defrosting circuit)

Output probe defrost circuit 1

Pa d09

See table below

Output probe defrost circuit 2

Pa d10

See table below

| Parameters value | Description |
| --- | --- |
| 0 | Defrost output on digital input |
| 1 | Defrost output on ST3 |
| 2 | Defrost output on ST4 |
| 3 | Defrost output on ST6 |

Delay between defrost start and compressors on.

Pa d11

It is the only  safety time which regulates both  compressors and capacity steps.

## Parameters table

All ”Energy 400” parameters are listed in the table below.

Configuration parameters

| CONFIGURATION PARAMETERS * |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of meas. |
| Pa G01 | Set Point “Cooling” |  |  |  |
| Pa G02 | Set Point “Heating” |  |  |  |
| Pa H01 | Maximum set point during heating |  | Pa H02 ¸ 90.0 | °C |
| Pa H02 | Minimum set point during heating |  | -40.0 ¸ Pa H01 | °C |
| Pa H03 | Maximum set point during cooling |  | Pa H04 ¸ 90.0 | °C |
| Pa H04 | Minimum set point during cooling |  | -40.0 ¸ Pa H03 | °C |
| Pa H05 | Number of circuits on machine |  | 0 ¸ 2 | Num |
| Pa H06 | Number of compressors per circuit |  | 0 ¸ 4 | Num |
| Pa H07 | Number of capacity steps per compressor |  | 0 ¸ 3 | Num |
| Pa H08 | Compressors on sequence |  | 0¸1 | Flag |
| Pa H09 | Circuit balancing |  | 0¸1 | Flag |
| Pa H10 | Heat Pump presence |  | 0 ¸ 1 | Flag |
| Pa H11 | Configuration ST1 |  | 0 ¸ 4 | Num |
| Pa H12 | Configuration ST2 |  | 0 ¸ 2 | Num |
| Pa H13 | Configuration ST3 |  | 0 ¸ 5 | Num |
| Pa H14 | Configuration ST4 |  | 0 ¸ 3 | Num |
| Pa H15 | Configuration ST5 |  | 0 ¸ 1 | Num |
| Pa H16 | Configuration ST6 |  | 0 ¸ 4 | Num |
| Pa H17 | Bottom of scale pressure value |  | 0-350 | KPa*10 |
| Pa H18 | Polarity ID1 ID2 ID3 ID4 |  | 0 ¸ 15 | Num |
| Pa H19 | Polarity ID5 ID6 ID7 ID8 |  | 0 ¸ 15 | Num |
| Pa H20 | Polarity ID9 ID10 ID11 ST4 |  | 0 ¸ 15 | Num |
| Pa H21 | Polarity ST1 |  | 0 ¸ 1 | Flag |
| Pa H22 | Polarity ST2 |  | 0 ¸ 1 | Flag |
| Pa H23 | Configuration ID1 |  | 0 ¸ 22 | Num |
| Pa H24 | Configuration ID2 |  | 0 ¸ 22 | Num |
| Pa H25 | Configuration ID3 |  | 0 ¸ 22 | Num |
| Pa H26 | Configuration ID4 |  | 0 ¸ 22 | Num |
| Pa H27 | Configuration ID5 |  | 0 ¸ 22 | Num |
| Pa H28 | Configuration ID6 |  | 0 ¸ 22 | Num |
| Pa H29 | Configuration ID7 |  | 0 ¸ 22 | Num |
| Pa H30 | Configuration ID8 |  | 0 ¸ 22 | Num |
| Pa H31 | Configuration ID9 |  | 0 ¸ 22 | Num |
| Pa H32 | Configuration ID10 |  | 0 ¸ 22 | Num |
| Pa H33 | Configuration ID11 |  | 0 ¸ 22 | Num |
| Pa H34 | Configuration ST4 if digital input |  | 0 ¸ 22 | Num |
| Pa H35 | Configuration relay 2 |  | 0 ¸ 11 | Num |
| Pa H36 | Configuration relay 3 |  | 0 ¸ 11 | Num |
| Pa H37 | Configuration relay 4 |  | 0 ¸ 11 | Num |
| Pa H38 | Configuration relay 5 |  | 0 ¸ 11 | Num |
| Pa H39 | Configuration relay 6 |  | 0 ¸ 11 | Num |
| Pa H40 | Configuration relay 7 |  | 0 ¸ 11 | Num |
| Pa H41 | Polarity RL2 |  | 0 ¸ 1 | Flag |
| Pa H42 | Polarity RL3 |  | 0 ¸ 1 | Flag |
| Pa H43 | Polarity RL4 |  | 0 ¸ 1 | Flag |
| Pa H44 | Polarity RL5 |  | 0 ¸ 1 | Flag |
| Pa H45 | Alarm relay polarity |  | 0 ¸ 1 | Flag |
| Pa H46 | Configuration fan 1 output |  | 0 ¸ 1 | Flag |
| Pa H47 | Configuration fan 2 output |  | 0 ¸ 1 | Flag |
| Pa H48 | Free |  | 0 ¸ 1 | Flag |
| Pa H49 | Selection of operating mode |  | 0 ¸ 1 | Flag |
| Pa H50 | Enable dynamic set point |  | 0 ¸ 1 | Flag |
| Pa H51 | Offset of dynamic set point during cooling |  | -50.0 ¸ 80.0 | °C |
| Pa H52 | Offset of dynamic set point during heating |  | -50.0 ¸ 80.0 | °C |
| Pa H53 | Dynamic outdoor temp. set point during cooling |  | -127 ¸ 127 | °C |
| Pa H54 | Dynamic outdoor temp. set point during heating |  | -127 ¸ 127 | °C |
| Pa H55 | Delta dynamic outdoor temp. set point during cooling |  | -50.0 ¸ 80.0 | °C |
| Pa H56 | Delta dynamic outdoor temp. set point during heating |  | -50.0 ¸ 80.0 | °C |
| Pa H57 | Offset ST1 |  | -12.7 ¸ 12.7 | °C |
| Pa H58 | Offset ST2 |  | -12.7 ¸ 12.7 | °C |
| Pa H59 | Offset ST3 |  | -127 ¸ 127 | °C/10-Kpa*10 |
| Pa H60 | Offset ST4 |  | -12.7 ¸ 12.7 | °C |
| Pa H61 | Offset ST5 |  | -12.7 ¸ 12.7 | °C |
| Pa H62 | Offset ST6 |  | -127 ¸ 127 | °C/10-Kpa*10 |
| Pa H63 | 0=50 Hz 1=60 Hz |  | 0 ¸ 1 | Flag |
| Pa H64 | 0= °C 1=°F |  | 0 ¸ 1 | Flag |
| Pa H65 | Family serial address |  | 0 ¸ 14 | Num. |
| Pa H66 | Device serial address |  | 0 ¸ 14 | Num. |
| Pa H67 | User password |  | 0 ¸ 255 | Num. |
| Pa H68 | Copy card password |  | 0 ¸ 255 | Num. |
| Pa H69 | Keyboard Presence |  | 0/1 | Flag |

*	If parameters in this category are modified, the controller must be turned off and on again to ensure correct functioning.

Alarm parameters

| ALARM PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa A01 | Low pressure switch bypass time after compressor on |  | 0 ¸ 255 | Seconds |
| Pa A02 | Low pressure alarm events per hour |  | 0 ¸ 255 | Num |
| Pa A03 | Flow switch bypass time after pump on |  | 0 ¸ 255 | Seconds |
| Pa A04 | Duration of active flow switch input |  | 0 ¸ 255 | Seconds |
| Pa A05 | Duration of inactive flow switch input |  | 0 ¸ 255 | Seconds |
| Pa A06 | Number of flow switch alarm events per hour |  | 0 ¸ 255 | Num |
| Pa A07 | Bypass compressor thermal switch from compressor on |  | 0 ¸ 255 | Seconds |
| Pa A08 | Number of compressors 1 + 2 thermal switch alarms/hour |  | 0 ¸ 255 | Num |
| Pa A09 | Number of fan thermal switch alarm events/hour |  | 0 ¸ 255 | Num |
| Pa A10 | Anti-freeze alarm bypass after ON-OFF |  | 0 ¸ 255 | Minutes |
| Pa A11 | Anti-freeze alarm activation set point |  | -127 ¸ 127 | °C |
| Pa A12 | Hysteresis of anti-freeze alarm |  | 0 ¸ 25.5 | °C |
| Pa A13 | Anti-freeze alarm events/hour |  | 0 ¸ 255 | Num |
| Pa A14 | Analogue input high pressure/temperature activation set point |  | 0 ¸ 900 | °C/10 – Kpa*10 |
| Pa A15 | Analogue input high pressure hysteresis |  | 0 ¸ 255 | °C/10 – Kpa*10 |
| Pa A16 | Analogue input low pressure activation bypass |  | 0 ¸ 255 | Seconds |
| Pa A17 | Analogue input low pressure activation set point |  | -500 ¸ 800 | °C/10 – Kpa*10 |
| Pa A18 | Analogue input low pressure hysteresis |  | 0 ¸ 255 | °C/10 – Kpa*10 |
| Pa A19 | Analogue input low pressure alarm events per hour |  | 0 ¸ 255 | Num |
| Pa A20 | Machine out of coolant differential |  | 0 ¸ 255 | °C |
| Pa A21 | Machine out of coolant bypass |  | 0 ¸ 255 | Minutes |
| Pa A22 | Machine out of coolant duration |  | 0 ¸ 255 | Minutes |
| Pa A23 | Machine out of coolant alarm triggered |  | 0 ¸ 1 | Flag |
| Pa A24 | Enable low pressure alarm during defrost |  | 0 ¸ 1 | Flag |
| Pa A25 | Input over-temperature set point |  | 0 ¸ 255 | °C |
| Pa A26 | Input over-temperature duration |  | 0 ¸ 255 | S*10 |

Compressor parameters

| COMPRESSOR PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa C01 | ON-OFF safety time |  | 0 ¸ 255 | Seconds*10 |
| Pa C02 | ON-ON safety time |  | 0 ¸ 255 | Seconds*10 |
| Pa C03 | Hysteresis regulation algorithm during cooling |  | 0 ¸ 25.5 | °C |
| Pa C04 | Hysteresis regulation algorithm during heating |  | 0 ¸ 25.5 | °C |
| Pa C05 | Regulation algorithm step intervention delta |  | 0 ¸ 25.5 | °C |
| Pa C06 | Compressor – compressor on interval |  | 0 ¸ 255 | Seconds |
| Pa C07 | Compressor – compressor off interval |  | 0 ¸ 255 | Seconds |
| Pa C08 | Capacity step on interval |  | 0 ¸ 255 | Seconds |

Fan control parameters

| FAN CONTROL PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa F01 | Fan output mode |  | 0 ¸ 2 | Num. |
| Pa F02 | Fan pick-up time |  | 0 ¸ 255 | Seconds/10 |
| Pa F03 | Fan phase shift |  | 0 ¸ 100 | Seconds*200 |
| Pa F04 | Impulse duration of triak on |  | 0 ¸ 255 | Seconds*200 |
| Pa F05 | Functioning in response to compressor request |  | 0 ¸ 1 | Flag |
| Pa F06 | Minimum speed during cooling |  | 0 ¸ 100 | % |
| Pa F07 | Maximum silent speed during cooling |  | 0 ¸ 100 | % |
| Pa F08 | Minimum fan speed temperature/pressure set point during cooling |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa F09 | Prop. band during cooling |  | 0 ¸ 255 | °C/10 - Kpa*10 |
| Pa F10 | Delta cut-off |  | 0 ¸ 255 | °C/10 - Kpa*10 |
| Pa F11 | Cut-off hysteresis. |  | 0 ¸ 255 | °C/10 - Kpa*10 |
| Pa F12 | Bypass time cut-off |  | 0 ¸ 255 | Seconds |
| Pa F13 | Max speed during cooling |  | 0 ¸ 100 | % |
| Pa F14 | Maximum fan speed temperature/pressure set point during cooling |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa F15 | Minimum speed during heating |  | 0 ¸ 100 | % |
| Pa F16 | Maximum silent speed during heating |  | 0 ¸ 100 | % |
| Pa F17 | Minimum fan speed temperature/pressure set point during heating |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa F18 | Prop. band during heating |  | 0 ¸ 255 | °C/10 - Kpa*10 |
| Pa F19 | Maximum fan speed during heating |  | 0 ¸ 100 | % |
| Pa F20 | Maximum fan speed temperature/pressure set point during heating |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa F21 | Preventilation in cooling mode |  | 0 ¸ 255 | Seconds |
| Pa F22 | Combined or separate fan control |  | 0 ¸ 1 | Flag |
| Pa F23 | Fan activation temperature/pressure set point during defrosting |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa F24 | Fan activation hysteresis during defrosting |  | 0 ¸ 255 | °C/10 - Kpa*10 |
| Pa F25 | Fan running time after defrost end |  | 0 ¸ 255 | Seconds |

Pump parameters

| PUMP PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa P01 | Pump operating mode |  | 0 ¸ 1 | Flag |
| Pa P02 | Delay between pump ON and compressor ON |  | 0 ¸ 255 | Seconds |
| Pa P03 | Delay between compressor OFF and pump OFF |  | 0 ¸ 255 | Seconds |

Electrical heater parameters

| ELECTRICAL HEATER PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa r01 | Configuration of electrical heaters in defrost mode |  | 0 ¸ 1 | Flag |
| Pa r02 | Configuration of electrical heaters on in cooling mode |  | 0 ¸ 1 | Flag |
| Pa r03 | Configuration of electrical heaters on in heating mode |  | 0 ¸ 1 | Flag |
| Pa r04 | Configuration of electrical heater 1 control probe |  | 0 ¸ 3 | Num |
| Pa r05 | Configuration of electrical heater 2 control probe |  | 0 ¸ 3 | Num |
| Pa r06 | Configuration of electrical heaters when OFF or on STAND-BY |  | 0 ¸ 1 | Flag |
| Pa r07 | Set point of electrical heater 1 in heating mode |  | Pa 10 ¸ Pa 09 | °C |
| Pa r08 | Set point of electrical heater 1 in cooling mode |  | Pa 10 ¸ Pa 09 | °C |
| Pa r09 | Max. set point electrical heaters |  | Pa 10 ¸ 127 | °C |
| Pa r10 | Min. set point electrical heaters |  | -127 ¸ Pa 09 | °C |
| Pa r11 | hysteresis of anti-freeze heaters |  | 0 ¸ 25.5 | °C |
| Pa R12 | Set point of external anti-freeze electrical heaters |  | Pa 10 ¸ Pa 09 | °C |
| Pa r13 | Set point of electrical heater 2 in heating mode |  | Pa 10 ¸ Pa 09 | °C |
| Pa r14 | Set point of electrical heater 2 in cooling mode |  | Pa 10 ¸ Pa 09 | °C |
| Pa r15 | Enable supplementary electrical heaters |  | 0 ¸ 1 | Flag |
| Pa r16 | Delta of activation of supplementary heater 1 |  | 0 ¸ 25.5 | °C |
| Pa r17 | Delta of activation of supplementary heater 2 |  | 0 ¸ 25.5 | °C |

Defrost parameters

| DEFROST PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa d01 | Defrost enabled |  | 0 ¸ 1 | Flag |
| Pa d02 | Defrost start temperature/pressure |  | -500 ¸ 800 | °C/10 - Kpa*10 |
| Pa d03 | Defrost interval |  | 0 ¸ 255 | Minutes |
| Pa d04 | Defrost end temperature/pressure |  | -500 ¸ 800 | °C/10 – Kpa*10 |
| Pa d05 | Maximum defrost time |  | 0 ¸ 255 | Minutes |
| Pa d06 | Compressor-reversing valve wait time |  | 0 ¸ 255 | Seconds |
| Pa d07 | Drip time |  | 0 ¸ 255 | Seconds |
| Pa d08 | Delay between defrosting of circuits |  | 0 ¸ 255 | Seconds * 10 |
| Pa d09 | Output probe defrost circuit 1 |  | 0 ¸ 3 | Num |
| Pa d10 | Output probe defrost circuit 2 |  | 0 ¸ 3 | Num |
| Pa d11 | Delay in compressors on in defrost mode |  | 0 ¸ 255 | Seconds |

Extension parameters

| EXTENSION PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa N01 | Polarity of ID12 ID13 ID14 ID15 |  | 0 ¸ 5 | Flag |
| Pa N02 | Configuration ID12 |  | 0 ¸ 22 | Num |
| Pa N03 | Configuration ID13 |  | 0 ¸ 22 | Num |
| Pa N04 | Configuration ID14 |  | 0 ¸ 22 | Num |
| Pa N05 | Configuration ID15 |  | 0 ¸ 22 | Num |
| Pa N06 | Configuration relay 9 |  | 0 ¸ 11 | Num |
| Pa N07 | Configuration relay 10 |  | 0 ¸ 11 | Num |

# Diagnostics

x

“Energy 400” can perform full systems diagnostics and signal a series of alarms.

Alarms

Alarm trigger and reset modes are set using parameters Pa A01 – Pa A26.

For some alarms the signal will not be given for a certain amount of time, determined by a parameter.

For some alarms the number of alarm events is counted; if the number of alarm events in the past hour exceeds a certain threshold set by a parameter, the alarm will switch from automatic to manual reset.

Alarm events per hour

Alarms are sampled every 226 seconds;

Example: if the number of events/hour is set to 3, the duration of an alarm must fall between 2*226 seconds and 3*226 seconds for the alarm to be switched from automatic to manual reset.

Time

225 s

225 s

225 s

225 s

1

2

3

Counter

Alarm

Automatic reset

Manual reset

Alarm sampling

If an alarm is triggered more than once within one sampling period (226 seconds), only one alarm will be counted.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

Alarms with manual reset are reset by pressing the ON-OFF button and releasing

Manual reset shuts down corresponding loads and requires an operator to intervene (reset the alarm using the ON-OFF control).

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

Manual reset alarms are used mainly to identify problems which could result in damage to the system

## List of alarms

When an alarm is triggered, two things occur:

- The corresponding loads are shut down

- The alarm appears on the keyboard display

The alarm message consists of a code with the format “Enn” (where nn is a 2-digit number identifying the type of alarm, such as: E00, E25, E39….).

All possible alarms are listed in the table below, along with their codes and the corresponding loads that will be shut down:

Tabella Allarmi

| CODE | MESSAGE | DESCRIPTION | LOADS SHUT DOWN |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | COMP.1 | COMP.2 | COMP.3 | COMP.4 | FAN1 | FAN2 | PUMP | RES.1 | RES.2 |
| E00 | Remote off | - All loads will be shut down; - Triggered by the digital input configured as “Remote OFF” (refer to digital inputs) | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E01 | High pressure circuit 1 | - Compressors in circuit 1 will be shut down; - Triggered by the digital input configured as “High pressure circuit 1” (refer to digital inputs) | YES | YES1 | YES1 | YES1 |  |  |  |  |  |
| E02 | Low pressure circuit 1 | - Compressors in circuit 1 will be shut down; also condenser fans if condensation is separate for the 2 circuits (refer to combined or separate condensation); - Triggered by the digital input configured as “Low pressure circuit 1” (refer to digital inputs); - Automatically reset unless alarm events per hour reaches the value of parameter Pa A02, after which manually reset; - Inactive during timer Pa A01 after compressor on or reversal of 4-way valve (reversing valve) in circuit 1 | YES | YES1 | YES1 | YES1 | YES4 |  |  |  |  |
| E03 | Thermal switch protection compressor 1 | - Compressor 1 will be shut down; - Triggered by the digital input configured as “Thermal switch compressor 1” (refer to digital inputs); - Automatically reset until alarm events per hour reaches the value of parameter Pa A07, after which manually reset; - Inactive during timer Pa A08 after compressor on. | YES |  |  |  |  |  |  |  |  |
| E04 | Thermal switch protection condenser fan circuit 1 | - Fans and compressors in circuit 1 will be shut down; if the 2 circuits are set up for combined condensation, (refer to combined or separate condensation) compressors in circuit 2 will also be shut down; - Triggered by the digital input configured as “Thermal switch fan circuit 1” (refer to digital inputs); - Automatically reset until alarm events per hour reaches the value of parameter Pa A09, after which manually reset; | YES | YES1 | YES1 - YES2 | YES1 - YES2 | YES | YES2 |  |  |  |
| E05 | Anti-freeze circuit 1 | - Fans and compressors in circuit 1 will be shut down; - Active if analogue probe ST2 (refer to analogue inputs) is configured as anti-freeze probe (Pa H12 = 1); - Triggered when probe ST2 detects a value lower than Pa A11; - Turned off if probe ST2 detects a value greater than Pa A11 + Pa A12; - Automatically reset until alarm events per hour reaches the value of parameter Pa A13,after which manually reset; - Inactive during timer Pa A10 after Energy 400 is turned on with the On-OFF key (refer to keyboard) or from the digital input ON-OFF (refer to digital inputs) or when heating mode is started. | YES | YES | YES | YES1 | YES | YES |  |  |  |
| E06 | Probe ST2 fault | - All loads will be shut down; - Triggered if probe ST2, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E07 | Probe ST3 fault | - All loads will be shut down; - Triggered if probe ST3, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E09 | High pressure compressor 1 | - Compressor 1 will be shut down; - Triggered by the digital input configured as “High pressure compressor 1” (refer to digital inputs); - Always manually reset | YES |  |  |  |  |  |  |  |  |
| E11 | High pressure circuit 1 on analog input | - Compressors in circuit 1 will be shut down; - Active if analog probe ST3 or ST4 (refer to analog inputs) is configured as pressure probe; - Active when the pressure probe (ST3/ST4) detects a value greater then Pa A14; - Inactive if the probe detects a value lower then Pa A14 – Pa A15; | YES | YES1 | YES1 | YES1 |  |  |  |  |  |
| E12 | Low pressure circuit 1 on analog input | - Compressors in circuit 1 will be shut down, as well as condenser fans if the 2 circuits have separate condensation (refer to combined or separate condensation); - Active if the analog probe ST6 (refer to analog inputs) is configured as pressure probe; - Active when the pressure probe ST6 detects a value lower then Pa A17; - Inactive if the probe detects a value greater then Pa A17 – Pa A18; - Automatically reset until alarm events per hour reaches the value of parameter Pa A19, after which manually reset; - Inactive during timer Pa A16 after compressor on or reversal of 4-way valve (reversing valve) of circuit 1 | YES | YES1 | YES1 | YES1 | YES4 |  |  |  |  |
| E13 | Thermal switch protection compressor 2 | - Compressor 2 will be shut down; - Triggered by the digital input configured as “Thermal switch compressor 2” (refer to digital inputs); - Automatically reset until alarm events per hour reach the value of parameter Pa A07, after which manually reset; - Inactive during timer Pa A08 after compressor is turned on. |  | YES |  |  |  |  |  |  |  |
| E19 | High pressure compressor 2 | - Compressor 2 will be shut down; - Triggered by the digital input configured as “High pressure compressor 1” (refer to digital inputs); - Always manually reset |  | YES |  |  |  |  |  |  |  |
| E21 | High pressure circuit 2 | - Compressors in circuit 2 will be shut down; - Triggered by the digital input configured as “High pressure circuit 2” (refer to digital inputs) |  |  | YES5 | YES5 |  |  |  |  |  |
| E22 | Low pressure circuit 2 | - Compressors in circuit 2 will be shut down, as well as condenser fans if the 2 circuits have separate condensation (refer to combined or separate condensation); - Triggered by the digital input configured as “Low pressure circuit 2” (refer to digital inputs); - Automatically reset until alarm events per hour reaches the value of parameter Pa A02, after which manually reset; - Inactive during timer Pa A01 after compressor on or reversal of 4-way valve (reversing valve) of circuit 1 |  |  | YES | YES |  | YES4 |  |  |  |
| E23 | Thermal switch protection compressor 3 | - Compressor 3 will be shut down; - Triggered by the digital input configured as “Thermal switch compressor 3” (refer to digital inputs); - Automatically reset until alarm events per hour reach value of parameter Pa A07, after which manually reset; - Inactive during timer Pa A08 after compressor on. |  |  | YES |  |  |  |  |  |  |
| E24 | Thermal switch protection condenser fan circuit 2 | - Fans and compressors in circuit 2 will be shut down; if the 2 circuits have combined condensation (refer to combined or separate condensation) the compressors in circuit 1 will also be shut down; - Triggered by the digital input configured as “Thermal switch circuit 2 fan” (refer to digital inputs); - Automatically reset until alarm events per hour reaches value of parameter Pa A09, after which manually reset; | YES2 | YES2 | YES | YES | YES2 | YES |  |  |  |
| E25 | Anti-freeze circuit 2 | - Fans and compressors will be shut down; - Active if analogue probe ST5 (refer to analogue inputs) is configured as anti-freeze probe (Pa H15 = 1); - Triggered when probe ST5 detects a value below Pa A11; - Turns off when probe ST5 detects a value above Pa A11 + Pa A12; - Automatically reset until alarm events per hour reaches value of parameter Pa A13, after which manually reset; - Inactive during timer Pa A10 after turning on Energy 400 using On-OFF key (refer to keyboard) or digital input ON-OFF (refer to digital inputs) or start of heating mode. | YES | YES | YES | YES | YES | YES |  |  |  |
| E26 | Probe ST5 fault | - All loads will be shut down; - Triggered if probe ST5, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E27 | Probe ST6 fault | - All loads will be shut down; - Triggered if probe ST6, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E29 | High pressure compressor 3 | - Compressor 3 will be shut down; - Triggered by the digital input configured as “High pressure compressor 3” (refer to digital inputs); - Always manually reset |  |  | YES |  |  |  |  |  |  |
| E31 | High pressure circuit 2 on analog input | - Compressors in circuit 2 will be shut down; - Active if analog probe ST3/ST4 (refer to analog inputs) is configured as pressure probe; - Active when the pressure probe (ST3/ST4) detects a value greater then Pa A14; - Inactive if the probe detects a value lower then Pa A14 – Pa A15; |  |  | YES5 | YES5 |  |  |  |  |  |
| E32 | Low pressure circuit 2 on analog input | - Compressors in circuit 2 will be shut down, as well as condenser fans if the 2 circuits have separate condensation (refer to combined or separate condensation); - Active if the analog probe ST6 (refer to analog inputs) is configured as pressure probe; - Active when the pressure probe ST6 detects a value lower then Pa A17; - Inactive if the probe detects a value greater then Pa A17 – Pa A18; - Automatically reset until alarm events per hour reaches the value of parameter Pa A19, after which manually reset; - Inactive during timer Pa A16 after compressor on or reversal of 4-way valve (reversing valve) of circuit 2 |  |  | YES | YES |  | YES4 |  |  |  |
| E33 | Thermal switch protection compressor 4 | - Compressor 4 will be shut down; - Triggered by the digital input configured as “Thermal switch compressor 4” (refer to digital inputs); - Automatically reset until alarm events per hour reaches the value of parameter Pa A07, after which manually reset; - Inactive during timer Pa A08 after compressor on. |  |  |  | YES |  |  |  |  |  |
| E39 | High pressure compressor 4 | - Compressor 4 will be shut down; - Triggered by the digital input configured as “High pressure compressor 4” (refer to digital inputs); - Always manually reset |  |  |  | YES |  |  |  |  |  |
| E40 | Probe ST1 fault | - All loads will be shut down; - Triggered if probe ST1, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E41 | Flow switch | - All compressors, fans and pump will be cut off if manually reset; - Triggered if the digital input configured as “Flow switch” (refer to digital inputs) remains active for an amount of time equal to Pa A04; - Goes off if the digital input configured as “Flow switch” (refer to digital inputs) remains inactive for an amount of time equal to Pa A05; - Automatically reset until alarm events per hour reaches the value of parameter Pa A06 , after which manually reset; - Inactive during timer Pa A03 following pump on. | YES | YES | YES | YES | YES | YES | YES3 |  |  |
| E42 | Probe ST4 fault | - All loads will be shut down; - Triggered if probe ST4, configured as an analogue input, shorts, is cut off, or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E43 | Anti-freeze external circuit 1,2 | - Fans and compressors will be shut down; - Active if analogue probe ST6 and/or ST3 (refer to analogue inputs) is configured as external anti-freeze probe (Pa H13 = 4, Pa H16=4); - Triggered when probe ST3 and/or ST6 detects a value below Pa A11; - Turns off when probe ST3 and/or ST6 detects a value above Pa A11 + Pa A12; - Automatically reset until alarm events per hour reaches value of parameter Pa A13, after which manually reset; - Inactive during timer Pa A10 after turning on Energy 400 using On-OFF key (refer to keyboard) or digital input ON-OFF (refer to digital inputs) or start of heating mode. | YES | YES | YES | YES | YES | YES |  |  |  |
| E44 | Machine out of coolant | - In all working modes, except if the boiler is active and during defrost, the machine is checked to identify circuit failures. For example: gas flooding, broken inversion valve in heat pump machines, compressor power phases exchange. - The regulator is active if Pa A23=1 and ST2 is configured as water output probe. An alarm arises if one of the following conditions lasts for a minimum time of Pa A22: - ST2-ST1(or ST3)<Pa A20 in heat pump configuration, - ST1(or ST3)-ST2<Pa A20 in cooling configuration. - The gas flooding alarm always needs a manual reset. - Time count resets with each mode change or if all the compressors are off. After a compressor start, the alarm is ignored for a time of Pa A21. | YES | YES | YES | YES | YES | YES |  |  |  |
| E45 | Configuration error | - All loads will be shut down; - Triggered if at least one of the following conditions apply: - H11= 2 (ST1 configured as request for heating), H12= 2 (ST2 configured as request for cooling) and both inputs are active. - Sum of compressors and capacity steps on machine exceeds 4 - The keyboard is declared present (Pa H69=1) and there is no communication between the keyboard and the basic unit. | YES | YES | YES | YES | YES | YES | YES | YES | YES |
| E46 | High temperature regulation algorithm | - All loads will be shut down except the pump; - Triggered if probe ST1 (refer to analogue inputs) has a value exceeding Pa A25 for an amount of time exceeding Pa 26 in cooling mode; - Goes off if probe ST1 (refer to analogue inputs) has a value lower than Pa A25 – Pa A12; - Automatically reset. | YES | YES | YES | YES | YES | YES |  | YES | YES |

1 If it belongs to circuit 1

2 If combined condensation system

3 Only if manual reset

4 With separate ventilation

5 If it belongs to circuit 2

outputs defined as capacity steps will go off if there is an alarm for the compressor to which they belong

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

The tables below list alarms by type (digital or analogue).

TABLE OF DIGITAL ALARMS:

Digital alarms

| Alarm name | Bypass trigger event | Bypass time | Trigger duration | Deactivation duration | N. alarm events/hour |
| --- | --- | --- | --- | --- | --- |
| Compressor 1,2,3,4 high pressure alarm | None | absent | absent | absent | Manual reset |
| High pressure circuit alarm | None | absent | absent | absent | Manual reset |
| Low pressure alarm | A compressor coming on in the circuit or reversal of 4-way valve | Pa A01 | absent | absent | Pa A02 |
| Flow switch alarm | Pump coming on | Pa A03 | Pa A04 | Pa A05 | Pa A06 |
| Compressor 1,2,3,4 thermal switch alarm | Compressor coming on | Pa A07 | absent | absent | Pa A08 |
| Fan 1,2 thermal switch alarm | None | absent | absent | absent | Pa A09 |

TABLE OF ANALOGUE ALARMS:

Analogue alarms

| Alarm name | Event | Bypass time | Trigger set point | Hysteresis | N. alarm events/hour | Regulation probe |
| --- | --- | --- | --- | --- | --- | --- |
| Anti-freeze alarm circuit 1 | On Off, input in heating mode, remote on off | Pa A10 | Pa A11 | Pa A12 positive | Pa A13 | ST2 if configuration parameter Pa H12 = 1, otherwise alarm is inactive |
| Anti-freeze alarm circuit 2 | On Off, input in heating mode, remote on off | Pa A10 | Pa A11 | Pa A12 positive | Pa A13 | ST5 if configuration parameter Pa H15 = 1, otherwise alarm is inactive |
| External anti-freeze alarm circuit 1/2 | On Off, input in heating mode, remote on off | Pa A10 | Pa A11 | Pa A12 positive | Pa A13 | ST3/ST6 if configuration parameter Pa H13/H16 = 4, otherwise alarm is inactive |
| Low pressure /low temperature condensation alarm circuit 1 | Compressor turned on or reversal of 4-way valve | Par A16 | Pa A17 | Pa A18 positive | Pa A19 | ST3 se Pa H13=1 or 2 or else ST4 if Pa H14 = 1, otherwise alarm is inactive |
| Low pressure /low temperature condensation alarm circuit 2 | Compressor turned on or reversal of 4-3way valve | Par A16 | Pa A17 | Pa A18 positive | Pa A19 | ST6 if Pa H16=1, otherwise alarm is inactive |
| High pressure /high temperature condensation alarm circuit 1 | None | absent | Pa A14 | Pa A15 negative | Manual reset | ST3 if Pa H13=1 or 2, or ST4 if Pa H14 = 1; otherwise alarm is inactive |
| High pressure /high temperature condensation alarm circuit 2 | None | absent | Pa A14 | Pa A15 negative | Manual reset | ST6 if Pa H16=1 or 2, otherwise alarm is inactive |
| High temperature regulation algorithm alarm | None | absent | Pa A25 | Pa A12 negative | Automatic reset | ST1 |

# Technical features

x

## Technical data

|  | Typical | Min. | Max. |
| --- | --- | --- | --- |
| Power supply voltage | 12V~ | 10V~ | 14V~ |
| Power supply frequency | 50Hz/60Hz | --- | --- |
| Power | 5VA | --- | --- |
| Insulation class | 1 | --- | --- |
| Protection grade | Front panel IP0 | --- | --- |
| Operating temperature | 25°C | 0°C | 60°C |
| Operating humidity (non-condensing) | 30% | 10% | 90% |
| Storage temperature | 25°C | -20°C | 85°C |
| Storage humidity (non-condensing) | 30% | 10% | 90% |

## Electromechanical features

| 110/230 V digital outputs | n 8 5 A resistive relays; ¼ hp 230VAC; 1/8 hp 125VAC (on base module) the total amout of relays current must be lower than 10A n 2 5 A resistive relays; ¼ hp 230VAC; 1/8 hp 125VAC (on expansion module) |
| --- | --- |
| Analogue outputs | n° 2 triac piloting outputs or configurable 4-20 mA outputs |
| Analogue inputs | n 4 NTC R25 10K n° 2 configurable input or 4-20mA o r NTC R25 10K |
| Digital inputs | N 11 voltage-free digital inputs (on base module) N° 4 voltage-free digital inputs (on expansion module) |
| Terminals and connectors | N 1 10-way high voltage connectors, step 7.5 N 2 16-way rapid clamp connectors for low voltage, step 4.2, AWG 16-28 N 1 p2.5 5–way connector for remote control and programming with external copy card, AWG 24-30 n 1 20-way connector for connection of expansion n 1 3-way screw terminal for remote keyboard |
| Serial ports | n° 1 9600 serial port n° 1 2400 serial port |

The instrument must be powered with a suitable current transformer with the following features:

current transformer

- Primary voltage:		230V~±10%; 110V~±10%

- Secondary voltage:		12V~

- Power supply frequency:		50Hz; 60Hz

- Power:			11VA;

## Regulations

The product complies with the following European Community Directives:

- Council Directive 73/23/CEE and subsequent modifications

- Council directive 89/336/CEE and subsequent modifications

and complies with the following harmonised regulations:

- LOW VOLTAGE: EN60335 as far as applicable

- EMISSION: EN50081-1 (EN55022)

- IMMUNITY: EN50082-1 (IEC 1000-4-2/3/4/5)

# Use of the device

x

## Permitted use

This product is used to control single and dual circuit chillers and heat pumps.

To ensure safety, the controller must be installed and operated in accordance with the instructions supplied, and access to high voltage components must be prevented under regular operating conditions. The device shall be properly protected against water and dust and shall be accessible by using a tool only. The device is suitable for incorporation in a household appliance and/or similar air conditioning device.

According to the reference regulations, it is classified:

- In terms of construction, as an automatic electronic control device to be incorporated with independent assembly or integrated;

- In terms of automatic operating features, as a type 1 action control device, with reference to manufacturing tolerances and drifts;

- As a class 2 device in relation to protection against electrical shock;

- As a class A device in relation to software structure and class.

## Forbidden use

Any use other than the permitted use is forbidden.

Please note that relay contacts supplied are functional and are subject to fault (in that they are controlled by an electronic component and be shorted or remain open); protection devices recommended by product standards or suggested by common sense in response to evident safety requirements shall be implemented outside of the instrument.

# Responsibility and residual risks

x

Microtech shall not be held liable for any damage incurred as a result of:

- installation/use other than those intended, and, in particular, failure to comply with the safety instructions specified by applicable regulations and/or provided in this document;

- use with equipment which does not provide adequate protection against electric shocks, water and dust under the effective conditions of installation;

- use with equipment which permits access to hazardous parts without the use of tools;

- installation/use with equipment which does not comply with current regulations and legislation.

# Glossary

x

Multiple inputs with an OR relationship to one another are equivalent to a single input with the following status:

OR logico

- Active if at least one input is active

- Inactive if no input is active

To “Scroll up” a menu means listing the various parameters from the bottom up (Pa10 -> Pa 09 -> Pa 08 ….)

Scroll up

Indicates that the instrument is waiting, in stand-by mode; all functions are suspended.

Stand-by

Set to zero.

Reset

Resetting an alarm means reactivating it ready for a new signal.

Reset alarm

A manual reset alarm must be reset using the keyboard.

Manual reset

To “Scroll down” in a menu is to list parameters from the top down (Pa08 -> Pa 09 -> Pa 10 ….)

Scroll down

Means flashing; normally refers to leds

BLINK

Average number of hours is the ratio between the total number of hours for which the compressors are available and the number of compressors in the circuit

Average number of hours

Devices in the system, including compressors, fans, hydraulic pump, electrical anti-freeze heaters…

Loads

A reference value (set by the user) defining the system’s operating status, such as the thermostat that controls temperature in the home: if we want to maintain a temperature of 20 °C we set the set point to 20°C (the heating system will come on if the temperature in the house falls below 20°C, and go off if it exceeds this value).

Set Point

Values falling within a given interval; Range 1…100 indicates all values between 1 and 100

Range

A hysteresis is normally defined around a set point to prevent frequent oscillation of the change of status of the load being controlled;

Hysteresis

Example: suppose we have a set point of 20 °C on a probe for measurement of room temperature, above which a compressor will be started up;

When room temperature nears the set point (20 °C) there will be an unstable phase during which the relay which starts up the compressor will frequently switch from ON to OFF and vice versa, which could result in serious damage to the system.

To prevent this problem a hysteresis is defined: an interval of tolerance within which there will be no change in status; in our example, we could set a hysteresis of 1 °C, in which case the compressor would be started up at 21 °C (set point  + hysteresis) and turned off at 19 °C (set point – hysteresis)

Memory in which data is maintained even when the device is turned off (as distinct from temporary memory, the data in which is lost when the device is turned off.)

Permanent memory

Temperature/pressure below or above which proportional output is cut off.

Cut-off

# ANALITIC INDEX

A

Alarm events per hour	42

Alarm parameters	39

Alarms	42

Analogue alarms	48

Analogue inputs	10

configuration table	10

resolution and precision	10

Anti-freeze/supplementary electrical heater control	29

diagram	29

Anti-freeze/supplementary electrical heaters	21

configuration	21

probe configuration	22

Average number of hours	52

B

Basic Module	6; 7

Basic Module Dimension	9

BLINK	52

C

CF (Control Fan) Modules	6

Combination mode – onoff keys	13

Combined or Separate Condensation	28

Components	6

Compressor (or power step) on/off sequences	18

Compressor configuration	17

Simple compressors	17

with 1 capacity step	17

with 2 or 3 capacity steps	18

Compressor control – regulation algorithm	25

Cooling diagram	25

Heating diagram	26

Compressor parameters	40

Compressor timing	19

Off-on and on-on diagram for 1 compressor	20

Off-on timing	20

on-on and off-off diagram 2 comp	20

On-on off-off times for 2 comp.	20

On-on timing	20

Compressor timing:	20

Compressors	17

coming on on the basis of hours of operation and circuit balancing	19

coming on on the basis of hours of operation and circuit saturation	18

unvaried on sequence with circuit balancing	19

unvaried on sequence with circuit saturation	19

Condensation fan	20

Condensation fan control	26

Cool mode	26

Heat mode	27

Condensation-Defrost probes	22

probe configuration	22

separate or combined condensation	22

Configuration of analogue inputs	10

Configuration of digital inputs	11

Configuration of fan outputs	12

Configuration of outputs	12

Configuration parameters	38

Connection diagrams	7

Connections with NTC sensors	7

Connections with pressure sensor	8

Control during defrost	31

Compressors	31

Fans	31

Reversing valve	31

Cooling	23

Copy Card	6; 16

Cross references	5

current transformer	49

Cut-off	52

D

Defrost	30

compressor management	30

Defrost end	31

diagram	32

Parameter configuration	31

Defrost parameters	41

Defrost start	30

diagram	31

Setting timer to zero	30

Stopping timer	30

Description of Parameters	33

Device off	23

DIAGNOSTICS	42

Differential temperature control	26

Digital alarms	48

Digital inputs	11

Configuration Table	11

polarity	11

Polarity table	11

Dimensions	9

Display	13

Drip time	31

Dynamic Set point	23

Control parameters	24

Modification depending on current input with negative offset	24

Modification depending on current input with positive offset	24

Modification depending on outdoor temperature with negative offset	25

Modification depending on outdoor temperature with positive offset	24

E

Electrical heater parameters	41

Electromechanical features	49

Expansion	6

Expansion Connectors diagram	8

Expansion module dimension	9

Extension parameters	41

F

Fan configuration	20

selection of output type	21

Fan control configuration	21

Fan control in cool mode

diagram	27

Fan control in heat mode

diagram	27

Fan control parameters	40

Forbidden use	50

FUNCTIONS	30

G

GLOSSARY	52

H

Heating	23

HOW TO USE THIS MANUAL	5

Hydraulic pump	21

Hydraulic pump control	28

diagram	28

Hysteresis	52

I

Icons for emphasis	5

Impulse duration	21

INSTALLATION	7

Internal fan	22

INTRODUCTION	6

K

Keyboard	13

Keyboard connectors	9

Keyboards	6

Keys	13

Mode	13

L

label	16

Led	13

List of alarms	42

Load control	25

Loads	52

Low voltage outputs	12

M

Manual reset	52

Menu structure	15

O

On-off – Alarms reset	13

Operating modes	23

configuration table	23

OR logico	52

Outputs	12

P

Pa H10	33

Parallel electrical heaters	29

Param Manager	6

PARAMETERS	33

Parameters table	38

Permanent memory	52

Permitted use	50

Phase shift	21

Physical quantities and units of measurement	12

Pick-up	21

Power outputs	12

Configuration table	12

Polarity Table	12

Power step	17

Programming parameters – Menu levels	14

Pump parameters	41

R

Range	52

Recording hours of operation	30

References	5

Regulation algorithm in cool mode	25

Regulation algorithm in heat mode	25

Regulations	49

Remote keyboard	14

Reset	52

Reset alarm	52

RESPONSIBILITY AND RESIDUAL RISKS	51

Reversing valve	21

Reversing valve control	29

Reversing valves	21

S

Safety timing	19

Scroll down	52

Scroll up	52

selection	12

Serial Interface (EWTK)	6

Serial outputs	12

Set Point	52

Setting set points	23

Stand-by	23; 52

Supplementary electrical heaters	29

SYSTEM CONFIGURATION	17

T

Tabella Allarmi	43

Technical data	49

TECHNICAL FEATURES	49

TEMPERATURE CONTROL FUNCTIONS	23

U

Unit of measurement:	12

USE OF THE DEVICE	50

USER INTERFACE	13

V

Visibility of parameters and submenus	16

W

Wall-mounted keyboard	14

|  |  | ENERGY 400 2000/10 Cod: 8MA10102 |
| --- | --- | --- |

   non sono ammesse configurazioni macchina con numero di gradini superiore a 4