ENERGY 100

Electronic Control for mono Compressor CHILLERS

User Manual

# CONTENTS

1    Contents	3

2	How to use this manual	5

3	Introduction	6

3.1	Components	6

3.1.1	Basic module	6

3.1.2	Keyboards	6

3.1.3	Interface module	6

3.2	Copy Card	6

3.2.1	Fan modules	6

3.2.2	Param Manager	6

4	Installation	7

4.1	Connection diagrams	7

4.2	Configuration of analogue inputs	8

4.3	Configuration of digital inputs	8

4.4	Configuration of outputs	9

4.4.1	Relays	9

4.4.2	Triac	9

4.4.3	Fan module pilot output	9

4.4.4	Additional keyboard output	9

4.4.5	Serial outputs	9

4.4.6	Copy card device	10

4.5	Units of measurement	10

5	User Interface	11

5.1	Keys	11

5.2	Displays	11

5.2.1	Display	11

5.2.2	Led	11

5.3	Remote keyboard	12

5.4	Parameter programming – Menu levels	12

5.4.1	Visibility of parameters and sub-menus	14

6	System configuration	15

6.1	Compressor	15

6.1.1	Compressor timing	15

6.2	Condensation fan	15

6.2.1	Fan configuration	15

6.3	Reversing valve	16

6.4	Hydraulic pump	16

6.5	Internal anti-freeze/supplementary electrical heaters	16

6.6	External anti-freeze electrical heaters	16

6.7	Boiler	17

6.8	Internal fan	17

7	Temperature control functions	18

7.1	Selection of operating mode from analogue input	18

7.2	Setting set points	19

7.3	Dynamic set point	19

7.4	Switching from digital input	20

7.5	Load control	21

7.5.1	Compressor control – regulation algorithm	21

7.5.2	Condensation fan control	21

7.5.3	Reversing valve control	23

7.5.4	Hydraulic pump control	23

7.5.5	Anti-freeze/supplementary electrical heater control	23

7.5.6	External anti-freeze electrical heater control	24

7.5.7	Boiler control	24

7.5.8	Internal fan control	24

8	Functions	26

8.1	Recording hours of operation	26

8.2	Defrosting	26

8.2.1	Defrost start	26

8.2.2	Defrost end	27

8.2.3	Counter mode	27

8.3	Hot start function	27

8.4	Machine out of coolant signal	27

8.5	Power failure	28

9	Parameters	29

9.1	Description of parameters	29

9.1.1	Configuration parameters	29

9.1.2	Alarm parameters	30

9.1.3	Compressor parameters	31

9.1.4	Fan control parameters	31

9.1.5	Pump parameters	32

9.1.6	Anti-freeze/boiler parameters	32

9.1.7	Defrost parameters	33

9.2	Table of parameters	33

10	Diagnostics	36

10.1	List of alarms	36

11	Technical data	41

11.1	Technical data	41

11.2	Electromechanical features	41

11.3	Dimensions	41

11.4	Regulations	41

12	Use of the device	42

12.1	Permitted use	42

12.2	Forbidden use	42

13	Responsibility and residual risks	43

14	Glossary	44

# How to use this manual

x

x

This manual is designed to permit quick, easy reference with the following features:

References column:

References

A column to the left of the text contains references to subjects discussed in the text to help you locate the information you need quickly and easily.

Cross references:

Cross references:

All words written in italics are referenced in the subject index to help you find the page containing details on this subject;

supposing you read the following text:

”when the alarm is triggered, the compressors will be shut down”

The italics mean that you will find a reference to the page on the topic of compressors listed under the item compressors in the index.

If you are consulting the manual “on-line” (using a computer), words which appear in italics are hyperlinks: just click on a word in italics with the mouse to go directly to the part of the manual that discusses this topic.

Some segments of text are marked by icons appearing in the references column with the meanings specified below:

Icons for emphasis

Take note: 	information on the topic under discussion which the user ought to keep in mind

<IMG INFO>

28,3

19,75

1

2

79,35

-9,9

-1

Tip: 	a recommendation which may help the user to understand and make use of the information supplied on the topic under discussion

<IMG INFO>

28,3

29,25

1

2

79,35

-14,65

-1

Warning! : 	information which is essential for preventing negative consequences for the system or a hazard to personnel, instruments, data, etc., and which users MUST read with care.

<IMG INFO>

28,3

23,55

1

2

79,35

-11,75

-1

# Introduction

x

x

Energy 100 is a compact device that permits control of air conditioning units of the following types:

- air-air

- air-water

- water-water

- motor-condensing

with a single circuito and 1 compressor.

It is possible to control condensation fan speed proportionately for currents of up to 2 A without using external devices.

Main characteristics:

- Temperature control on outflowing water probes.

- Condensation control

- Input may be configured for an NTC temperature probe or for a 4...20 mA signal (through parameters)

- Automatic change-over

- Boiler or supplementary electrical heater control for heating

- Internal fan control up to 3 steps in the air-air application

- Dynamic set point

- Parameter setting from the keyboard or through a personal computer

- Copy card for uploading and downloading parameter maps

- Remote keyboard (up to 100 m) which may be connected up directly without a serial interface

- 4-20 mA or 0-10 V output (optional internal card)

- User interface with a menu featuring 2 different levels of access through password management

- Interface menu may be fully configured from a PC.

## Components

We will now look at the basic components and accessories in the system and how they are connected.

### Basic module

The basic module is an electronic board, to be connected up as illustrated in the connection diagrams.

### Keyboards

Two types of keyboard are available:

- Panel keyboard

- Wall-mounted keyboard

- Interface module

### Interface module

A device which permits the controller to interface with a Personal Computer

It must be connected up as illustrated in the figure:

<IMG INFO>

339,85

117,45

0

2

42,55

14,15

-1

The PC must be connected with the interface module, and the interface module with the device, with no power on to any of the devices, and in compliance with current safety regulations. It is important to avoid electrostatic shocks, especially on exposed metal parts of the devices. Check that electrostatic charges are permitted to flow to earth.

<IMG INFO>

31,1

25,65

1

2

76,55

-12,8

-1

## Copy Card

A device which may be used to upload and download the Energy 100 parameter map.

### Fan modules

May be used to connect fans to Energy 100’s low voltage outputs.

### Param Manager

If you have an adequate Personal Computer with Windows 95 or a more recent operating system, the Param Manager software, and adequate interface module and proper wiring, you can have full control over all Energy 100 parameters via Personal Computer.

The instrument can be programmed easily and quickly using a series of interfaces which permit a logical, guided approach.

# Installation

x

<IMG INFO>

31,1

25,65

1

2

76,55

-12,8

-1

Before proceeding with any operation, first make sure that you have connected up the power supply to the device through an appropriate external current transformer. Always follow these rules when connecting boards to one another and to the application: Do not apply loads in excess of those specified herein to outputs;

<IMG INFO>

31

25

1

2

76

-12

-1

When connecting up loads, carefully observe the connection diagrams; wire low voltage loads separately from high voltage loads;

## Connection diagrams

REVERSING VALVE RELAY

12 AC

ST1

ID1

GND

ALL

GND

ST4

ST3

ST2

ID2

12 AC

12 DC

TK1

ID5

ID4

ID3

CF CONTROL

EMI

FILTER

Line

FAN  TRIAC

COMPRESSOR RELAY

PUMP RELAY

ELECTRICAL HEATERS RELAY

ALARM OUTPUT

Connection with ST3 probe configured as NTC

REVERSING VALVE RELAY

12 AC

ST1

ID1

GND

ALL

GND

ST4

ST3

ST2

ID2

12 AC

12 DC

TK1

ID5

ID4

ID3

CF CONTROL

EMI

FILTER

Line

FAN  TRIAC

COMPRESSOR RELAY

PUMP RELAY

ELECTRICAL HEATERS RELAY

ALARM OUTPUT

Connection with ST3 probe configured as 4-20 mA input

IInstrument configuration is determined by the values of the parameters associated with inputs and outputs.

## Configuration of analogue inputs

There are 4 analogue inputs:

Analogue inputs

- 3 NTC type temperature probes

- 1 input which may be configured for an NTC probe or a 4...20 mA signal.

The inputs, which shall henceforth be referred to as ST1…ST4, are configured as shown in the table below:

Analogue inputs: configuration table

| Pa. | Description | Value |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0 | 1 | 2 | 3 | 4 | 5 |
| Pa H05 | Configuration of analogue input ST1 | Probe absent | NTC input Inflowing water/air | Request for heating digital input | Request for regulation algorithm digital input6 | Not permitted | Not permitted |
| Pa H06 | Configuration of analogue input ST2 | Probe absent | NTC input Outflowing water/air, anti-freeze | Request for cooling digital input | Not permitted | Not permitted | Not permitted |
| Pa H07 | Configuration of analogue input ST3 | Probe absent | NTC input Condensation | 4...20 mA input for condensation | 4...20 mA input for dynamic set point | NTC input Anti-freeze for water-water machines with automatic (internal) reversing of coolant gas | NTC probe Regulation alogorithm in heating mode for water-water machines with manual reversal on water side |
| Pa H08 | Configuration of analogue input ST4 | Probe absent | NTC input Condensation | Multifunctional digital input | NTC input Outdoor temperature | Not permitted | Not permitted |

If input ST3 is defined as a 4...20 mA input, the scale bottom value of the pressure input is also significant: Pa H09, maximum input value; set the corresponding value to a current of 20 mA

## Configuration of digital inputs

There are 5 digital inputs, which will henceforth be identified as ID1…ID5.

Digital inputs

ST1, ST2 and ST4 may be added to these if they are configured as digital inputs (through parameters Pa H05, Pa H06, and Pa H08).

A total of 8 digital inputs is thus available.

The polarity of digital inputs is determined by the parameters listed below:

Digtial inputs: polarity

| Parameter | Description | Value |  |
| --- | --- | --- | --- |
|  |  | 0 | 1 |
| Pa H10 | Polarity of digital input ID1 | Active if closed | Active if open |
| Pa H11 | Polarity of digital input ID2 | Active if closed | Active if open |
| Pa H12 | Polarity of digital input ID3 | Active if closed | Active if open |
| Pa H13 | Polarity of digital input ID4 | Active if closed | Active if open |
| Pa H14 | Polarity of digital input ID5 | Active if closed | Active if open |
| Pa H15 | Polarity of input ST1 (configured as digital) | Active if closed | Active if open |
| Pa H16 | Polarity of input ST2 (configured as digital) | Active if closed | Active if open |
| Pa H17 | Polarity of input ST4 (configured as digital) | Active if closed | Active if open |

ID1 : High pressure input

ID2 : Low pressure input

The functions of the other inputs may be configured using parameters:

ST1, ST2: (Refer to Analogue inputs: configuration table)

ID3, ID4, ID5 and ST4: as shown in the table below

Digtial inputs: configuration table

| Digital input configuration parameter | Parameter code | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 0 | 1 | 2 | 3 | 4 |
| Configuration parameter ID3 | Pa H18 | Thermal switch - compressor | Thermal switch - fan | Flow switch | Remote heat cool | Remote On-off |
| Configuration parameter ID4 | Pa H19 | Thermal switch - compressor | Thermal switch - fan | Flow switch | Remote heat cool | Remote On-off |
| Configuration parameter ID5 | Pa H20 | Thermal switch - compressor | Thermal switch - fan | Flow switch | Remote heat cool | Remote On-off |
| Configuration parameter ST4 | Pa H21 | Thermal switch - compressor | Thermal switch - fan | Flow switch | Remote heat cool | Remote On-off |

If more than one of the parameters appearing in table 3 is configured with the same value, the function will be called up in response to at least one of the inputs.

## Configuration of outputs

The instrument has the following outputs:

Outputs

- 4 relay contacts

- triac outputs

- 1 keyboard output

- Fan module pilot output

### Relays

- RL1 - compressor, 2 A 115VAC/230VAC

- RL2 - configurable, 2 A 115VAC/230VAC

- RL3 - configurable, 2 A 115VAC/230VAC

- RL4 - configurable, 2 A 115VAC/230VAC

Outputs RL2, RL3, and RL4 may be configured as shown in the table below:

Relays: configuration table

| Pa. | Description | Value |  |  |
| --- | --- | --- | --- | --- |
|  |  | 0 | 1 | 2 |
| Pa H22 | Configuration of relay RL2 | Pump | Internal fan speed 3 1 | Not permitted |
| Pa H23 | Configuration of relay RL3 | Reversing valve | Internal fan speed 3 3 | Not permitted |
| Pa H24 | Configuration of relay RL4 | Anti-freeze electrical heaters | Internal fan speed 3 2 | Boiler |

If multiple outputs are configured to run the same resource, the outputs will be activated in parallel.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

### Triac

- TK – Control of condensation fan or supplementary anti-freeze heaters, maximum current 2 A 250V~

The TK  output may be configured as shown below:

TK output: configuration table

| Pa. | Description | Value |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 0 | 1 | 2 | 3 |
| Pa F01 | Configuration of TK output | Proportional condensation fan control | ON-OFF temperature fan control | Anti-freeze electrical heaters for water-water machine with gas reversal | On-off in response to request from compressor |

- ALL - 12-24 V~ output for alarm, maximum current  500 mA.

The power supply to the alarm output must be kept separate from the controller power supply.

<IMG INFO>

33,9

27,7

1

2

73,7

-13,85

-1

### Fan module pilot output

- TK TTL – Low voltage output piloting external fan control modules.

### Additional keyboard output

The keyboard output may be used for an additional keyboard.

Connect as shown in the diagram below.:

<IMG INFO>

141,5

152,5

0

2

141,75

14,15

-1

### Serial outputs

There are 2 asynchronous outputs on the control:

- channel for serial communication with a personal computer through a Microtech interface module

- channel for serial communication with a standard Microtech keyboard. Power supply 12 VDC (2400, and 8,1).

### Copy card device

A copy card for reading and writing parameter maps may be connected to the serial connector.

- Copying the parameter map to the internal memory using the copy card: turn the power on to the instrument with the copy card already in place.

- Downloading the parameter map from the internal memory to the copy card: first connect the copy card to the instrument, entering the password corresponding to parameter Pa H46. While it is downloading data the instrument will display the label Occ. Disconnect the copy card when finished.

## Units of measurement

Control temperature may be displayed in:

- degrees °C, with decimal point

# User Interface

x

L’interfaccia, costituita dal frontale dello strumento, permette di svolgere tutte le operazioni legate all’uso dello strumento ed in particolare di:

- Impostare il modo di funzionamento

- Gestire le situazioni di allarme

- Verificare lo stato delle risorse

Front panel of the instrument

<IMG INFO>

198,35

97,25

0

2

113,4

14,15

-1

Keys

Keyboard

Selects operating mode:

Mode

If heating mode is enabled, each time the key is pressed the following sequence occurs:

Stand-by - cooling  heating  stand-by

<IMG INFO>

36,8

29,3

1

2

70,85

-14,65

-1

if heating mode is not enabled:

Stand-by   cooling  stand-by

In menu mode, this key acts as a SCROLL UP or UP key (increasing value).

Resets alarms, and turns the instrument on and off.

On-off – Reset alarms

<IMG INFO>

36,8

30,25

1

2

71,4

18,15

-1

Press once to reset all manually reset alarms not currently active.

Hold down the key for 2 seconds to turn the instrument  from on to off or vice versa. When off the heat led only stays on. In menu mode this key acts as the SCROLL DOWN or DOWN key (decreasing value).

Mode – on-off key combination

Pressing the “mode” and “on-off” keys at the same time.

If you press both keys at the same time and then release within 2 seconds, you will move one level deeper in the display menu.

If you press both keys for more than 2 seconds you will move one level up.

If you are currently viewing the lowest level in the menu and you press both keys and release within 2 seconds, you will go up one level.

<IMG INFO>

50,85

52,05

1

2

56,7

-26

-1

## Displays

Il dispositivo è in grado di comunicare qualsiasi tipo di informazione inerente il suo status, la sua configurazione, gli allarmi attraverso un display  e dei led presenti nel frontale.

### Display

Normal display shows:

- regulation temperature in tenths of degrees Celsius.

- the alarm code, if at least one alarm is active. If multiple alarms are active, the one with greater priority will be displayed, according to the Table of Alarms.

If temperature control is not analogue and depends on the status of a digital input (ST1 or ST2 configured as digital inputs), the “On” or “Off” label will be displayed, depending on whether temperature control is active or not.

<IMG INFO>

56,5

27,05

1

2

51

-13,5

-1

- In menu mode display depends on the current position.  Labels and codes are provided to help the user identify the function set.

- Heat led: when displaying hours of operation, indicates that the value must be multiplied x 100

### Led

Led 1 compressor 1.

ON if compressor 1 is active

<IMG INFO>

28,3

35,55

1

2

79,35

-17,75

-1

- OFF if compressor 1 is off

- BLINKS if safety timing is in progress

Defrost led

ON if defrosting is in progress

<IMG INFO>

31,1

29,3

1

2

76,55

-14,65

-1

- OFF if defrosting is disabled or has been completed

- BLINKS if timing is in progress (defrost interval)

Electrical heater/boiler led

ON if the internal anti-freeze electrical heater or boiler is on

<IMG INFO>

28,3

30,45

1

2

79,35

-15,25

-1

- OFF if the internal anti-freeze electrical heater or boiler is off

Heating led

ON if the device is in heating mode

<IMG INFO>

28,3

28

1

2

79,35

-14

-1

The interface on the front panel of the instrument can be used to carry out all the operations connected to the use of the instrument, and in particular to:

Set operating mode

<IMG INFO>

28,3

27,35

1

2

79,35

-13,7

-1

- Respond to alarm situations

Check the state of resources

## Remote keyboard

The remote keyboard on the display is an exact copy of the information displayed on the instrument, with the same leds;

Remote keyboard

Remote keyboard

<IMG INFO>

254,85

106,65

0

2

85,05

14,15

-1

It performs exactly the same functions as those described in the display section.

The only difference is in use of the UP and DOWN keys (to increase and decrease value), which are separate from the MODE and ON/OFF keys.

Connection with the controller is illustrated below:

Connection

<IMG INFO>

141,7

174,15

0

2

141,75

14,15

-1

## Parameter programming – Menu levels

Device parameters may be modified using a Personal Computer (with the required software, interface key and cables), or using the HyperCodex91keyboard.

If using the keyboard, access to parameters is arranged in a hierarchy of levels which may be accessed by pressing the “mode and “on-off” keys at the same time (as described above).

Each menu level is identified by a mnemonic code which appears on the display.

The structure is set up as shown in the diagram below:

Control probe

Current alarm

Set point:

Analog input:

Alarms:

Digital input:

Ore. Funz.:

Password:

Parameters:

Cooling set point label:

Heating set point label:

Input code: 
 -

Current alarm code:

Input code: 
-

Heating set point value

Cooling set point value

Configuration par.:

Compressor par.:

Fan par.:

Alarm par.:

Pump par.:

Anti-freeze par.:

Defrost par.:

Par. index 
-

Valore parametro

Numero ore parametro

Numero ore parametro

Valore parametro

Valore parametro

Valore parametro

Valore parametro

Valore parametro

Valore parametro

Pump hours:

Compressor hours:

Password value

Digital input status

Analog input value

Par. value 
-

Par. value 
-

Par. value 
-

Par. value 
-

Par. value 
-

Par. value 
-

Menu structure

Level  1

Level  2

Level  3

Level  4

Level  0

### Visibility of parameters and sub-menus

With a personal computer, interface key, suitable cables and the “Param Manager” software, it is possible to restrict the visibility and modification of parameters and entire submenus.

A “visibility value” may be assigned to each parameter, as described below:

| Value | Meaning |
| --- | --- |
| 0003 | Parameter or label visible at all times |
| 0258 | Parameter or label visible if user password entered correctly (password = Pa H46) |
| 0770 | Parameter or label visible if user password entered correctly (password = Pa H46). Parameter cannot be modified. |
| 0768 | Parameter visible from PC only. |

Some visibility settings are factory set.

For more information, please refer to the “Param Manager” instructions.

# System configuration

x

In this section we will look at how to configure parameters for various loads on the basis of the type of installation to be controlled.

## Compressor

Energy 100 can control systems consisting of one cooling circuit with 1 compressor.

The first compressor must be connected to output RL1 (relay);

Compressors will turned on or off depending on the temperatures detected and the temperature control functions that have been set (refer to the section on Compressor controls – regulation algorithm)

The polarity of RL1 is unvariable:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- relay ON if compressor 1/ capacity step ON

### Compressor timing

The turning on and off of compressors must comply with safety times which may be set by the user using the parameters specified below:

Safety timing

There is a safety interval between the time a compressor goes off and the time the same compressor comes back on (compressor on…off safety time, controlled by parameter Pa C01);

Off-on timing

This interval of time must elapse when the “Energy 100” is turned on.

On-on timing

There is a safety interval between the time a compressor is turned on and the time it is turned on again (compressor on...on safety time, controlled by parameter Pa C02) .

Off-on and on-on  comp. diagram

Compressor

ON

OFF

Off-on safety time

Pa C01

Seconds * 10

On-on safety time Pa CO2

## Condensation fan

### Fan configuration

The reference is to the fan control unit located outside near the heat exchanger which normally acts as a condenser. If a heat pump is used, the exchanger will operate as an evaporator.

<IMG INFO>

33

22

1

2

73

-11

-1

First of all, connect the fan up correctly to the appropriate output (refer to connection diagrams).

The fan output may be configured to work proportionately or as ON-OFF.

Pa F01 – Selection of triac output mode (TK and TK TTL):

- 0= proportional fan output (TK)

- 1= ON-OFF fan output; in this mode the fan will be off if the proportional control has an output of 0 , on at maximum speed (no capacity step) if control output is greater than 0.

- 2= external anti-freeze electrical heater control, for water-water machines with gas reversal

- 3= on-off operation when called up by the compressor. In this mode the fan is turned off and on depending on compressor status

If the output is configured as proportional TK the PICK-UP, PHASE SHIFT and IMPULSE DURATION parameters are also significant.

Every time the external fan is started up, power is supplied to the exchanger fan at maximum voltage, and the fan operates at maximum speed, for an amount of time equal to Pa F02 seconds; after this time the fan operates at the speed set by the regulator.

Pick-up

Pa F02 = Fan pick-up time (seconds)

Determines a delay during which it is possible to compensate the different electrical characteristics of the fan drive motors:

Phase shift

Pa F03 = duration of fan phase shift, expressed as a percentage.

Determines the duration of the TK output piloting impulse in microseconds*10

Impulse duration

Pa F04= triak piloting impulse duration

## Reversing valve

The reversing valve is used only when operating in “heat pump” mode.

It is active if:

- relay 3 configuration parameter Pa H23= 0.

- heat pump is enabled,  Pa H28= 1.

The reversing valve is off if the instrument is OFF or on stand-by.

Polarity may be configured using the following parameter:

Polarity

Pa H38= Reversing valve polarity

- 0: relay active in cool mode

- 1: relay active in heat mode

In cooling mode the reversing valve is never active.

## Hydraulic pump

The hydraulic pump must be connected to the output of relay RL2 (refer to connection diagram).

It is active only if the corresponding parameter, Pa H22, is set to 0.

The pump may be configured to function in two different ways using parameter Pa P01:

- Pa P01 = 0 : continuous operation

- Pa P01 = 1 : operation when called up by regulation algorithm (compressor)

CONTINUOUS OPERATION:

Continuous operation

Pump is on at all times.

OPERATION IN RESPONSE TO REQUEST:

Operation in response to request

- The pump comes on in response to a request from the regulation algorithm.

- The compressor comes on following a delay (Pa P02) after the time the pump comes on.

- The pump goes off following a delay (Pa P03) after the regulation algorithm has OFF status.

- During defrosting, when the compressor is OFF, the pump stays on.

Errore. Il collegamento non è valido.

Errore. Il collegamento non è valido. The pump is turned off if:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- there is an alarm comporting pump shutodown, such as a  manually reset flow switch alarm

- the instrument is on stand-by or OFF

When there is a current flow switch alarm with automatic resetting (refer to table of alarms), the pump will remain on even if the compressor is OFF due to the alarm.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

## Internal anti-freeze/supplementary electrical heaters

Anti-freeze/supplementary heaters are connected up to relay output RL4 (refer to connection diagram).

They are active only if the corresponding parameter, Pa H24, is set to 0.

If the output is configured this way, it will command the electrical heaters to come on and go off in accordance with the electrical heater configuration parameters, r01…r06, as described in the table below:

configuration

| Pa. | Description | Value |  |
| --- | --- | --- | --- |
|  |  | 0 | 1 |
| Pa r01 | Defrost configuration | comes on only when requested by control | always on during defrost |
| Pa r02 | Cooling mode configuration | off during cooling | on during cooling (depending on anti-freeze electrical heater control) |
| Pa r03 | Heating mode configuration | off during heating | on during heating (depending on anti-freeze electrical heater control) |
| Pa r04 | Configuration of electrical heater control probe in heating mode | controlled on the basis of ST1 (refer to connection diagrams) if Pa H05 (config. ST1)= 1 otherwise off | controlled on the basis of ST2 (refer to connection diagrams) if Pa H06 (config. ST2)= 1 otherwise off |
| Pa r05 | Configuration of control probe in cooling mode | controlled on the basis of ST1 (refer to connection diagrams) if Pa H05 (config. ST1)= 1 otherwise off | controlled on the basis of ST2 (refer to connection diagrams) if Pa H06 (config. ST2)= 1 otherwise off |
| Pa r06 | Configuration when OFF or on stand-by | Off when instrument is OFF or on stand-by | On when instrument is OFF or on stand-by |

## External anti-freeze electrical heaters

External anti-freeze electrical heaters are used on water-water machines with gas reversal.

They are connected to the triac TK output (refer to connection diagram) and controlled on the basis of probe ST3 (refer to analogue inputs) .

They are active only if:

- output TK is configured for anti-freeze electrical heaters, on a water-water machine with gas reversal (Pa F01= 2)

- ST3 is configured as an NTC anti-freeze input on a water-water machine with gas reversal (Pa H07= 4)

## Boiler

The output for boiler controller is relay RL4 (refer to connection diagram) with a suitable configuration.

The boiler output may operate in two different ways:

- to supplement another heating resource

- to provide heating with boiler only.

SUPPLEMENTARY BOILER:

The output is active if:

- relay 4 configuration parameter, Pa H24= 2.

- heat pump is declared present, Pa H28= 1.

- ST4 is configured as an outdoor probe, Pa H08= 3.

HEATING BOILER:

The output is active if:

relay 4 configuration parameter, Pa H24= 2.

heat pump is declared not present (H28= 0)

The boiler is turned off if:

- the device is operating in cooling mode

- the device is on stand-by or OFF

- there is a boiler shutdown alarm (refer to table of alarms)

## Internal fan

Outputs RL2, RL3, RL4 (refer to connection diagram) may be used for the internal fan, depending on the “fan control step” to be used.

relay 2 configuration parameter Pa H22= 1.

1 fan control step

2 fan control steps

2 fan control steps are active if:

- relay RL2 configuration parameter Pa H22= 1

- relay RL4 configuration parameter Pa H24= 1

3 fan control steps

3 fan control steps are active if:

- relay RL2 configuration parameter Pa H22= 1

- relay RL4 configuration parameter Pa H24= 1

- relay RL3 configuration parameter Pa H23= 1

The internal fan is turned off if:

- ST1probe configuration parameter  1(no probe)

- the device is on stand-by or OFF

- there is an alarm which has shut down the circuit (refer to table of alarms).

# Temperature control functions

x

x

Once Energy 100 has been configured, loads may be controlled on the basis of temperature and pressure conditions detected by probes and temperature control functions which may be defined using the appropriate parameters.

There are 4 possible operating modes:

Operating modes

- cooling

- heating

- stand-by

- off

Cooling: this is the “summer” operating mode; the machine is configured for cooling.

Cooling

Heating: this is the “winter” operating mode; the machine is configured for heating

Heating

Stand-by: the machine does not govern any temperature control function; it continues to signal alarms

Stand-by

Off: the machine is turned off.

Device off

The operating mode is determined by settings entered on the keyboard and by the following

Parameters:

- Operating mode parameter (Pa  H27)

- Heat pump parameter (Pa H28)

- Configuration parameter ST1  (Pa  H05) ( refer to Analogue inputs: configuration table)

- Configuration parameter ST2  (Pa  H06) (refer to Analogue inputs: configuration table)

Operating mode selection parameter (Pa  H27)

0= Selection from keyboard

1= Selection from digital input (refer to digital inputs)

2= Selection from analogue input (probe ST4)

Heat pump parameter (Pa H10)

0 = Heat pump not present

1= Heat pump present

Heating mode is permitted only if:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- heat pump is present (Pa H28= 1) or

- relay RL4 is configured as boiler output (Pa H24= 2).

Combinations of these parameters will generate the following rules:

Operating modes: configuration table

| Operating mode | Mode selection parameter Pa H27 | Configuration parameter ST1 Pa H05 | Configuration parameter ST2 Pa H06 |
| --- | --- | --- | --- |
| Mode selection from keyboard | 0 | Other than 2 | Other than 2 |
| Mode selection from digital input. | 1 | Other than 2 | Other than 2 |
| Mode selection from analogue input (ST4) | 2 | Other than 2 | Other than 2 |
| If input ST1 is on, operating mode is heating; if not, stand-by | Any | 2 | Other than 2 |
| If input ST2 is on, operating mode is cooling; if not, stand-by | Any | Other than 2 | 2 |
| If input ST1 is on, operating mode is heating; if ST2 is on, operating mode is cooling; if ST1 and ST2 are both on, there is a configuration error; if neither is on, operating mode is stand-by | Any | 2 | 2 |

## Selection of operating mode from analogue input

The controller permits selection of operating mode on the basis of the temperature detected and supplied by input ST4 (refer to analogue inputs).

This is permitted if both of the following conditions apply:

- probe ST4 is configured as an outdoor temperature probe (Pa H08= 3)

- mode selection parameter Pa H27= 2

In this case mode is selected automatically, on the basis of the following regulation algorithm parameters:

- Heating mode set point Pa H29

- Mode selection differential Pa H30.

An example of operation is shown in the diagram below:

Heating set point H29

Mode selection differential H30

Outdoor temperature

Mode

cooling

heating

Diagram

Mode may be changed from the keyboard for temperatures which fall within the mode selection differential (determined by parameter H30) only.

ON OFF digital input, if on, turns off all loads and displays “E00”.

## Setting set points

Loads are turned on and off dynamically on the basis of temperature control functions, temperature/pressure values detected by probes, and set points.

There are two set point values:

Cooling set point: this is the set point used as a reference when the device is in cooling mode

Heating set point: this is the set point used as a reference when the device is in heating mode

Set points may be modified using the keyboard, by accessing the “SET” sub-menu (refer to menu structure).

They may be given values within a range determined by parameters Pa H02 – Pa H01 (Heating) and Pa H04 – Pa H03 (Cooling).

## Dynamic set point

The regulation algorithm may be used to modify the set point automatically on the basis of outdoor conditions.

This modification is achieved by adding a positive or negative offset value to the set point, depending on:

- 4-20 mA analogue input (proportionate to a signal set by the user)

or

- temperature of outdoor probe

This function has two purposes: to save energy, or to operate the machine under particularly harsh outdoor temperature conditions.

<IMG INFO>

28

29

1

2

79

-14

-1

The dynamic set point is active if:

- Activation parameter Pa H31 = 1

- probe ST3 (analogue inputs) is configured as a current input for a dynamic set point (Pa H07 = 3) or probe ST4 (analogue inputs) is configured as an outdoor temperature probe (Pa H08 = 3)

Dynamic set point control parameters:

Control parameters

- Pa H32= Max. offset during cooling.

- Pa H33= Max. offset during heating

- Pa H34= Outdoor temperature set point during cooling

- Pa H35= Outdoor temperature set point during heating

- Pa H36= Heating and cooling temperature delta

The interaction of these parameters is illustrated in the graphs below:

Cooling

Modification on the basis of current input in cooling mode

Offset

Set-point

Current

20 mA

4 mA

Max

offset

In Heating

Modification on the basis of current input in heating mode

Current

20 mA

4 mA

Max

offset

In cooling

Modification on the basis of outdoor temperature in cooling mode

Offset

Set-point

Max

offset

In heating

Modification on the basis of outdoor temperature in heating mode

Temp.

Delta

Set temp. ext. in heating

## Switching from digital input

Digital inputs ID3, ID4, ID5 and ST4 (analogue inputs) may be configured to give an ON-OFF command. If this type of input is activated, the instrument will turn off all loads and show “E00” on the display.

## Load control

The parameters used to control loads on the basis of the temperature/pressure conditions detected by the probes are described below.

### Compressor control – regulation algorithm

The regulation algorithm calculates the load to be supplied through the compressors for both heating and cooling.

REGULATION ALGORITHM IN COOL MODE

Regulation algorithm in cool mode

If probe ST2 (analogue inputs) is not configured as a digital input for requests for cooling (Pa H06=2) or probe ST1(analogue inputs)  as a digital input for regulation algorithm requests (Pa H05=3), compressor management will depend on ambient temperature and a SET POINT which may be entered using the keyboard.

ST1 = temperature of inflowing water or inlet air

SET COOL= cooling set point set from keyboard

Pa C03 = hysteresis of cooling thermostat

<IMG INFO>

183,9

158,5

0

2

120,5

14,15

-1

If  Pa H05= 3, the compressor will be turned off and on depending on the status of input ST1.

Cooling diagram

If Pa H06= 2, the compressor will be turned off and on depending on the status of input ST2.

REGULATION ALGORITHM IN HEAT MODE

Regulation algorithm in heat mode

If probe ST1(analogue inputs) is not configured as a digital input for requests for heat (Pa H05=2) or as a digital input for regulation algorithm requests (Pa H05=3), compressor management will depend on:

- temperature ST3 (analogue inputs), if configuration parameter ST3 Pa H07= 5 (for water-water machines with water reversal)

- otherwise, temperature ST1(analogue inputs)

- a HEATING SET POINT which may be set from the keyboard

ST1/ST3 =Temperature of inflowing water or inlet air

SET HEATING= Heating set point set using the keyboard

Pa C04 = Hysteresis of heating thermostat

<IMG INFO>

183,9

158

0

2

120,5

14,15

-1

If  Pa H05= 2 or 3, the compressor is turned off and on depending on the status of input ST1.

Heating diagram

A compressor will always be off if:

It is not associated with a relay (power output)

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- The compressor has been shut down (refer to table of alarms)

- Safety timing is in progress

- The boiler is on

- The time lapse between pump on and compressor on is in progress (safety timing)

- Preventilation is in progress in cooling mode

- Energy 100 is on stand-by or off

- The parameter for configuration of probe ST1 Pa H05 = 0 (probe absent)

### Condensation fan control

Condensation control is dependent on the condensation temperature or pressure for the circuit.

Fan control will be on if:

- at least one probe per circuit is configured as a condensation probe (pressure or temperature); if not, the fan for the circuit will come ON and go OFF in response to the circuit compressors.

Fan control may be independent of the compressor, or it may be carried out in response to requests from the compressor;

Operating mode is determined by parameter Pa F05:

|  | Value |  |
| --- | --- | --- |
|  | 0 | 1 |
| Pa F05: fan output mode | if the compressor is off, the fan is off | condensation control is independent of the compressor |

When the compressor is started up, if the proportional control requests fan cut-off, the cut-off may be excluded for an amount of time equal to Pa F12 beginning when the compressor is turned on. If the controller requests cut-off during this time period, the fan will run at minimum speed.

If parameter Pa F05 is set to 1, condensation control will be dependent on condensation temperature or pressure, depending on how the following parameters are set:

The fan control unit may have a minimum speed, a maximum speed, and a “silent” speed (for silent operation, for instance during the night), as well as a proportional band within these values.

Silent speed

The fan will always be off if:

there is an alarm indicating that a condensation fan has shut down (refer to table of alarms).

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

- Energy 100 is on stand-by or off

CONDENSATION FAN CONTROL IN COOL MODE

Cool mode

Pa F06 = Minimum fan speed in COOL mode;

Pa F07 = Maximum silent fan speed in COOL mode

Pa F08 = Minimum fan speed temperature/pressure set point in COOL mode

Pa F09 = Prop. band Fan in COOL mode;

Pa F10 = Fan cut-off delta;

Pa F11 = Cut-off hysteresis;

Pa F13 = Maximum fan speed in COOL mode

Pa F14 = Maximum fan speed temperature/pressure set point in COOL mode

An example of interaction of these parameters is shown in the figure below:

Fan control in cool mode: diagram

Fan control in cool mode

<IMG INFO>

282,8

222,2

0

2

70,9

14,15

-1

In cooling mode only, if Pa F05 = 0 (operation in response to request from compressor), the fan will provide preventilation before the compressor comes on for an amount of time equal to Pa F25 (preventilation time in cooling mode).

Preventilation

Preventilation prevents the compressor from coming on with a condensation pressure that is too high.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

CONDENSATION FAN CONTROL IN HEAT MODE

Heat mode

Pa F15 = Minimum fan speed in HEAT mode;

Pa F16 = Maximum silent fan speed in HEAT mode;

Pa F17 = Minimum fan speed temperature/pressure set point in HEAT mode;

Pa F18 = Prop. band Fan in HEAT mode

Pa F10 = Fan cut-off delta;

Pa F11 = Cut-off hysteresis;

Pa F19 = Maximum fan speed in HEAT mode;

Pa F20 = Maximum fan speed temperature/pressure set point in HEAT mode.

An example of interaction of these parameters is shown in the figure below:

Fan control in heat mode: diagram

Fan control in heat mode

<IMG INFO>

282,8

226,3

0

2

70,9

14,15

-1

Control is not active if:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- defrosting is in progress

- the boiler is on

### Reversing valve control

Refer to section on reversing valves.

### Hydraulic pump control

Refer to section on the hydraulic pump.

### Anti-freeze/supplementary electrical heater control

Electrical heater control employs two separate set points, one for heating mode and one for cooling mode:

- Pa r07: electrical heater 1 set point in heating mode

- Pa r08: electrical heater 1 set point 1 in cooling mode

The two set points of the anti-freeze electrical heaters fall between minimum and maximum values which the user may set using the following parameters:

- Pa r09: maximum set point of anti-freeze electrical heaters

- Pa r10:  minimum set point of anti-freeze electrical heaters

When off or on stand-by, control is based on the cooling set point, using the control probe used in heating mode.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

Parameter Pa R11 determines the hysteresis around the set points for the anti-freeze/supplementary electrical heaters.

An example of operation is shown in the diagram below

diagram

Diagram illustrating anti-freeze/supplementary electrical heater control

<IMG INFO>

170

145,5

0

2

127,6

14,15

-1

### External anti-freeze electrical heater control

External anti-freeze electrical heaters are used on water-water machines with gas reversal.

External anti-freeze electrical heater output is active only if probe ST3 is configured as an anti-freeze NTC input for water-water machines with GAS  reversal (Pa H07= 4)

Control is based on probe ST3 with a set point which may be set using parameter Pa r12 and a hysteresis of Pa r11. Control is similar to that of internal electrical heaters.

### Boiler control

SUPPLEMENTARY BOILER:

The boiler is turned on in heating mode if outdoor temperature drops below Pa r13.

In this case the compressor and fan are turned off and heating is achieved using only the boiler.

The heat pump is turned back on if the outdoor temperature exceeds Pa r14+Pa r13.

If the boiler is working, temperature control is achieved using the boiler output; control is similar to compressor control in HEATING mode.

BOILER IN HEATING MODE:.

Temperature control in heating mode makes use of the boiler output, and is similar to compressor control in heat.ing mode;

The compressor and the external fan are turned off..

The boiler is turned off if:

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

- in cooling mode

- on stand-by or OFF

- there is a boiler shutdown alarm (refer to table of alarms)

### Internal fan control

INTERNAL FAN IN COOLING MODE:

The internal fan is turned off if:

- probe ST1 configuration parameter Pa H05  1

- there is a circuit shutdown alarm

- the instrument is OFF or on stand-by.

It is turned on at a speed depending on the difference between temperature ST1 and the COOLING set point.

Parameters:

Pa F21= Fan control step differential

Pa F22= Fan control step hysteresis

Diagram illustrating internal fan control in cooling mode

<IMG INFO>

282,8

234,75

0

2

70,9

14,15

-1

INTERNAL FAN CONTROL IN HEATING MODE:

The internal fan is turned off if:

- there is a hot start shutdown

- the heat pump is not present (Pa H28= 0)

Otherwise it is on, at a speed which depends on the difference between temperature ST1 and the HEATING set point.

Parameters:

Pa F20= Fan control step differential

Pa F21= Fan control step hysteresis

Diagram illustrating internal fan control in cooling mode

<IMG INFO>

282,8

229,65

0

2

70,9

14,15

-1

# Functions

x

## Recording hours of operation

The device stores the number of hours of operation of the following in permanent memory:

- hydraulic pump

- compressors

It is precise to within one minute.

Hours of operation may be displayed by entering the appropriate menu with the label Ohr (refer to menu structure).

The whole value is displayed if it is less than 999 hours; if it exceeds this value, the hundreds of hours will be shown and the decimal point will appear:

For example, 1234 hours will be displayed as follows:

<IMG INFO>

84,75

37,4

0

2

170,1

14,15

-1

To set the number of hours to zero, hold the DOWN key (refer to keys) down for two seconds while displaying the number of hours of operation.

MEMORY

35.48

MEMORY

35

Power failure

In the event of a power failure, the latest fraction of an hour recorded is set to 0, so that duration is rounded down

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

## Defrosting

The defrost function is active in heating mode only.

It is used to prevent ice formation on the surface of the external exchanger.

Ice formation on the external exchanger occurs more frequently when outdoor air is cold with high humidity.

Ice formation considerably reduces the machine’s thermodynamic performance and poses a risk of damage to the machine.

Defrosting is enabled if:

- it is enabled by the parameter (Pa d01= 1)

- there is at least one condensation probe (Pa H07, for input ST3= 1 or 2, or Pa H08, for input ST4= 1)

- the reversing valve is present

Defrost start and stop commands are given on the basis of condensation probe readings and parameter settings, as described below:

### Defrost start

- If condensation temperature/pressure drops below Pa d02 (Defrost start temperature) and the compressor is ON, the response counter starts (Pa d03, defrost response time).

- When duration Pa d03 has expired, the instrument begins defrosting.

- At this point, if Pa d06 (compressor…valve delay time) = 0, the compressor will stay on. If not, the control illustrated in the diagram below will be applied:

diagram

<IMG INFO>

282,8

133

0

2

70,9

14,15

-1

This delay prevents liquid from flowing back into the compressor.

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

During defrosting the reversal valve and the external fan are turned off.

<IMG INFO>

33,95

22,75

1

2

73,7

-11,4

-1

### Defrost end

Defrost will end if:

- temperature/pressure rises above Pa d04 (defrost end temperature/pressure).

- duration of defrosting reaches Pa d05 (max defrost time)

at the end of defrosting, if drip time Pa d07= 0, the compressor will stay on; if not, the control illustrated in the figure will be applied:

diagram

<IMG INFO>

282,8

129,25

0

2

70,9

14,15

-1

### Counter mode

- The defrost interval counter is interrupted when temperature/pressure rises above Pa d02 (defrost start temperature/pressure) or the compressor is turned off.

- The counter is set to zero after one of the following events: defrost cycle performed; power off; change in operating mode.

- The counter is also set to zero when the temperature/pressure rises above Pa d04 (defrost end temperature/pressure).

## Hot start function

This function is provided in HEATING mode only, using the internal fan, only when the internal exchanger is sufficiently hot. It prevents an unpleasant draft of cold air.

The function is active if:

- internal ventilation is active

- configuration parameter ST2 Pa H06= 1 (NTC probe outflowing water/air)

- in heating mode

The diagram below illustrates the function:

Regulation algorithm

ST2= water/air temperature probe

Pa F23= HOT START set point;

Pa F24= HOT START hysteresis

diagram

<IMG INFO>

211,95

180,75

0

2

106,35

14,15

-1

## Machine out of coolant signal

In all operating modes except boiler in operation or defrosting, machine functions are controlled to detect leakage in the coolant circuit or breakage of the reversing valves (if used as a heat pump).

The signal is given with code E44 (refer to table of alarms).

The regulation algorithm is enabled by Pa A23= 1; and ST2 (analogue inputs) must be configured as outflowing water input (Pa H06= 1).

The alarm is triggered if one of the following conditions apply continuously for an amount of time exceeding Pa A22:

- in heating mode: the difference in temperature represented by ST2-ST1 (or ST3)  (analogue inputs)  is less than Pa A20

- in cooling mode: the difference in temperature represented by ST1 (or ST3) -ST2  (analogue inputs) is less than Pa A20

The machine out of coolant alarm is always manually reset.

The timer is set to zero every time operating mode is changed and whenever the compressor is turned off. The counter is stopped for an amount of time which may be set using parameter Pa A21 whenever the compressor is turned on.

## Power failure

In the event of a power failure, when the power is restored the control will return to the status it had before the power went out.

If defrosting is underway, it will be cancelled. All timing in progress when the power goes out will be cancelled and started again.

# Parameters

x

x

Parameters make the ”Energy 100” a fully configurable device.

They may be modified through:

- instrument keyboard

- memory card

- personal computer (with a suitable connection and “Param manager” software)

## Description of parameters

We will now look at parameters in detail, divided by category.

### Configuration parameters

Determine the features of the machine. If one or more parameters in this category are modified, the controller must be switched off after the modification and switched on again to ensure correct operation.

Set point “cooling”

Pa G01

setpoint in “cooling” mode

Set point “heating”

Pa G02

setpoint in “heating” mode

Maximum set point during “heating”

Pa H01

Upper limit on set point in “heating” mode

Minimum set point during “heating”

Pa H02

Lower limit on set point in “heating” mode

Maximum set point during “cooling”

Pa H03

Upper limit on set point in “cooling” mode

Minimum set point during cooling

Pa H04

Lower limit on set point in “cooling” mode

Configuration ST1

Pa H05

Used to configure analogue input ST1

0= No probe

1= Inflowing water/air analogue input

2= Heating request digital input

3= Regulation algorithm request digital input

Configuration ST2

Pa H06

0= No probe

1= Outflowing water/antifreeze/inlet air analogue input

2= Cooling request digital input

Configuration ST3

Pa H07

0= No probe

1= Condensation control analogue input

2= 4...20 mA condensation input

3= 4...20 mA dynamic set point input

4= Antifreeze analogue input for water-water machines with gas reversal

5= Regulation algorithm input in “heating” mode for water-water machines with manual reversal

Configuration ST4

Pa H08

0= No probe

1= Condensation control analogue input

2= Multifunctional digital input

3= Outdoor temperature analogue input

Bottom of scale pressure value

Pa H09

Maximum inflowing value; determines the value corresponding to a current of 20 mA

Polarity of digital input ID1

Pa H10

Polarity of digital input ID2

Pa H11

Polarity of digital input ID3

Pa H12

Polarity of digital input ID4

Pa H13

Polarity of digital input ID5

Pa H14

0= Active when contact closed

1= Active when contact open

Polarity of analogue input ST1

Pa H15

Polarity of analogue input ST2

Pa H16

Polarity of analogue input ST4

Pa H17

If configured as digital inputs:

0= Active when contact closed

1= Active when contact open

Configuration of digital input ID3

Pa H18

Configuration of digital input ID4

Pa H19

Configuration of digital input ID5

Pa H20

0= Compressor 1 thermal switch

1= Fan thermal switch

2= Flow switch

3= Remote Heat/Cool

4= Remote ON-OFF

ST4 configuration if configured as digital input

Pa H21

0= Compressor thermal switch

1= Fan thermal switch

2= Flow switch

3= Remote Heat/Cool

4= Remote ON-OFF

Configuration of output RL2

Pa H22

0= Pump

1= Internal fan step 1

Configuration of output relay RL3

Pa H23

0= Reversal

1= Internal fan step 3

Configuration of output relay RL4

Pa H24

0= Anti-freeze electrical heaters

1= Internal fan step 2

2= Boiler

Optional analogue output configuration

Pa H25

0= no optional output

1= fan speed 4-20 mA output

2=  0-10 V fan speed output

Configuration of serial protocol (not used)

Pa H26

0= no output

1= keyboard output

Selection of operating mode

Pa H27

May be used to select which input determines operation in Heating/Cooling mode

0= Selection from keyboard

1= Selection from digital input

2= Selection from analogue input (probe ST4)

Presence of heat pump

Pa H28

0= Heat pump absent

1= Heat pump present

Heating mode set point

Pa H29

If mode selection from analogue input is enabled, this is the value of ST4 below which the control will switch to “heating” mode

Mode selection differential

Pa H30

If mode selection from analogue input is enabled, this is the temperature differential for switching to “cooling” mode

Enable dynamic set point

Pa H31

Enables dynamic set point function

0= Dynamic set point disabled

1= Dynamic set point enabled

Dynamic set point offset in cooling mode

Pa H32

The maximum value that may be added to the set point in “cooling” mode

Dynamic set point offset in heating mode

Pa H33

The maximum value that may be added to the set point in “heating” mode

Outdoor temperature dynamic set point in cooling mode

Pa H34

The temperature above which the set point offset is zero in cooling mode.

Outdoor temperature dynamic set point in heating mode

Pa H35

The temperature above which the set point offset is zero in heating mode.

Outdoor temperature dynamic set point differential in heating mode

Pa H36

May be used to set the differential for the outdoor temperature above which the maximum offset applies.

Reversing valve polarity

Pa H37

0=relay ON in cooling mode

1=relay ON in heating mode

Offset ST1,

Pa H38

Offset ST2,

Pa H39

Offset ST4

Pa H41

These parameters may be used to compensate the error that may occur between the temperature reading and the actual temperature or pressure.

Offset ST3

Pa H40

This parameter may be used to compensate the error that may occur between the temperature or pressure reading and the actual temperature or pressure.

mains frequency

Pa H42

mains frequency 50 Hz

mains frequency 60 Hz

Family serial address,

Pa H43

Device serial address

Pa H44

May be used to select serial address. Both normally  0.

User password

Pa H45

May be used to enter a parameter for access to level two parameters. May also be used to copy instrument parameters to copy card

Copy card write password

Pa H46

The password that must be entered to copy parameters to the copy card.

Do not modify

Pa H47

This parameter must always be 0

### Alarm parameters

Low pressure pressure switch bypass time.

Pa A01

Determines the delay between starting up the compressor and starting up the low pressure digital alarm diagnostics. Expressed in seconds.

Low pressure alarm events per hour

Pa A02

Used to set the number of low pressure digital alarm events per hour beyond which the system will switch from automatic reset to manual reset.

Bypass flow switch after pump on

Pa A03

Determines the delay between activation of the hydraulic pump and activation of the flow switch alarm diagnostics. Expressed in seconds.

Duration of active flow switch input

Pa A04

May be used to set the amount of time for which the flow switch digital input must remain active to generate a flow switch alarm. The timer starts after the flow switch by-pass time. Expressed in seconds.

Duration of inactive flow switch input

Pa A05

May be used to set the time for which the flow switch digital input must remain inactive to be included in the corresponding alarm. Expressed in seconds.

Number of flow switch alarms/hour

Pa A06

May be used to set the number of flow switch digital alarms per hour after which the alarm is switched from automatic to manual reset. When this occurs, the hydraulic pump is deactivated.

Compressor thermal switch bypass following compressor on

Pa A07

Determines the delay between compressor activation and activation of the compressor thermal switch digital diagnostics alarm. Expressed in seconds.

Number of compressor protection alarm events/hour

Pa A08

May be used to set a number of compressor thermal switch alarm events per hour beyond which the alarm is switched from automatic to manual reset..

Fan thermal switch alarm events per hour

Pa A09

May be used to set a number of fan thermal switch alarm events per hour beyond which the alarm is switched from automatic to manual reset.

Anti-freeze alarm by-pass

Pa A10

May be used to set a delay in triggering of anti-freeze alarm after the machine is starter up. Expressed in minutes.

Anti-freeze alarm set point

Pa A11

May be used to set the temperature below which the anti-freeze alarm is triggered.

Anti-freeze alarm differential

Pa A12

May be used to set the anti-freeze alarm differential.

Pa A13

Anti-freeze alarm events per hour

May be used to set a number of anti-freeze alarm events per hour beyond which the alarm is switched from automatic to manual reset.

Analogue input high pressure set point

Pa A14

May be used to set a condensation pressure/temperature value beyond which the high pressure alarm will be triggered.

Analogue input high pressure hysteresis

Pa A15

May be used to set the differential for the analogue high pressure alarm.

Analogue input low pressure bypass

Pa A16

Determines the delay after turning on the compressor before activation of the analogue input low pressure alarm. Expressed in seconds.

Analogue input low pressure set point

Pa A17

May be used to set a temperature/pressure value below which the low pressure alarm will be triggered.

Analogue input low pressure hysteresis

Pa A18

May be used to set the differential for the analogue low pressure alarm.

Analogue input low pressure alarm events/hour

Pa A19

May be used to set a number of low pressure analogue alarm events per hour beyond which the alarm will be switched from automatic to manual reset.

Machine out of coolant differential

Pa A20

If the absolute value of the difference between the set point and the temperature control probe exceeds this parameter, the machine out of coolant diagnostics counter will start.

Machine out of coolant bypass

Pa A21

Determines the delay between the turning on of the first compressor in the corresponding cooling circuit and activation of the machine out of coolant alarm diagnostics. Expressed in minutes.

Machine out of coolant duration

Pa A22

Determines the amount of time beyond which the machine out of coolant alarm will be triggered.

Machine out of coolant alarm activation

Pa A23

Enables machine out of coolant alarm

Enable low pressure alarm during defrosting

Pa A24

Enables the minimum alarm during defrosting. If 0, the low pressure alarm is disabled during defrosting.

### Compressor parameters

OFF-ON safety time

Pa C01

The minimum amount of time that must pass between turning off the compressor and turning it on again. Expressed in tens of seconds.

ON-ON safety time

Pa C02

The minimum amount of time that must pass between turning the compressor on and turning it on again. Expressed in tens of seconds.

Cooling regulation algorithm hysteresis

Pa C03

May be used to select intervention differential in cooling mode.

Heating regulation algorithm hysteresis

Pa C04

May be used to select intervention differential in heating mode.

### Fan control parameters

Pa F01

Fan output configuration

0: proportional condensation control TK output

1: ON-OFF TK output

2: anti-freeze electrical heater output for water-water machines with gas reversal

3: ON-OFF on the basis of compressor calls

Fan pick-up time

Pa F02

Time for which fan runs at maximum speed after starting up. Expressed in seconds/10.

Fan phase shift

Pa F03

May be used to adapt output to various types of fans.

Impulse duration of triac on

Pa F04

May be used to vary the length of the impulse from the triac.

Functioning in response to compressor request

Pa F05

0: if the compressor is off, the fan is off

1: Condensation control is independent of the compressor

Minimum speed during cooling

Pa F06

Minimum value of proportional fan control during cooling. Expressed as a percentage of the maximum permitted voltage, from 0 to 100%,.

Pa F07

Maximum silent speed during cooling

Maximum value of proportional fan control during cooling. Expressed as a percentage of the maximum permitted voltage, from 0 to 100%,.

Pa F08

Minimum fan speed temperature/pressure set point during cooling

Condensation pressure/temperature value below which the fan runs at minimum cooling speed.

Pa F09

Proportional band during cooling

Temperature/pressure differential corresponding to change from minimum to silent maximum fan speed during cooling.

Cut-off differential

Pa F10

Condensation temperature/pressure differential within which fan continues to run at low speed.

Cut-off hysteresis.

Pa F11

Condensation temperature/pressure differential for fan cut-off.

Cut-off bypass time

Pa F12

Determines the amount of time after fan start-up during which fan cut-off is excluded. Expressed in seconds.

Maximum speed during cooling

Pa F13

May be used to set a speed step corresponding to a given temperature/pressure value during cooling.

Maximum fan speed temperature/pressure set point in cooling mode

Pa F14

Condensation temperature/pressure value corresponding to the fan speed set for par. F19. F13.

Minimum speed during heating

Pa F15

Minimum proportional fan control value in heating mode. Expressed as a percentage of the maximum permitted voltage, from 0 to 100%,.

Maximum silent speed during heating

Pa F16

Maximum value of proportional fan control during heating. Expressed as a percentage of the maximum permitted voltage, from 0 to 100%,.

Minimum fan speed temperature/pressure set point during heating

Pa F17

Condensation temperature/pressure value above which the fan operates at minimum speed in heating mode.

Proportional band during heating

Pa F18

Temperature/pressure differential corresponding to a change from minimum to maximum silent fan speed during heating.

Maximum speed during heating

Pa F19

May be used to set a speed step corresponding to a given temperature/pressure value during heating.

Maximum fan speed temperature/pressure set point during heating

Pa F20

Condensation temperature/pressure value corresponding to the fan speed set for par. F19. Pa F19

Internal fan step differential

Pa F21

May be used to set a temperature differential between one step of fan control and the next for internal fan control.

Internal fan step hysteresis

Pa F22

May be used to set a hysteresis for each fan control step cut-off.

Hot start set point

Pa F23

May be used to set a temperature value for probe ST2 below which internal fan control is shut down.

Hot start hysteresis

Pa F24

May be used to set a hysteresis for the hot start function.

Preventilation in cooling mode

Pa F25

May be used to set a preventilation time in cooling mode before the compressor is turned on.

### Pump parameters

Pump operating mode

Pa P01

May be used to determine pump operating mode:

0=continuous operation

1=operation in response to a request from the regulation algorithm

Delay between pump ON and compressor ON

Pa P02

May be used to set a delay between starting a pump and starting a compressor, expressed in seconds. Expressed in secods.

Delay between compressor OFF and pump OFF

Pa P03

May be used to set a delay between turning off a compressor and turning off a pump, expressed in seconds. Expressed in seconds.

### Anti-freeze/boiler parameters

Configuration of electrical heaters in defrost mode

Pa r01

Determines electrical heater operation during defrosting

0=come on only in response to a request from the regulation algorithm

1=always on during defrosting

Configuration of electrical heaters on in cooling mode

Pa r02

Determines electrical heater operation in cooling mode

0=off during cooling

1=on during cooling (in response to anti-freeze electrical heater regulation algorithm)

Configuration of electrical heaters on in heating mode

Pa r03

Determines electrical heater operation  in heating mode

0=off during heating

1= on during heating (in response to anti-freeze electrical heater regulation algorithm)

Configuration of anti-freeze electrical heater control probe in heating mode

Pa r04

Determines electrical heater control  probe in heating mode

0= Controls on the basis of probe ST1

1= Controls on the basis of probe ST2

Configuration of anti-freeze electrical heater control probe in cooling mode

Pa r05

Determines electrical heater control probe in cooling mode

0= Controls on the basis of probe ST1

1= Controls on the basis of probe ST2

Configuration of electrical heaters when OFF or on stand-by

Pa r06

Determines the status of electrical heaters when the instrument is OFF or on stand-by

0=Always off when OFF or on stand-by

1=On when OFF or on stand-by (in response to anti-freeze electrical heater control algorithm)

Set point of anti-freeze electrical heaters in heating mode

Pa r07

Temperature value below which anti-freeze electrical heaters come on in heating mode.

Set point of anti-freeze electrical heaters in cooling mode

Pa r08

Temperature value below which anti-freeze electrical heaters come on in cooling mode.

Maximum set point of anti-freeze electrical heaters

Pa r09

Determines the maximum setting of the anti-freeze electrical heater set point.

Minimum set point of anti-freeze electrical heaters

Pa r10

Determines the minimum setting of the anti-freeze electrical heater set points.

Anti-freeze heater hysteresis

Pa r11

Anti-freeze electrical heater control algorithm hysteresis.

Set point of external anti-freeze electrical heaters

Pa r12

Temperature below which external anti-freeze electrical heaters come on.

Outdoor temperature set point for boiler on

Pa r13

The temperature below which the boiler is turned on and the heat pump is turned off.

Boiler off differential

Pa r14

Boiler off differential. If outdoor temperature exceeds Pa r14+Pa r13, the boiler will be turned off and the heat pump will be turned on.

### Defrost parameters

Defrost enabled

Pa d01

0= defrost function disabled

1= defrost function enabled

Defrost start temperature/pressure

Pa d02

Temperature/pressure below which the defrost cycle is started.

Defrost interval (response time)

Pa d03

Duration for which probe remains below defrost start temperature/pressure, expressed in minutes. Expressed in minutes.

Defrost end temperature/pressure

Pa d04

Temperature/pressure above which defrost ends.

Maximum defrost time (time-out)

Pa d05

Maximum duration of defrosting. Expressed in minutes.

Compressor-reversing valve wait time (anti-bleeding)

Pa d06

Wait time between compressor going off and reversal of the 4-way valve at the beginning of the defrost cycle.

Drip time

Pa d07

Wait time at the end of the defrost cycle between turning off the compressor and reversing the 4-way valve.

## Table of parameters

All ”Energy 100” parameters are listed in the table below.

Configuration parameters

| CONFIGURATION PARAMETERS* |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Default | Limits | Unit of measurement |
| Pa G01 | Set Point “Cooling” |  |  |  |
| PA G02 | Set Point “Heating” |  |  |  |
| Pa H01 | Upper limit on “heating” set point | 60.0 | H02  90.0 | C/10 |
| Pa H02 | Lower limit pm “heating” set point | 30.0 | -40.0  H01 | C/10 |
| Pa H03 | Upper limit on “cooling” set point | 40.0 | H04  90.0 | C/10 |
| Pa H04 | Lower limit on “cooling” set point | 0.0 | -40.0  H03 | C/10 |
| Pa H05 | Configuration of analogue input ST1 | 1 | 0  3 | Num |
| Pa H06 | Configuration of analogue input ST2 | 1 | 0  3 | Num |
| Pa H07 | Configuration of analogue input ST3 | 1 | 0  5 | Num |
| Pa H08 | Configuration of analogue input ST4 | 1 | 0  3 | Num |
| Pa H09 | Bottom of scale pressure value | 300 | 0300 | KPa*10 |
| Pa H10 | Polarity of digital input ID1 | 1 | 0  1 | Flag |
| Pa H11 | Polarity of digital input ID2 | 1 | 0  1 | Flag |
| Pa H12 | Polarity of digital input ID3 | 1 | 0  1 | Flag |
| Pa H13 | Polarity of digital input ID4 | 1 | 0  1 | Flag |
| Pa H14 | Polarity of digital input ID5 | 1 | 0  1 | Flag |
| Pa H15 | Polarity of input ST1 (configured as digital) | 1 | 0  1 | Flag |
| Pa H16 | Polarity of input ST2 (configured as digital) | 1 | 0  1 | Flag |
| Pa H17 | Polarity of input ST4 (configured as digital) | 1 | 0  1 | Flag |
| Pa H18 | Configuration of digital input ID3 | 0 | 0  4 | Num |
| Pa H19 | Configuration of digital input ID4 | 1 | 0  4 | Num |
| Pa H20 | Configuration of digital input ID5 | 2 | 0  4 | Num |
| Pa H21 | Configuration ST4 if digital input | 4 | 0  4 | Num |
| Pa H22 | Configuration of relay RL2 | 0 | 0  1 | flag |
| Pa H23 | Configuration of relay RL3 | 0 | 0  1 | flag |
| Pa H24 | Configuration of relay RL4 | 0 | 0  2 | Num |
| Pa H25 | Configuration of optional output | 0 | 0  3 | Num |
| Pa H26 | Configuration of keyboard output | 0 | 0  1 | Num |
| Pa H27 | Selection of operating mode | 0 | 0  2 | Num |
| Pa H28 | Presence of heat pump | 1 | 0  1 | Flag |
| Pa H29 | Set point in AUTOMODE | 10 | 0  255 | C |
| Pa H30 | Differential in AUTOMODE | 15.0 | 0  25.5 | C/10 |
| Pa H31 | Dynamic set point enabled | 1 | 0  1 | Flag |
| Pa H32 | Proportional band of “cooling” dynamic set point | 5.0 | 0  25.5 | C/10 |
| Pa H33 | Proportional band of “heating” dynamic set point | 5.0 | 0  25.5 | C/10 |
| Pa H34 | Outdoor temp.dynamic set point in cooling mode | 13 | 0  255 | C |
| Pa H35 | Outdoor temp. dynamic set point in heating mode | 22 | 0  255 | C |
| Pa H36 | Differential of outdoor temp. dynamic set point | 5.0 | 0  25.5 | C/10 |
| Pa H37 | Reversing valve polarity | 1 | 0  1 | Flag |
| Pa H38 | Offset ST1 | 0.0 | -12.7  12.7 | C/10 |
| Pa H39 | Offset ST2 | 0.0 | -12.7  12.7 | C/10 |
| Pa H40 | Offset ST3 | 0 | -127  127 | C/10 - kPa*10 |
| Pa H41 | Offset ST4 | 0.0 | -12.7  12.7 | C/10 |
| Pa H42 | Frequency 50/60 Hz | 0 | 0  1 | Flag |
| Pa H43 | Family serial address | 0 | 0  14 | Num. |
| Pa H44 | Device serial address | 0 | 0  14 | Num. |
| Pa H45 | User password | 1 | 0  255 | Num |
| Pa H46 | Copy card write password | 2 | 0  255 | Num |
| Pa H47 | Do not modify | 0 | 0  1 | Num |

- If parameters in this category are modified, the controller must be turned off after the modification and turned on again to guarantee correct functioning.

Table of parameters: alarm parameters

| ALARM PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa A01 | Low pressure pressure switch bypass time. | 20 | 0  255 | Seconds |
| Pa A02 | Low pressure alarm events per hour | 4 | 0  255 | Num |
| Pa A03 | Flow switch by-pass after pump is turned on | 10 | 0  255 | Seconds |
| Pa A04 | Duration of active flow switch input | 15 | 0  255 | Seconds |
| Pa A05 | Duration of inactive flow switch input | 15 | 0  255 | Seconds |
| Pa A06 | Number of flow switch alarms/hour | 5 | 0  255 | Num |
| Pa A07 | Compressor thermal switch bypass following compressor on | 5 | 0  255 | Seconds |
| Pa A08 | Fan thermal switch alarm events per hour | 2 | 0  255 | Num |
| Pa A09 | Fan thermal switch alarm events per hour | 2 | 0  255 | Num |
| Pa A10 | Anti-freeze alarm by-pass after ON-OFF | 5 | 0  255 | Minutes |
| Pa A11 | Anti-freeze alarm set point | 2 | -127  127 | C |
| Pa A12 | Anti-freeze alarm hysteresis | 1.0 | 0  25.5 | C/10 |
| Pa A13 | Anti-freeze alarm events per hour | 2 | 0  255 | Num |
| Pa A14 | High pressure analogue alarm set point | 600 | 0  900 | C/10 - kPa*10 |
| Pa A15 | Analogue input high pressure hysteresis | 10 | 0  255 | C/10 - kPa*10 |
| Pa A16 | Analogue input low pressure by-pass | 10 | 0  255 | Seconds |
| Pa A17 | Analogue input low pressure alarm set point | -30 | -500  800 | C/10 - kPa*10 |
| Pa A18 | Analogue input low pressure alarm hysteresis | 10 | 0  255 | C/10 - kPa*10 |
| Pa A19 | Low pressure alarm events per hour | 2 | 0  255 | Num |
| Pa A20 | Machine out of coolant differential | 30 | 0  25.5 | C/10 |
| Pa A21 | Machine out of coolant by-pass | 30 | 0  255 | Minutes |
| Pa A22 | Machine out of coolant duration | 120 | 0  255 | Minutes |
| Pa A23 | Machine out of coolant alarm activation | 0 | 0  1 | Flag |
| Pa A24 | Enable low pressure alarm during defrosting | 0 | 0  1 | Flag |

Table of parameters: compressor parameters

| COMPRESSOR PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa C01 | ON-OFF safety time | 3 | 0  255 | Seconds*10 |
| Pa C02 | ON-ON safety time | 3 | 0  255 | Seconds*10 |
| Pa C03 | Cooling regulation algorithm hysteresis | 1.5 | 0  25.5 | C/10 |
| Pa C04 | Heating regulation algorithm hysteresis | 1.5 | 0  25.5 | C/10 |

Table of parameters: fan control parameters

| FAN CONTROL PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa F01 | Fan output configuration | 0 | 0  3 | Num. |
| Pa F02 | Fan pick-up time | 50 | 0  255 | Seconds/10 |
| Pa F03 | Fan phase shift | 5 | 0  100 | % |
| Pa F04 | Impulse duration of triac on | 30 | 0  255 | uS*10 |
| Pa F05 | Functioning in response to compressor request | 1 | 0  1 | Flag |
| Pa F06 | Minimum speed during cooling | 22 | 0  100 | % |
| Pa F07 | Maximum silent speed in cooling mode | 70 | 0  100 | % |
| Pa F08 | Minimum fan speed temperature/pressure set point during cooling | 400 | -500  800 | C/10 - kPa*10 |
| Pa F09 | Prop. band during cooling | 100 | 0  255 | C/10 - kPa*10 |
| Pa F10 | Cut-off differential | 30 | 0  255 | C/10 - kPa*10 |
| Pa F11 | Cut-off hysteresis. | 10 | 0  255 | C/10 - kPa*10 |
| Pa F12 | Cut-off bypass time | 20 | 0  255 | Seconds |
| Pa F13 | Max speed in cooling mode | 89 | 0  100 | % |
| Pa F14 | Maximum fan speed temperature/pressure set point in cooling mode | 700 | -500  800 | C/10 - kPa*10 |
| Pa F15 | Minimum speed during heating | 30 | 0  100 | % |
| Pa F16 | Maximum speed during heating | 70 | 0  100 | % |
| Pa F17 | Minimum fan speed temperature/pressure set point during heating | 100 | -500  800 | C/10 - kPa*10 |
| Pa F18 | Proportional band during heating | 50 | 0  255 | C/10 - kPa*10 |
| Pa F19 | Maximum speed during heating | 90 | 0  100 | % |
| Pa F20 | Maximum fan speed temperature/pressure set point during heating | 50 | -500  800 | C/10 - kPa*10 |
| Pa F21 | Internal fan step differential | 20 | 0  25.5 | C/10 |
| Pa F22 | Internal fan step hysteresis | 10 | 0  25.5 | C/10 |
| Pa F23 | Hot start set point | 50 | 0  255 | C |
| Pa F24 | Hot start hysteresis | 10 | 0  25.5 | C/10 |
| Pa F25 | Preventilation in cooling mode | 0 | 0  255 | Seconds |

Table of parameters: pump parameters

| PUMP PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa P01 | Pump operating mode | 1 | 0  1 | Flag |
| Pa P02 | Delay between pump ON and compressor ON | 200 | 0  255 | Seconds |
| Pa P03 | Delay between compressor OFF and pump OFF | 230 | 0  255 | Seconds |

Table of parameters: anti-freeze/boiler parameters

| ANTI-FREEZE/BOILER PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa r01 | Configuration of electrical heaters in defrost mode | 1 | 0  1 | Flag |
| Pa r02 | Configuration of electrical heaters on in cooling mode | 1 | 0  1 | Flag |
| Pa r03 | Configuration of electrical heaters on in heating mode | 1 | 0  1 | Flag |
| Pa r04 | Configuration of anti-freeze electrical heater control probe in heating mode | 1 | 0  1 | Flag |
| Pa r05 | Configuration of anti-freeze electrical heater control probe in cooling mode | 1 | 0  1 | Flag |
| Pa r06 | Electrical heater configuration when OFF or on STAND-BY | 1 | 0  1 | Flag |
| Pa r07 | Internal anti-freeze heater set point in heating mode | 2 | Pa r09Pa r10 | C |
| Pa r08 | Internal anti-freeze heater set point in cooling mode | 1 | Pa r09Pa r10 | C |
| Pa r09 | Maximum set point of anti-freeze electrical heaters | 90 | Pa r10127 | C |
| Pa r10 | Minimum set point of anti-freeze electrical heaters | -10 | -127  Pa r09 | C |
| Pa r11 | Anti-freeze heater hysteresis | 1.0 | 0  25.5 | C/10 |
| Pa r12 | Outdoor anti-freeze heater set point | 5 | Pa r09Pa r10 | C |
| Pa r13 | Outdoor temperature set point for boiler on | 10 | -127  127 | C |
| Pa r14 | Outdoor temperature differential for boiler off | 20 | 0  25.5 | C/10 |

Table of parameters: defrost parameters

| DEFROST PARAMETERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Par. | Description | Value | Limits | Unit of measurement |
| Pa d01 | Defrost enabled | 1 | 0  1 | Flag |
| Pa d02 | Defrost start temperature/pressure | -20 | -500  800 | C/10 - kPa*10 |
| Pa d03 | Defrost call time | 20 | 0  255 | Minutes |
| Pa d04 | Defrost end temperature/pressure | 300 | -500  800 | C/10 - kPa*10 |
| Pa d05 | Defrost time-out | 30 | 0  255 | Minutes |
| Pa d06 | Anti bleeding time | 30 | 0  255 | Seconds |
| Pa d07 | Drip time | 30 | 0  255 | Seconds |

# Diagnostics

x

“Energy 100” can perform full systems diagnostics and signal a series of alarms.

Alarms

Alarm trigger and reset modes are set using parameters Pa A01 – Pa A26.

For some alarms the signal will not be given for a certain amount of time, determined by a parameter.

For some alarms, the number of alarm events per hour is counted: if the number of alarm events has exceeded a threshold determined by a parameter within the last hour, the alarm will switch from automatic reset to manual reset.

Alarm events per hour

Alarms are sampled every 225 seconds;

Example: if the number of events/hour is set to 3,  the duration of an alarm must fall between 2*225 seconds and 3*225 seconds for the alarm to be switched from automatic to manual reset.

Time

225 s

225 s

225 s

225 s

1

2

3

Counter

Alarm

Automatic reset

Manual reset

Alarm

sampling

If an alarm is triggered more than once within one sampling period (225 seconds), only one alarm will be counted.

<IMG INFO>

36,75

24,25

1

2

70,85

-12,15

-1

Alarms with manual reset are reset by pressing the ON-OFF button and releasing.

Manual reset shuts down corresponding loads and requires an operator to intervene (reset the alarm using the ON-OFF control).

<IMG INFO>

28,3

29,3

1

2

79,35

-14,65

-1

Manual reset alarms are used mainly to identify problems which could result in damage to the system.

## List of alarms

When an alarm is triggered, two things occur:

- The corresponding loads are shut down

- The alarm appears on the keyboard display

The alarm message consists of a code with the format “Enn” (where nn is a 2-digit number identifying the type of alarm, such as: E00, E25, E39….).

All possible alarms are listed in the table below, along with their codes and the corresponding loads that will be shut down:

Tabella Allarmi

| CODE | SIGNAL | DESCRIPTION | LOADS SHUT DOWN |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | COMP. | EXT.. FAN. | INT. FAN | PUMP | EL. HEATER | BOILER |
| E00 | Remote Off | - All loads will be shut down; - Triggered by the digital input configured as “Remote ON-OFF ” (refer to digital inputs) | YES | YES | YES | YES | YES (if Pa r06=0) | YES |
| E01 | High pressure (digital) | - Compressors will be shut down; - Triggered by digital input ID1 (refer to digital inputs) - Always manually reset | YES |  |  |  |  |  |
| E02 | Low pressure (digital) | - Compressors and fans will be shut down; - Triggered by digital input ID2 (refer to digital inputs); - Automatically reset unless alarm events per hour reaches the value of parameter Pa A02, after which manually reset; - Inactive during timer Pa A01 after a compressor is turned on or the 4-way valve (reversing valve) is reversed. - Inactive during defrosting if Pa 24=0. | YES | YES | YES |  |  |  |
| E03 | Compressor thermal switch protection | - Compressors will be shut down; - Triggered by the digital input configured as “Compressor thermal switch” (refer to digital inputs); - Automatically reset unless alarm events per hour reaches the value of parameter Pa A07, after which manually reset; - Inactive during timer Pa A08 after compressor is turned on. | YES |  |  |  |  |  |
| E04 | Thermal switch protection condenser fan | - Compressors and fans will be shut down; - Triggered by the digital input configured as “Fan thermal switch” (refer to digital inputs); - Automatically reset unless alarm events per hour reaches the value of parameter Pa A09, after which manually reset; | YES | YES | YES |  |  |  |
| E05 | Anti-freeze | - External fans and compressor will be shut down; - Active if analogue probe ST2 (refer to analogue inputs) is configured as an anti-freeze probe (Pa H06 = 1); - Triggered when probe ST2 detects a value below Pa A11; - Goes off if ST2 detects a value greater than Pa A11 + Pa A12; - Automatically reset unless alarm events per hour reaches the value of parameter Pa A13, after which manually reset; - Inactive during timer Pa A10 after Energy 100 is turned on using the On-OFF key (refer to keyboard) or digital ON-OFF input (refer to digital inputs) or after switching to heating mode. | YES | YES |  |  |  |  |
| E06 | Probe ST2 fault | - All loads will be shut down; - Triggered if probe ST2, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES |
| E07 | Probe ST3 fault | - All loads will be shut down; - Triggered if probe ST3, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES |
| E11 | High pressure / high temperature (analogue) | - Compressor will be shut down; - Active if at least one probe is configured for condensation control (refer to analogue inputs) - Triggered when the condensation probe detects a value in excess of Pa A14 - Turned off if temperature/pressure falls below Pa A14 – Pa A15. - Always manually reset | YES |  |  |  |  |  |
| E12 | Low pressure / low temperature (analogue) | - Compressor and fans will be shut down; - Active if at least one probe is configured for condensation control (refer to analogue inputs) - Triggered when the condensation probe detects a value below Pa A17 - Goes off if temperature/pressure exceeds Pa A17 – Pa A18. - Automatically reset unless alarm events per hour reaches the value of parameter Pa A19, after which manually reset; - Inactive during timer Pa A16 after compressor is turned on or 4-way valve (reversing valve) is reversed | YES | YES | YES |  |  |  |
| E40 | Probe ST1 fault | - All loads will be shut down; - Triggered if probe ST1, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES |
| E41 | Flow switch (external consent) | - Compressor, external fans and pumps (*) will be turned off if the alarm is to be manually reset; - Triggered if the digital input configured as “flow switch” (refer to digital inputs) remains active for an amount of time equal to Pa A04; - Goes off if the digital input configured as “flow switch” (refer to digital inputs) remains inactive for an amount of time equal to Pa A05; - Automatically reset unless alarm events per hour reaches the value of parameter Pa A06, after which manually reset; - Inactive during timer Pa A03 after pump (hydraulic pump) is turned on | YES | YES |  | YES |  |  |
| E42 | Probe ST4 fault | - All loads will be shut down; - Triggered if probe ST4, configured as an analogue input, shorts or is cut off or probe limits are exceeded (-50°C.. 100°C). | YES | YES | YES | YES | YES | YES |
| E43 | Anti-freeze alarm in secondary circuits (water-water machines with gas investion and heat pump) | - Compressor will be shut down; - Active if probe ST3 is configured as an anit-freeze probe for water-water machines with gas reversal (refer to analogue inputs) - Triggered if probe ST3 detects a value below Pa A11 - Goes off if temperature detected by ST3 exceeds Pa A11 + Pa A12. - Automatically reset unless alarm events per hour reaches the value of parameter Pa A13, after which manually reset; - Inactive during timer Pa A10 after Energy 100 is turned on using the On-OFF key (refer to keyboard) or digital ON-OFF input (refer to digital inputs) or after switching to heating mode. | YES |  |  |  |  |  |
| E44 | Machine out of coolant | - Compressor and fans will be shut down; - In all operating modes except boiler use or defrosting, the machine is checked for leakage in the gas circuit or breakage of the reversal valves (heat pump operation). - Triggered in heating mode if ST2-ST1(or ST3) < Pa A20 continuously for an amount of time in excess of Pa A21 Triggered in cooling mode if ST1(or ST3)-ST2 < Pa A20 continuousaly for an amount of time in excess of Pa A21 - Always manually reset - Timer is reset every time operating mode is changed with the compressor turned off. - Inactive for the duration of parameter Pa A22 after compressor is turned on. | YES | YES | YES |  |  |  |
| E45 | Configuration error | - All loads will be shut down; - If ST1 is configured as a request for heating digital input and ST2 as a request for cooling input (refer to analogue inputs), the alarm will be triggered if both inputs are active. | YES | YES | YES | YES | YES | YES |

Le successive tabelle riassumono gli allarmi raggruppati per tipologia (digitale o analogico).

TABELLA ALLARMI DIGITALI:

Allarmi digitali

| Nome allarme | Evento attivazione bypass | Tempo Bypass | Durata attivazione | Durata disattivazione | N° interventi ora |
| --- | --- | --- | --- | --- | --- |
| Allarme alta pressione compressore 1 | Nessuno | non presente | non presente | non presente | Riarmo manuale |
| Allarme alta pressione | Nessuno | non presente | non presente | non presente | Riarmo manuale |
| Allarme bassa pressione | Accensione di un compressore del circuito o inversione valvola 4 vie | Pa A01 | non presente | non presente | Pa A02 |
| Allarme flussostato | Attivazione pompa | Pa A03 | Pa A04 | Pa A05 | Pa A06 |
| Termica compressore 1 | Accensione di un compressore | Pa A07 | non presente | non presente | Pa A08 |

TABELLA ALLARMI ANALOGICI:

Allarmi analogici

| Nome allarme | Evento | Tempo. Bypass | SET attivazione | Isteresi | N° interventi ora | Sonda di regolazione |
| --- | --- | --- | --- | --- | --- | --- |
| Allarme antigelo | On Off, ingresso in modo heat, on off remoto | Pa A10 | Pa A11 | Pa A12 positiva | Pa A13 | ST2 se il parametro configurazione Pa H06 = 1, altrimenti allarme non attivo |
| Allarme bassa pressione/bassa temperatura condensazione | Accensione di un compressore o inversione valvola 4 vie | Par A16 | Pa A17 | Pa A18 positiva | Pa A19 | Sonda configurata come controllo condensazione |
| Allarme alta pressione/temperatura condensazione | Nessuno | non presente | Pa A14 | Pa A15 negativa | Riarmo manuale | Sonda configurata come controllo condensazione |
| Allarme over temperature | Nessuno | La Durata di attivazione deve superare Pa A26 | Pa A25 |  | Riarmo automatico | ST1 |

# Technical data

x

## Technical data

|  | Typical | Min. | Max. |
| --- | --- | --- | --- |
| Power supply voltage | 12V~ | 10V~ | 14V~ |
| Power supply frequency | 50Hz/60Hz | --- | --- |
| Power | 3.5VA | --- | --- |
| Insulation class | 1 | --- | --- |
| Grado di protezione | Frontale IP65 | --- | --- |
| Operating temperature | 25°C | 0°C | 60°C |
| Operating humidity (non-condensing) | 30% | 10% | 90% |
| Storage temperature | 25°C | -20°C | 85°C |
| Storage humidity (non-condensing) | 30% | 10% | 90% |

## Electromechanical features

| 115/230 V digital outputs | - n° 4 relè 2A - 1 TRIAC 2 A |
| --- | --- |
| 24 V~ outputs | - 1 TRIAC output, no optic insulation; max. 500 mA. |
| Analogue inputs | - 3 temperature sensors, range -30C  90C; - 1 configurable input: 4...20 mA transducer or temperature sensor, range -30C  90C; |
| Digital inputs | - n 5 voltage-free digital inputs |
| Terminals and connectors | - 1 9-way snap-on high voltage connector AWG 16-28 - 1 16 way snap-on low voltage connector, thread 4.2, AWG 16-28 - 1 p2,5 5–way remote control and copy card connector, AWG 24-30 - 1 p 2 3-way remote keyboard or optional relay connector, AWG 22-30; |
| Display and leds | - 3 digits + sign; - 5 red leds |
| Keys | - 2 keys |
| Serials | - n° 1 serial 9600 |

The instrument must be powered with a suitable current transformer with the following features:

current transformer

- Primary voltage:		230V~-15%+6%; 110V~±10%

- Secondary voltage:		12V~

- Power supply frequency:		50Hz; 60Hz

- Power:			5VA;

## Dimensions

Dimensions:	Front panel 76x34, depth 58mm

Container: 	PC+ABS plastic resin with V0 extinguishing classification

Assembly: 	Panel, on 71x29mm hole

dimensions

<IMG INFO>

170

95,3

0

2

127,6

14,15

-1

## Regulations

The product complies with the following European Community Directives:

- Council Directive 73/23/CEE and subsequent modifications

- Council directive 89/336/CEE and subsequent modifications

and complies with the following harmonised regulations:

- LOW VOLTAGE: EN60730

- EMISSION: EN50081-1 (EN55022)

- IMMUNITY: EN50082-1 (IEC 801-2,3,4)

# Use of the device

x

## Permitted use

This product is used to control single circuit chillers and heat pumps.

To ensure safety, the controller must be installed and operated in accordance with the instructions supplied, and access to high voltage components must be prevented under regular operating conditions. The device shall be properly protected against water and dust and shall be accessible by using a tool only. The device is suitable for incorporation in a household appliance and/or similar air conditioning device.

According to the reference regulations, it is classified:

- In terms of construction, as an automatic electronic control device to be incorporated with independent assembly or integrated;

- In terms of automatic operating features, as a type 1 action control device, with reference to manufacturing tolerances and drifts;

- As a class 2 device in relation to protection against electrical shock;

- As a class A device in relation to software structure and class.

## Forbidden use

Any use other than the permitted use is forbidden.

Please note that relay contacts supplied are functional and are subject to fault (in that they are controlled by an electronic component and may be shorted or remain open); protection devices recommended by product standards or suggested by common sense in response to evident safety requirements shall be implemented outside of the instrument.

# Responsibility and residual risks

x

Microtech shall not be held liable for any damage incurred as a result of:

- installation/use other than those intended, and, in particular, failure to comply with the safety instructions specified by applicable regulations and/or provided in this document;

- use with equipment which does not provide adequate protection against electric shocks, water and dust under the effective conditions of installation;

- use with equipment which permits access to hazardous parts without the use of tools;

- installation/use with equipment which does not comply with current regulations and legislation.

# Glossary

x

Multiple inputs with an OR relationship to one another are equivalent to a single input with the following status:

Logical OR

Active if at least one input is active

Inactive if no input is active

To “Scroll up” a menu means listing the various parameters from the bottom up (Pa10 -> Pa 09 -> Pa 08 ….)

Scroll up

Indicates that the instrument is waiting, in stand-by mode; all functions are suspended.

Stand-by

Set to zero.

Reset

Resetting an alarm means reactivating it ready for a new signal.

Reset alarm

A manual reset alarm must be reset using the keyboard.

Manual reset

To “Scroll down” in a menu is to list parameters from the top down (Pa08 -> Pa 09 -> Pa 10 ….)

Scroll down

Means flashing; normally refers to leds

BLINK

Average number of hours is the ratio between the total number of hours for which the compressors are available and the number of compressors in the circuit

Average number of hours

Devices in the system, including compressors, fans, hydraulic pump, electrical anti-freeze heaters…

Loads

A reference value (set by the user) defining the system’s operating status, such as the thermostat that controls temperature in the home: if we want to maintain a temperature of 20 °C we set the set point to 20°C (the heating system will come on if the temperature in the house falls below 20°C, and go off if it exceeds this value).

Set Point

Values falling within a given interval; Range 1…100 indicates all values between 1 and 100

Range

A hysteresis is normally defined around a set point to prevent frequent oscillation of the change of status of the load being controlled;

Hysteresis

Example: suppose we have a set point of 20 °C on a probe for measurement of room temperature, above which a compressor will be started up;

When room temperature nears the set point (20 °C) there will be an unstable phase during which the relay which starts up the compressor will frequently switch from ON to OFF and vice versa, which could result in serious damage to the system.

To prevent this problem a hysteresis is defined: an interval of tolerance within which there will be no change in status; in our example, we could set a hysteresis of 1 °C, in which case the compressor would be started up at 21 °C (set point  + hysteresis) and turned off at 19 °C (set point – hysteresis)

Memory in which data is maintained even when the device is turned off (as distinct from temporary memory, the data in which is lost when the device is turned off.)

Permanent memory

Temperature/Pressure below or above which proportional output is cut-off

Cut-off

# ANALITIC INDEX

A

Additional keyboard output	9

Alarm events per hour	36

Alarm parameters	30

Alarms	36

Allarmi analogici	40

Allarmi digitali	40

Analogue inputs	8

configuration table	8

Anti-freeze/boiler parameters	32

Anti-freeze/supplementary electrical heater control	23

diagram	23

Average number of hours	44

B

Basic module	6

BLINK	44

Boiler	17

Boiler control	24

C

Components	6

Compressor	15

Compressor control – regulation algorithm	21

Cooling diagram	21

Heating diagram	21

Compressor parameters	31

Compressor timing	15

Off-on and on-on  comp. diagram	15

Off-on timing	15

On-on timing	15

Condensation fan	15

Condensation fan control	21

Cool mode	22

Heat mode	22

Configuration of analogue inputs	8

Configuration of digital inputs	8

Configuration of outputs	9

Configuration parameters	29; 33

Connection diagrams	7

Connection with ST3 probe configured as 4-20 mA input	7

Connection with ST3 probe configured as NTC	7

Cooling	18

Copy Card	6

Copy card device	10

Counter mode	27

Cross references:	5

current transformer	41

Cut-off	44

D

Defrost end	27

diagram	27

Defrost parameters	33

Defrost start	26

diagram	26

Defrosting	26

Description of parameters	29

Device off	18

DIAGNOSTICS	36

Digital inputs	8

Digtial inputs

configuration table	8

polarity	8

Dimensions	41

Display	11

Displays	11

Dynamic set point	19

Control parameters	19

Modification on the basis of current input in cooling mode	20

Modification on the basis of current input in heating mode	20

Modification on the basis of outdoor temperature in cooling mode	20

Modification on the basis of outdoor temperature in heating mode	20

E

Electromechanical features	41

External anti-freeze electrical heater control	24

External anti-freeze electrical heaters	16

F

Fan configuration	15

Fan control in cool mode

diagram	22

Fan control in heat mode

diagram	23

Fan control parameters	31

Fan module pilot output	9

Fan modules	6

Forbidden use	42

FUNCTIONS	26

G

GLOSSARY	44

H

Heating	18

Hot start function	27

diagram	27

HOW TO USE THIS MANUAL	5

Hydraulic pump	16

Continuous operation	16

Operation in response to request	16

Hydraulic pump control	23

Hysteresis	44

I

Icons for emphasis	5

Impulse duration	15

INSTALLATION	7

Interface module	6

Internal anti-freeze/supplementary electrical heaters	16

configuration	16

Internal fan	17

1 fan control step	17

2 fan control steps	17

3 fan control steps	17

Internal fan control	24

Internal fan:	17

INTRODUCTION	6

K

Keyboard	11

Keyboards	6

Keys	11

Mode	11

Mode – on-off key combination	11

On-off – Reset alarms	11

L

Led	11

List of alarms	36

Load control	21

Loads	44

Logical OR	44

M

Machine out of coolant signal	27

Manual reset	44

Menu structure	13

O

Operating modes	18

configuration table	18

Outputs	9

P

Param Manager	6

Parameter programming – Menu levels	12

PARAMETERS	29

Permanent memory	44

Permitted use	42

Phase shift	15

Pick-up	15

Power failure	28

Preventilation	22

Pump parameters	32

R

Range	44

Recording hours of operation	26

References	5

Regulation algorithm in cool mode	21

Regulation algorithm in heat mode	21

Regulations	41

Relays	9

configuration table	9

Remote keyboard	12

Reset	44

Reset alarm	44

RESPONSIBILITY AND RESIDUAL RISKS	43

Reversing valve	16

Polarity	16

Reversing valve control	23

S

Safety timing	15

Scroll down	44

Scroll up	44

Selection of operating mode from analogue input	18

Diagram	19

Serial outputs	9

Set Point	44

Setting set points	19

Silent speed	22

Stand-by	18; 44

Switching from digital input	20

SYSTEM CONFIGURATION	15

T

Tabella Allarmi	37

Table of parameters	33

alarm parameters	34

anti-freeze/boiler parameters	35

compressor parameters	34

defrost parameters	35

fan control parameters	34

pump parameters	35

Technical data	41

TECHNICAL DATA	41

TEMPERATURE CONTROL FUNCTIONS	18

TK output

configuration table	9

Triac	9

U

Units of measurement	10

USE OF THE DEVICE	42

USER INTERFACE	11

V

Visibility of parameters and sub-menus	14