FakeMODBUS

Televis Compact Driver

HOWTO

Sommario

1	Televis Compact Modbus Driver Example	3

1.1	Technical Specification for device FakeMODBUS	4

1.1.1	Controller resources accessed using  MODBUS function H03 and H04	4

1.1.2	Controller  commands to be used with MODBUS function H06	4

1.1.3	Controller parameters accessed  using  MODBUS function H03 and H06	4

1.1.4	MODBUS function H11 format	4

1.2	Communication settings for MODBUS device	6

1.3	MODBUS device identification	6

1.3.1	Identification with MODBUS function H11	7

1.3.2	Identification, alternative method	8

1.3.3	Identification with MODBUS function H2B	10

1.4	Analog input reading without existence condition	12

1.5	Digital input reading without existence condition	13

1.6	Alarm reading with existence condition	14

1.7	Analog input reading with existence condition	15

1.7.1	Analog input conditioned by probe error	15

1.7.2	Analog input conditioned by parameter	16

1.8	Digital input reading conditioned	16

1.9	Parameters	17

1.10	Remote commands	19

# Televis Compact Modbus Driver Example

This document describes an example of how to compile the P04354 excel model to create a device driver to be used with the new TelevisCompact.

The file P04354_FakeModbus_v1_1.xls is supplied as reference for the following paragraphs, unless otherwise specified. The following chapters will refer to an example of technical specification summarized in Cap 1.1.

## Technical Specification for device FakeMODBUS

Let’ s assume to have a fake modbus controllers family described by the following technical specification and composed by 3 different models identified as FakeMB mini, FakeMB midi, FakeMB maxi

### Controller resources accessed using  MODBUS function H03 and H04

| Function | Address | WORDS | Measure | Unit | Format | FakeMB mini | FakeMB midi | FakeMB maxi |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| H04 | H01FF | 2 | Phase voltage | V/100 | Unsigned long | X | X | X |
| H04 | H0201 | 2 | Analogue input 1 | C° | Signed long | X | X | X |
| H04 | H0203 | 2 | Analogue input 2 | C° | Signed long |  | X | X |
| H03 | H0211 | 1 | Digital input 1 | Bool | Unsigned int | X | X | X |
| H03 | H0211 | 1 | Digital input 2 | Bool | Unsigned int |  |  |  |
| H03 | H0205 | 2 | High temperature1 | C° | Signed long | X | X | X |
| H03 | H0205 | 2 | Low temperature 1 | C° | Signed long | X | X | X |
| H03 | H0209 | 1 | Error probe 1 | Bool | Unsigned int | X | X | X |
| H03 | H0207 | 2 | High temperature 2 | C° | Signed long |  |  |  |
| H03 | H0207 | 2 | Low temperature 2 | C° | Signed long |  |  |  |
| H03 | H0212 | 1 | Digital output 1 | Bool | Unsigned int | X | X | X |
| H03 | H0212 | 1 | Light | Bool | Unsigned int | X | X | X |

### Controller  commands to be used with MODBUS function H06

| Address | WORDS | Command | Value | Format | FakeMB mini | FakeMB midi | FakeMB maxi |
| --- | --- | --- | --- | --- | --- | --- | --- |
| H02A | 1 | Reset alarms | 0 | Unsigned int | X | X | X |
| H02A | 1 | Light ON | 1 | Unsigned int | X | X | X |
| H02A | 1 | Light OFF | 2 | Unsigned int | X | X | X |
| H02B | 1 | Reboot | -1 | Signed int | X | X | X |

### Controller parameters accessed  using  MODBUS function H03 and H06

| Address | Label | Min | Max | Default | WORDS | FakeMB mini | FakeMB midi | FakeMB maxi |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| H030 | HA1 | -100 | 100 | 100 | 1 | X | X | X |
| H032 | LA1 | -100 | 100 | 0 | 1 | X | X | X |
| H034 | HA2 | -100 | 100 | 100 | 1 |  | X | X |
| H036 | LA2 | -100 | 100 | 0 | 1 |  | X | X |
| H040 | NUM_ANAG_IN | 1 | 3 | 1 | 1 | X | X | X |
| J042 | NUM_DIG_IN | 1 | 3 | 1 | 1 | X | X | X |

### MODBUS function H11 format

It is described the way the controller answers to the H11 function. The answer is specific for each Modbus controller.

Master query:

| Byte 1 | Byte 2 | Byte 3 | Byte4 |
| --- | --- | --- | --- |
| Slave address | Function H11 | MSB CRC | LSB CRC |

Slave response:

| Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 | Byte 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Slave address | Function H11 | Byte number | ID device | Data | Data | Data | MSB CRC | LSB CRC |

Where the ID device depends upon the device model and it will be:

- 121	for the FakeMB mini

- 130	for the FakeMB midi

- 170	for the FakeMB maxi

And the Data field will be always 0.

## Communication settings for MODBUS device

The settings for the serial connection and the number of MODBUS address to check during network discover are listed in the P0435 excel file  at the Legenda sheet .

In this page an important cell is the Network Address Filter: MODBUS devices can have an address varying between 1 and 255, the value of this cell can reduce this range, thus reducing the time of the network discover.

E.G.: assuming that the MODBUS device will never be installed with an address higher than 20, it’s possible to fill this field with the range 1-20, thus avoiding unnecessary scanning of subsequent 235 address and reducing the time to scan the network of MODBUS instruments.

If not specified the fields Baud Rate and Parity have as default value 9600, even.

The field Filename defines the name of the binary file containing the driver you are going to produce, it is important that this name is different from the name of any other driver currently in use or still present in your TelevisCompact system, whether provided by Eliwell or produced by the user.

It’s also possible to provide some advanced parameters such as the Device Timeout and the dimension of the buffer used by the Transmitter (Device buffer TX(bytes)) and by the Receiver (Device buffer RX(bytes)). These settings may be useful to achieve an higher acquisition speed, but a bad value may cause a not working driver. Please pay attention that this can speed up the acquisition if you have several device of this kind in your network, if you have just one the improvement could be negligible. So if you are not interested in improving the performance or you don’t know which are the values for your device, leave the default values.

## MODBUS device identification

The first thing to set up in a driver is the way the device is recognized by the Televis Compact. This can be done finding out a request or a series of requests that return data that are unique to this device. These requests can be the identification requests (e.g. MODBUS commands H11 or H2B) or readings of memory register (e.g MODBUS commands H03 or H04).

The process is composed by the following items:

- A request or series of requests to the device. These requests must be added to the Client page as a Support resource.

- A sequence of expressions (it could be just one) that must be evaluated using as input the reply of the device to the identification request. To state that the device is recognized, the last expression must be return a value which is not 0 (LASTVALUE must be not 0). Besides that, at least one expression must contain a SET operator where the MODELCODE variable is set. The MODELCODE set this way will be matched with the POLI values in the P0435 Models page, if a match exists then the device is successfully detected and the NAME corresponding to the given POLI will be assigned to the device.

- A list of POLI,NAME couple. These must be added to the Models page.

Let’s see two examples in the next sections. The first one refers to the sample driver that we are building in this “how to” document. The second one does not refers to the driver we are building, it refers to a technique that is used when there is no identification request available or when the device is a programmable device (e.g. an Eliwell XT Pro).

### Identification with MODBUS function H11

The identification of the instrument is performed with the MODBUS function H11 that, if implemented in the firmware, returns a unique ID number.

Note that while the request is uniquely encoded by the MODBUS protocol, the format and size of the response data field varies from manufacturer to manufacturer ( refer to the controller specification )

E.G.: knowing that the response return 4 bytes of data where the first identifies the ID of the device, we will have the following steps:

Master query:

| Slave address | 08h |
| --- | --- |
| Function | 11h |
| MSB CRC | C6h |
| LSB CRC | 7Ch |

Slave response:

| Slave address | 08h |
| --- | --- |
| Function | 11h |
| Byte number | 04h |
| Data 1 (ID) | 82h |
| Data 2 | 00h |
| Data 3 | 00h |
| Data 4 | 00h |
| MSB CRC | 42h |
| LSB CRC | B9h |

This command is encoded in the Client page using an expression of type RAW in the field MODBUS_ADDRESS as follows:

RAW({MTA,H11,MCRC2},{MTA,H11,H04,XD(0),XI(3),MCRC2})

Pay attention to the usage of the XD(0) operator. XD is used to extract data from the reply and here it extracts the 4th byte, which is the one who carries the information about the model.

Hereafter how the Client page appears:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | Ident |
| MODBUS_COMMAND | C |
| MODBUS_ADDRESS | RAW({MTA,H11,MCRC2},{MTA,H11,H04,XD(0),XI(3),MCRC2}) |
| FILTER | HFF |
| EXISTENCE | CONST(0) |
| TYPE | Support |

In the DataAcquisitionInit page the field access described in the Client page is referenced by using the  “Client(…)” operator  applied to the field access LABEL (which is “ident”).

The value retrieved with the field access is then  associated to the MODELCODE with the command:

SET(MODELCODE)=Client(ident)

Hereafter how the DataAcquisitionInit  page appears:

| COLUMN | VALUE |
| --- | --- |
| FUNCTION | IDENTIFICATION |
| PROTOCOL | ANY |
| 0 | SET(MODELCODE)=Client(ident) |

The MODELCODE is uniquely associated with the name of the model trough the field POLI in the Models page, which is a reference to the ParamsDefaults page.

Note that the fields PARAM_MANAGER_NAME and PARAM_MANAGER_NAME_MODBUS in the Models page cannot contain spaces, unlike the field MODEL_NAME.

### Identification, alternative method

This example does not refer to the P04354_FakeMODBUS.xls.

This technique should be used when the device does not support an identification command. This happens quite often and it is a common situation when a programmable device is in use.

In this situation, the driver developer must identify a register that holds a value that is typical to the devices. It can be a firmware version, revision or, when a programmable device is in use, a custom value that the developer of the application that runs on the programmable device has included with the only purpose of making the combination of device+application identifiable.

E.g. An application was developed for an XTPro device. The XTPro application holds the value 113 in the register at address H0200, that can be read with the H03 command.

To identify this device the reading of the register must be added to the Client page as follows:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | Ident |
| FORMAT |  |
| MEASUREMENT_UNIT | CONST(VM00020) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H0200 |
| FILTER | HFFFF |
| EXISTENCE | CONST(0) |
| TYPE | Support |

Afterwards, the data gathered by this request must be processed in the DataAcquisitionInit page as follows:

| COLUMN | VALUE |
| --- | --- |
| FUNCTION | IDENTIFICATION |
| PROTOCOL | ANY |
| 0 | SET(MODELCODE)=Client(ident) |

The expression provided just takes the value gathered by reading the H0200 register and writes it in the MODELCODE variable.

Please pay attention to the following fact. The identification process requires that the result of the last expression is not 0. When a SET operator is used, the result of the expression is the value used to set the variable. So in most cases (and in this one too) we are lucky, because the value returned by the request is not 0, but if it would have been 0, the page would have been changed as follows:

| COLUMN | VALUE |
| --- | --- |
| FUNCTION | IDENTIFICATION |
| PROTOCOL | ANY |
| 0 | SET(MODELCODE)=Client(ident) |
| 1 | GET(MODELCODE)=FIX(0) |

Here, the first expression sets the MODELCODE, the second one compares it to 0. If the value is 0, the result of comparison is TRUE, which is automatically converted to 1 (FALSE would have been converted to 0).

Anyhow, it is deprecated and highly discouraged to choose a 0 value for identification. This is because 0 it’s a value that it is commonly stored in registers of every device and this can lead to a wrong identification of devices.

Let’s back to the example of the XTPro device with 113 stored in the H0200. After the expression is evaluated, MODELCODE will be set to 113.  The Models page is compiled as follows:

| COLUMN | VALUE |
| --- | --- |
| POLI | 113 |
| MODEL_NAME | XTPro Application |

Here the 113 value has a match in the POLI column, so the device is successfully detected and its name will be “XTPro Application”.

### Identification with MODBUS function H2B

This is a quite complex identification method that usually require more requests. If  you decide to use this method use the same approach described for command H11.

Alarm reading without existence condition

The reading of a single alarm is achieved by compiling a single row in the P0435 Client page.

E.G.: if you want read the status of the alarm High Threshold AI1 and knowing that is indicated by the value of the first bit of the LSB of the register at the address 0205h, the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | AlmH1 |
| DESCRIPTION | High Threshold AI1 |
| DESCRIPTION_CODE | ALM00177 |
| PROGRESSIVE | 1 |
| MEASUREMENT_UNIT | CONST(VM00021) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H0205 |
| FILTER | H0001 |
| EXISTENCE | CONST(1) |
| TYPE | Alarm |

Note that the correct values for the fields DESCRIPTION_CODE and MEASUREMENT_UNIT can be derived directly from the Televis Compact dictionary file of the desired language.

The dictionary files are on board of the Televis Compact and they can be downloaded using a Web browser. Valid dictionary links are

http://compactip/bin/Invenys.Dictionaries/Dictionary.de-DE.txt		GERMAN

http://compactip/bin/Invenys.Dictionaries/Dictionary.en-GB.txt		ENGLISH

http://compactip/bin/Invenys.Dictionaries/Dictionary.es-ES.txt		SPANISH

http://compactip/bin/Invenys.Dictionaries/Dictionary.fr-FR.txt		FRENCH

http://compactip/bin/Invenys.Dictionaries/Dictionary.it-IT.txt		ITALIAN

where compactip is the ip address of your Televis Compact. More links will be available when more languages will be supported.

In case of different alarms with the same DESCRIPTION_CODE, it is necessary to identify each resource uniquely using the PROGESSIVE field.

So if we had multiple alarms with the same DESCRIPTION_CODE value, each row would have over the field MODBUS_ADDRESS and FILTER different, also the field PROGRESSIVE with a value ranging from 1 to n, where n is the number of alarms.

## Analog input reading without existence condition

The reading of an analog input without existence condition is achieved by compiling a single row in the P0435 Client page.

E.G.: if you want read the value of the analog input Phase Voltage and knowing that this value is in V/100, unsigned, indicated by the two registers starting at address 01FFh and is always available (without existence condition), the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | AI0 |
| DESCRIPTION | Phase Voltage |
| DESCRIPTION_CODE | CUS40000 |
| PROGRESSIVE | Phase-Voltage |
| FORMAT | CONST(-2) |
| MEASUREMENT_UNIT | CONST(VM00008) |
| MODBUS_COMMAND | A |
| MODBUS_ADDRESS | H01FF |
| FILTER | S[4] |
| EXISTENCE | CONST(1) |
| TYPE | AI |

Let’s look at the Filter field. Nowadays is quite common to see devices that store their resources as 32 bits variable. Unluckily the MODBUS protocol just manages 16 bits register. To overcome this limitations is quite common to store these values on 2 adjacent registers.

To manage this situation in the Televis Compact, you have to provide the lowest address of the registry pair and telling that the value is 4 bytes wide by using S[4] as filter. For the sake of clarity, S[4] is a short form for the 4 byte long mask HFFFFFFFF. Doing this way, the Televis Compact will automatically understand that the value spans over 2 registers.

This example shows how to assign to a resource a description that is not linked to the TelevisCompact dictionary.

Note that the value CUS40000 of the field DESCRIPTION_CODE indicates a custom description that must be defined in the PROGRESSIVE field. The set of chars admitted I the PROGRESSIVE column are a-z A-Z 0-9 .(dot) and –(hyphen), this restriction is due to the fact that this field act as resource identifier inside the software , but a proper custom name can be set in the supervisor system using a full character set.

Of course this applies to any type of resource, either an analog or digital input, output, or alarm.

## Digital input reading without existence condition

The reading of a digital input without existence condition is achieved by compiling a single row in the P0435 Client page.

E.G.: if you want read the value of the Digital input 1 and knowing that this value is expressed by the first bit of the LSB of the register at address 0211h, the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | DI1 |
| DESCRIPTION | Digital Input 1 |
| DESCRIPTION_CODE | STA00001 |
| PROGRESSIVE | 1 |
| MEASUREMENT_UNIT | CONST(VM00021) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H0211 |
| FILTER | H0001 |
| EXISTENCE | CONST(1) |
| TYPE | DI |

## Alarm reading with existence condition

The reading of a single alarm with existence condition is achieved by compiling a single row in the P0435 Client page, and possibly a row in the Params page.

E.G.: if you want read the status of the alarm High Temperature 2 conditioned by the value of the parameter NUM_ANAG_IN and indicated by the value of the first bit of the LSB of the register at address 0207h, the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | AlmH2 |
| DESCRIPTION | High Temperature 2 |
| DESCRIPTION_CODE | ALM00177 |
| MEASUREMENT_UNIT | CONST(VM00021) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H0207 |
| FILTER | H0001 |
| EXISTENCE | Params(NUM_ANAG_IN)>CONST(1) |
| TYPE | Alarm |

Note that the difference from reading an alarm without existence condition is the presence of a Boolean expression in the field EXISTENCE. In this particular case, we reference the value NUM_ANAG_IN in the Params page that, if greater than 1, it guarantees the existence of the alarm described (for the parameters refer to the relevant section).

Again you can have multiple similar alarms, so if we had more alarms of the same types as described above, each row would have different value for MODBUS_ADDRESS and FILTER field, and the filed PROGRESSIVE with a value ranging from 1 to n, where n is the number of alarms with the same DESCRIPTION_CODE, we would have also different EXISTENCE field, such Params(NUM_ ANAG_IN)>CONST(3) for the existence of alarms 1 to 4.

## Analog input reading with existence condition

The reading of a analog input without existence condition is achieved by compiling a single row in the P0435 Client page.

### Analog input conditioned by probe error

E.G.: if you want read the value of analog input  Probe 1 and knowing that it is conditioned only on the correct operation of the probe itself, which can also be a negative value, expressed in C°, with a decimal place, in the two bytes read at address 2001h,  the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | AI1 |
| DESCRIPTION | Analog Input 1 |
| DESCRIPTION_CODE | INP40000 |
| PROGRESSIVE | 1 |
| FORMAT | CONST(-1) |
| COMPLEMENTED | TRUE |
| MEASUREMENT_UNIT | CONST(VM00000) |
| MODBUS_COMMAND | A |
| MODBUS_ADDRESS | H0201 |
| FILTER | S[4] |
| EXISTENCE | CONST(1) |
| TYPE | AI |
| TEST_CONDITION | Client(ProbErr1) |

In this case, in addition to the fields used in the examples above, you specify the COMPLEMENTED field, indicating that the value may be read can also be negative, and the TEST_CONDITION field, in which, instead of a boolean expression is placed a direct reference to the row with LABEL set to ProbErr1 in the same Client page. In this way the resource is defined as ever-existing, but in error if there is a physical error of the probe itself.

In case of probe error the data of the probe is filed by the TelevisCompact so as be recognizable in historical data analysis phase.

For completeness the row that is referred to Client(ProbErr1) could be the following:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | ProbeErr1 |
| DESCRIPTION | Probe Error 1 |
| DESCRIPTION_CODE | ALM40125 |
| MEASUREMENT_UNIT | CONST(VM00021) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H0209 |
| FILTER | H0001 |
| EXISTENCE | CONST(1) |
| TYPE | Alarm |

### Analog input conditioned by parameter

However, if the existence of a probe is determined by a parameter, you can indicate this using the EXISTENCE field, for example:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | AI2 |
| DESCRIPTION | Analog Input 2 |
| DESCRIPTION_CODE | INP40000 |
| PROGRESSIVE | 2 |
| FORMAT | CONST(-1) |
| COMPLEMENTED | TRUE |
| MEASUREMENT_UNIT | CONST(VM00000) |
| MODBUS_COMMAND | A |
| MODBUS_ADDRESS | H0203 |
| FILTER | S[4] |
| EXISTENCE | Params(NUM_SONDE_ANAG)>CONST(1) |
| TYPE | AI |

## Digital input reading conditioned

The reading of a digital input conditioned is achieved by compiling a single row in the P0435 Client page.

E.G.: if you want red the status of  Digital Input 2 conditioned by the value of the parameter NUM_IN_DIG and indicated by the value of second bit of the LSB of the register at address 2011h, the required fields on the row in the Client page are:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | Di2 |
| DESCRIPTION | Digital Input 2 |
| DESCRIPTION_CODE | STA40001 |
| PROGRESSIVE | 2 |
| MEASUREMENT_UNIT | CONST(VM00021) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H2011 |
| FILTER | H0002 |
| EXISTENCE | Params(NUM_DIG_IN)>CONST(1) |
| TYPE | DI |

## Parameters

The parameters of a MODBUS device are descrive using mainly the two page Params and ParamsDefaults, and if the driver is applicabile to different models, the Models page also.

The most important of the three page is the Params page: it describes the entire list of parameters provided by the MODBUS device an uses many of the fields already described in previous examples in the Client Page.

In addition there are fields LOW_LIMIT, HIGH_LIMIT and R_W_RW that as you can guess from the names themselves indicate respectively the minimum value, the maximum value and the access mode for the single parameter described in the row of the page.

The LOW_LIMIT and HIGH_LIMIT fields have a peculiarity when dealing with values that are represented with a resolution of one or more decimal positions. The values provided as limits must be multiplied by the power of ten corresponding to the value resolution, in order to remove the fractional part.

E.g. If a set point has a resolution of 1 decimal position, its limits could be -23.5 and 23. These values must be multiplied by 101 before being written in the Params Page as -235 and 230.

When you write a parameters, the Televis Compact application checks is the value to be written is within the allowed range, if the check fails the writing operation is forbidden. So please pay attention when you write down the limits of a parameter with a resolution of one or more decimal positions because an wrong value could inhibit the modification of that parameter.

E.G.: As the description of the parameter Number of analog inputs, with value in the range 1-3, numeric, unsigned, two bytes and accessible for both reading and writing at the address 040h, the necessary fields in the corresponding row of the Params page are:

| CAMPO | VALORE |
| --- | --- |
| INDEX | Unique number |
| LABEL | NUM_ANAG_IN |
| DESCRIPTION | Number Analog Inputs |
| DESCRIPTION_CODE | CUS40000 |
| PROGRESSIVE | Number-Analog-Inputs |
| LOW_LIMIT | 1 |
| HIGH_LIMIT | 3 |
| MEASUREMENT_UNIT | CONST(VM00020) |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H040 |
| FILTER | HFFFF |
| R_W_RW | RW |

The default values of parameters are listed in the ParamsDefaults page which must necessarily have the same number of rows in the Params page. The fields that link the two pages are the field INDEX and the field LABEL. The subsequent fields in ParamDefaults page are used to indicate different sets of default values of the parameters used to model the device using the field Poli in the Models page.

E.G.: if you have three models, respectively with POLI 121, 130 and 170 described in the Models page and you want to describe the set of default values for parameters, the Models page will have the following fields: INDEX, LABEL, 121, 130, 170.

## Remote commands

In this section we are going to talk about the remote commands that can be sent to a device (e.g. “Turn On”,”Turn Off”,”Defrost”).

This section needs introduction to avoid misunderstanding of the word command, that can be used for both a remote command (e.g. “Turn On”,”Turn Off”,”Defrost”) and a basic protocol command (e.g. H06 for writing a MODBUS register). We’ll refer to the former as remote commands or commands and to the latter as requests.

The Televis Compact manages the remote commands as a sequence of simple writing request:

- The remote commands must be inserted in the Client page. They are similar to resources because they have a description and an existence condition, but they differ because they do not have an associated memory address or value condition. Instead, they have a sequence of request, which must be inserted in the WRITE_SEQUENCE cell, using references to the simple request that are inserted in the Write Page.

- The simple writing request must be inserted in the Write Page.

E.g. Let’s build the “Reset Alarms” remote command for the sample device we are building. As we can read in the specification, it’s possible to trigger the “Reset Alarm” function by writing the value 0 in the register H02A using the H06 MODBUS request.

First of all, let’s add the writing request to the Write page as follows:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| NAME | Reset Alarms |
| VALUE | 0 |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H02A |
| FILTER | HFFFF |

After that add a row in the Client Page with the following data:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | Cmd1 |
| DESCRIPTION | Reset Alarms |
| DESCRIPTION_CODE | CUS40000 |
| PROGRESSIVE | Reset-Alarms |
| EXISTENCE | CONST(1) |
| TYPE | Net Command |
| WRITE_SEQUENCE | Reset Alarms |

Please pay attention that each item that you place in the WRITE_SEQUENCE column will refer to an item in the Write Page. The reference is done by name.

Example: To describe the Reboot command that we know from technical specification to writing with the MODBUS command H06 at the address 02Bh the word (two bytes) with a value of -1, the required fields in the corresponding row of the Write page are:

| CAMPO | VALORE |
| --- | --- |
| INDEX | Unique number |
| NAME | Reboot |
| VALUE | -1 |
| COMPLEMENTED | TRUE |
| MODBUS_COMMAND | S |
| MODBUS_ADDRESS | H02B |
| FILTER | HFFFF |

After that add a row in the Client Page with the following data:

| COLUMN | VALUE |
| --- | --- |
| INDEX | Unique number |
| LABEL | Cmd4 |
| DESCRIPTION | Reboot |
| DESCRIPTION_CODE | CUS40000 |
| PROGRESSIVE | Reboot |
| EXISTENCE | CONST(1) |
| TYPE | Net Command |
| WRITE_SEQUENCE | Reboot |