Dear Leonid,

Here the driver that I made myself: this is the first (and I hope the last) driver I did; I tried to introduce all your request. I used the Thermocool wizard and your information about input and output allocation.

- On/Off state of unit OK (analog input 5: 0: off, 1: on, 2: shutdown (READ).

In global command using "ON/OFF"	 to on-off the chiller

- compressors number OK parameter (number of Evaporator, Circuit for Ev, Comp for

Circ)

- stages number (per compressor) OK parameter

- compressors and steps state OK (digital output)

- active steps number (?) OK (digital output, the same above)

- fans state  (speed)	OK (analog input 4: televis net doesn't support analog output...)

- current capacity of unit OK (analog input 6: number of steps actives for the circuit)

- input water temperature OK (first analog input)

- output water temperature OK (second analog input)

- alarm messages OK (only digital input)

- set point of thermoregulator OK parameter

- differential of regulator OK parameter

- fans set points OK parameters

- fans proportional band OK parameters

To add the driver:

- for example create C:\EwScript directory and copy inside the driver;

- Then insert at the end of the file DtmCfg.ini (you can find it in C:\WINDOWS\system32) this information:

#

# EXTERNAL DRIVER

#

[EXTPRT]

PATH="C:\EwScript"

That’s all !

When you start with Televis Net, you have to the plant setting action to find the XT

then

this window occur

double click on network 1 to reduce the address to search the XT to do not spend to much time: set these values

then confirm and search

if all is ok, in few seconds you can see this:

Push on complete and back: if you want here you can change the labels.

At this point just during the configuration the driver send the password to read/write, so you can read the parameters, modify the setpoint, start the acquisitions and see the alarms

The global command that I implemented are: on/off and write serial password under defrost command. To modify the Cold parameters it is necessary to implement another global command to enter and esc from configuration mode.

# NOTE

This drive is for exhibition only: to use Energy XT under televis net it is necessary to manage an issue that I will describe you in this few lines:

Energy XT has a serial password to let you read/write parameters and variables;

(the serial password works in toggle way only in ram, so at a power on the serial communication is protected (only standard 43 command is allowed to perform the reconize).

If you have a power down of the Energy XT during acquisition, after power on of the Energy, Televis Net cannot recovery no link, because Energy XT loses the serial password sent automatically from the driver at the beginning during the network configuration. To recovery it you have to stop the acquisition, send the password (defrost command) and restart the acquisition

So, this means that for real use of Energy XT with televise net in modbus, it is necessary to modify Energy XT firmware or to modify Televis net to manage the  nolink for energy XT.

It is not impossible work, but it is work and it has to be justificate and planned in the technical department. Energy XTPRO has not this issue because the marketing guys just decided from long time to have the possibility to have XTPRO under televis net with modbus protocol, no for Energy XT.

Sandro and/or Marco will decide for this work with marketing guys.